## HMBP
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | HMBP
Business Plan Program | Administration/Documentation | 1010003 |  |  | Business Activities Page and/or Business Owner/Operator Identification Page | Failure to electronically submit the Business Activities Page and/or Business Owner Operator Identification Page, or failure to report complete or accurate information on these forms. | 19 CCR 4 2652(a)(1); HSC 6.95 25508(a)(1), 25508(a)(3) | 2021-08-02 | 2024-09-30 | 2024-09-30 | Revised | 9 | Owner/Operator Information |  | Business Owner/Operator ID and Business Activities pages electronically submitted and are accurate | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit the Business Activities Page and/or Business Owner Operator Identification Page, or failure to report complete or accurate information on these forms. |  |  | OBSERVATION: The business failed to electronically submit the Business Activities Page and/or Business Owner Operator Identification Page, or failed to report complete or accurate information on these forms. CORRECTIVE ACTION: Complete and electronically submit the Business Activities Page and/or Business Owner Operator Identification Page. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010010 |  |  | Emergency Response Plan and Procedures | Failure to establish and/or electronically submit an adequate emergency response plan and procedures for a release or threatened release of a hazardous material. *Verify agricultural handler exemption HSC 25507.1 | 19 CCR 4 2658; HSC 6.95 25505(a)(3), 25508(a)(1), 25508(a)(3) | 2020-10-01 | 2024-09-30 | 2024-09-30 | Revised | 14 | Emergency Response Plan |  | Electronically submitted adequate response plan/procedures for release/threatened release of hazmat | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to establish and/or electronically submit an adequate emergency response plan and procedures for a release or threatened release of a hazardous material. *Verify agricultural handler exemption HSC 25507.1 |  |  | OBSERVATION: The business failed to establish and electronically submit adequate emergency response procedures for a release or threatened release of a hazardous material. CORRECTIVE ACTION: Establish and electronically submit adequate emergency response procedures for a release or threatened release of a hazardous material within 30 days. | [6 empty] | Yes
Business Plan Program | Training | 1020001 |  |  | Training Program Not Included or Not Adequate | Failure to establish and/or electronically submit an adequate training program in safety procedures in the event of a release or threatened release of a hazardous material. *Verify agricultural handler exemption HSC 25507.1 | 19 CCR 4 2659(a); HSC 6.95 25505(a)(4), 25508(a)(1), 25508(a)(3) | 2021-08-02 | 2024-09-30 | 2024-09-30 | Revised | 15 | Training Program |  | Established and electronically submitted adequate training program | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to establish and/or electronically submit an adequate training program in safety procedures in the event of a release or threatened release of a hazardous material. *Verify agricultural handler exemption HSC 25507.1 |  |  | OBSERVATION: The business failed to establish and electronically submit an adequate employee training plan, which is reasonable and appropriate for the size of the business and the nature of the hazardous material handled. CORRECTIVE ACTION: Establish and electronically submit an adequate employee training plan, which is reasonable and appropriate for the size of the business and the nature of the hazardous material handled. | OBSERVATION: The business failed to establish and electronically submit an adequate employee training plan, which is reasonable and appropriate for the size of the business and the nature of the hazardous material(s) handled. CORRECTIVE ACTION: Establish and electronically submit an adequate training plan, which is reasonable and appropriate for the size of the business and the nature of the hazardous material(s) handled. | [5 empty] | Yes
Business Plan Program | Training | 1020002 |  |  | Training Not Provided and/or Documented | Failure to provide initial and annual training to all employees in safety procedures in the event of a release or threatened release of a hazardous material or failure to document and maintain training records for a minimum of three years. | HSC 6.95 25505(a)(4); 19 CCR 4 2659(b) | 2014-07-01 | 2024-09-30 | 2024-09-30 | Revised | 16 | Training Program |  | Provided initial and annual training and maintained training records for a minimum of three years | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide initial and annual training to all employees in safety procedures in the event of a release or threatened release of a hazardous material or failure to document and maintain training records for a minimum of three years. |  |  | OBSERVATION: The business failed to provide initial and annual training to all employees in safety procedures in the event of a release or threatened release of a hazardous material including familiarity with the emergency response plan or failure to document and maintain training records for a minimum of three years. CORRECTIVE ACTION: Establish and electronically submit an employee training program containing provisions to ensure initial and annual training for all employees in safety procedures in the event of a release or threatened release of a hazardous material and document and maintain training records for a minimum of three years. | OBSERVATION: The business failed to provide initial and annual training to all employees in safety procedures in the event of a release or threatened release of a hazardous material; or failed to document and maintains training records for a minimum of three years. CORRECTIVE ACTION: Establish and electronically submit an employee training program containing provisions for training applicable staff in release reporting procedures. Submit documentation to the unified program agency demonstrating appropriate personnel have received initial training and maintain ongoing annual training records for a minimum of three years. | OBSERVATION: The business did not provide one or more of the following: initial employee training, adequate employee training, annual employee training and/or maintain records of employee training. CORRECTIVE ACTION: Provide all employees with required training that includes: safe handling hazardous materials, emergency response procedures, and proper use of response equipment. Maintain records of training available for 3 years. |  |  |  |  | Yes
Business Plan Program | Administration/Documentation | 1010014 |  |  | Agricultural Handler Emergency Response Plan | Failure to electronically submit the emergency response plan and procedures when not meeting the agricultural handler exemption requirements. | 19 CCR 4 2670, 2671; HSC 6.95 25507.1(a), 25508(a)(1) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 18 | Agricultural Handlers |  | Agricultural handler exemption requirements are met when not submitting an emergency response plan | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit the emergency response plan and procedures when not meeting the agricultural handler exemption requirements. |  |  | OBSERVATION: Agricultural facility did not comply with one or more of the following requirement: annually submit a business plan, post required signs on buildings and/or provide required training to employees. When not meeting all of these requirements, an emergency response plan is required to be established and electronically submitted. CORRECTIVE ACTION: Establish and electronically submit an emergency response plan. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010015 |  |  | Agricultural Handler Training Program | Failure to electronically submit the training program in safety procedures when not meeting the agricultural handler exemption requirements. | 19 CCR 4 2670, 2671; HSC 6.95 25507.1(a), 25508(a)(1) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 19 | Agricultural Handlers |  | Agricultural handler exemption requirements are met when not submitting a training program | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit the training program in safety procedures when not meeting the agricultural handler exemption requirements. |  |  | OBSERVATION: Agricultural facility did not comply with one or more of the following requirement: annually submit a business plan, post required signs on buildings and/or provide required training to employees. When not meeting all of these requirements, a training plan is required to be established and electronically submitted. CORRECTIVE ACTION: Establish and electronically submit a training plan. | [6 empty] | Yes
Business Plan Program | Operations/Maintenance | 1030001 |  |  | Agricultural handlers warning signs | Failure of agricultural handler to post warning signs on buildings where pesticides, petroleum, or fertilizers are stored, that are visible from any direction of probable approach, contain all required information, and are in appropriate language | 19 CCR 4 2670, 2671; HSC 6.95 25507.1(a)(2) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 20 | Agricultural Handlers |  | Warning signs posted on buildings where pesticides, petroleum, or fertilizers are stored | 88 | yes | yes | Yes | yes | yes | yes | yes | Minor | Yes |  | 30 | Failure of agricultural handler to post warning signs on buildings where pesticides, petroleum, or fertilizers are stored, that are visible from any direction of probable approach, contain all required information, and are in appropriate language |  |  | OBSERVATION: Owner/Operator failed to post warning signs on buildings where pesticides, petroleum, or fertilizers are stored that are visible from any direction of probable approach, contain all required information, and are in appropriate language. CORRECTIVE ACTION: Post warning signs on buildings where pesticides, petroleum, or fertilizers are stored, and meet all posting requirements. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010 |  |  | HMBP-Administration/Documentation - General | Administration/Documentation - General | 19 CCR 4 Multiple Sections; HSC 6.95 Multiple Sections | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 23 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes
Business Plan Program | Training | 1020 |  |  | HMBP-Training - General | Training - General | 19 CCR 4 Multiple Sections; HSC 6.95 Multiple Sections | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 25 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes
Business Plan Program | Operations/Maintenance | 1030 |  |  | HMBP-Operations/Maintenance - General | Operations/Maintenance - General | 19 CCR 4 Multiple Sections; HSC 6.95 Multiple Sections | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 27 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes
Business Plan Program | Release/Leaks/Spills | 1040 |  |  | HMBP-Release/Leaks/Spills - General | Release/Leaks/Spills - General | 19 CCR 4 Multiple Sections; HSC 6.95 Multiple Sections | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 29 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes
Business Plan Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 1050 |  |  | HMBP-Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 19 CCR 4 Multiple Sections; HSC 6.95 Multiple Sections | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 31 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes

## CalARP
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | CalARP Level 1 | CalARP Level 2 | CalARP Level 3 | CalARP Level 4
CalARP Program | Administration/Documentation | 5010001 |  |  | Applicability: Table 1 or 2 | Failure to comply with the provisions of 19 CCR 4.5 pursuant to the time frames identified in Section 2745.1(b) if a stationary source has a process with more than a threshold quantity of a regulated substance as listed in Tables 1 or 2 of Section 2770.5. | 19 CCR 4.5 2735.4(a)(1) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 1 | General | General Applicability | Complied with CalARP provisions when having a RS in a process listed in Table 1/2 | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to comply with the provisions of 19 CCR 4.5 pursuant to the time frames identified in Section 2745.1(b) if a stationary source has a process with more than a threshold quantity of a regulated substance as listed in Tables 1 or 2 of Section 2770.5. |  |  | OBSERVATION: The stationary source has a process with more than a threshold quantity of a regulated substance onsite as listed in Table 1/Table 2 and has not complied with the provisions of Title 19, Division 2, Chapter 4.5 by the date on which the regulated substance was first present in a process above the threshold quantity. CORRECTIVE ACTION: Contact the CUPA to determine adequate timelines for full implementation. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010002 |  |  | Applicability: Table 3 | Failure to comply with the appropriate provisions of 19 CCR 4.5 prior to the date in which a regulated substance is first present in a process above the listed threshold quantity, as listed in Table 3 of Section 2770.5. | 19 CCR 4.5 2735.4(a)(2) | 2020-10-01 | 2024-09-30 | 2024-09-30 | Revised | 2 | General | General Applicability | Complied with CalARP provisions when having a RS in a process listed in Table 3 | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to comply with the appropriate provisions of 19 CCR 4.5 prior to the date in which a regulated substance is first present in a process above the listed threshold quantity, as listed in Table 3 of Section 2770.5. |  |  | OBSERVATION: The stationary source has a process with more than a threshold quantity of a regulated substance onsite as listed in Table 3 and has not complied with the provisions of Title 19, Division 2, Chapter 4.5 by the date on which the regulated substance was first present in a process above the threshold quantity. CORRECTIVE ACTION: Contact the CUPA to determine adequate timelines for full implementation. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010003 |  |  | Applicability: Tables 1 or 2 and Table 3 | Failure to comply with the provisions of 19 CCR 4.5 pursuant to the time frames identified in Section 2745.1(b) if a stationary source has a process with more than a threshold quantity of a regulated substance as listed in Tables 1 or 2 and Table 3 of Section 2770.5. | 19 CCR 4.5 2735.4(a)(3) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 3 | General | General Applicability | Complied with CalARP provisions when having a RS in a process listed in Table 1/2 and 3 | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to comply with the provisions of 19 CCR 4.5 pursuant to the time frames identified in Section 2745.1(b) if a stationary source has a process with more than a threshold quantity of a regulated substance as listed in Tables 1 or 2 and Table 3 of Section 2770.5. |  |  | OBSERVATION: The stationary source has a process with more than a threshold quantity of a regulated substance onsite as listed in Table 1/Table 2/ and Table 3 and has not complied with the provisions of Title 19, Division 2, Chapter 4.5 by the date on which the regulated substance was first present in a process above the threshold quantity. CORRECTIVE ACTION: Contact the CUPA to determine adequate timelines for full implementation. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010004 |  |  | General Requirements: Risk Management Plan Coordination | Failure of the owner or operator of a stationary source to closely coordinate with the UPA to implement the requirements of 19 CCR 4.5 and to determine the appropriate level of documentation required for a Risk Management Plan to comply with Sections 2745.3 through 2745.9. | 19 CCR 4.5 2735.5(a) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 4 | General | Coordination | Closely coordinated with the UPA to implement the CalARP requirements | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator of a stationary source to closely coordinate with the UPA to implement the requirements of 19 CCR 4.5 and to determine the appropriate level of documentation required for a Risk Management Plan to comply with Sections 2745.3 through 2745.9. |  |  | OBSERVATION: The owner/operator of the stationary source failed to closely coordinate with the CUPA to implement the requirements of Title 19, Division 2, Chapter 4.5 and to determine the appropriate level of documentation required for a Risk Management Plan to comply with sections 2745.3 through 2745.9. CORRECTIVE ACTION: Contact the CUPA to coordinate implementation of the requirements and to determine the appropriate level documentation required for a Risk Management Plan. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010006 |  |  | General Requirements: Program 1 Requirements - Emergency Response | Failure to ensure that response actions have been coordinated with local emergency planning and response agencies | 19 CCR 4.5 2735.5(d)(3) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 5 | General | Coordination | Ensured response actions have been coordinated with local emergency planning and response agencies. | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that response actions have been coordinated with local emergency planning and response agencies |  |  | OBSERVATION: The owner/operator of the stationary source failed to ensure that response actions have been coordinated with local emergency planning and response agencies. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that response actions have been coordinated with local emergency planning and response agencies. | [6 empty] | Yes | No | No | No
CalARP Program | Administration/Documentation | 5010009 |  |  | CalARP Program Management System: Program Level 2 or 3 | Failure to develop a management system to oversee the implementation of the risk management program elements. | 19 CCR 4.5 2735.6(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 6 | General | Management System - Program Level 2 or 3 | Developed a management system to oversee the implementation of the risk management program elements. | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop a management system to oversee the implementation of the risk management program elements. |  |  | OBSERVATION: The owner/operator of the stationary source failed to develop a management system to oversee the implementation of the risk management program elements. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating a management system to oversee the implementation of the risk management program elements has been developed. | [6 empty] | No | Yes | Yes | No
CalARP Program | Administration/Documentation | 5010010 |  |  | CalARP Program Management System: Program Level 2 or 3 - Overall Responsibility | Failure to assign a qualified person or position who has the overall responsibility for the development, implementation, and integration of the risk management program elements. | 19 CCR 4.5 2735.6(b) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 7 | General | Management System - Program Level 2 or 3 | Assigned a qualified person or position who has the overall responsibility for the RMP elements. | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to assign a qualified person or position who has the overall responsibility for the development, implementation, and integration of the risk management program elements. |  |  | OBSERVATION: The owner/operator of the stationary source failed to assign a qualified person or position who has the overall responsibility for the development, implementation, and integration of the risk management program elements. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating a qualified person or position who has the overall responsibility for the development, implementation, and integration of the risk management program elements has been assigned. | [6 empty] | No | Yes | Yes | No
CalARP Program | Administration/Documentation | 5010011 |  |  | CalARP Program Management System: Program Level 2 or 3 - Org Chart | Failure to document the following when responsibility for implementing individual requirements of 19 CCR 4.5 is assigned to persons other than the person identified in 19 CCR section 2735.6(b): 1. Names or positions. 2. Lines of authority defined through an organization chart or similar document. | 19 CCR 4.5 2735.6(c) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 8 | General | Management System - Program Level 2 or 3 | Documented the names or positions and lines of authority through an organization chart or document. | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to document the following when responsibility for implementing individual requirements of 19 CCR 4.5 is assigned to persons other than the person identified in 19 CCR section 2735.6(b): 1. Names or positions. 2. Lines of authority defined through an organization chart or similar document. |  |  | OBSERVATION: The owner/operator of the stationary source failed to document the names or positions and lines of authority defined through an organization chart or similar document when responsibility for implementing individual requirements of 19 CCR 4.5 is assigned to persons other than the qualified person or position who has the overall responsibility for the development, implementation, and integration of the risk management program elements. CORRECTIVE ACTION: Submit a copy of the organization chart or similar document to the CUPA defining the names or positions and lines of authority of the person(s) responsible for implementing individual requirements of the risk program elements. | [6 empty] | No | Yes | Yes | No
CalARP Program | Administration/Documentation | 5010005 |  |  | General Requirements: Risk Management Plan - Program Level 1 | Failure to submit an RMP which includes all requirements described in Sections 2745.3 through 2745.5 and 2745.8 through 2745.9. | 19 CCR 4.5 2735.5(b)(1), 2735.5(d), 2745.1(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 9 | RMP Components and Submission | RMP Submission - Program Level 1 | Submitted a RMP which includes all requirements in Section 2745.3 to 2745.5 and 2745.8 to 2745.9 | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit an RMP which includes all requirements described in Sections 2745.3 through 2745.5 and 2745.8 through 2745.9. |  |  | OBSERVATION: The owner/operator of the stationary source failed to submit a Risk Management Plan which includes all requirements described in Sections 2745.3 through 2745.5 and 2745.8 through 2745.9. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan to the CUPA that includes all requirements described in Sections 2745.3 through 2745.5 and 2745.8 through 2745.9. | [6 empty] | Yes | No | No | No
CalARP Program | Administration/Documentation | 5010007 |  |  | General Requirements: Risk Management Plan - Program Level 2, 3, or 4 | Failure to submit an RMP which includes all requirements described in Sections 2745.3 through 2745.9. | 19 CCR 4.5 2735.5(b)(1), 2745.1(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 10 | RMP Components and Submission | RMP Submission - Program Level 2, 3, or 4 | Submitted a RMP which includes all requirements in Section 2745.3 through 2745.9 | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit an RMP which includes all requirements described in Sections 2745.3 through 2745.9. |  |  | OBSERVATION: The owner/operator of the stationary source failed to submit a Risk Management Plan which includes all requirements described in Sections 2745.3 through 2745.9. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan to the CUPA that includes all requirements described in Sections 2745.3 through 2745.9. | [6 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010018 |  |  | Submission: Risk Management Plan Existing Stationary Source - Table 3 | Failure of a stationary source to submit a Risk Management Plan to the UPA after the owner or operator has received a notice from the UPA requesting submission of a Risk Management Plan. | CHSC 25536(b) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 11 | RMP Components and Submission | RMP Submission | RMP submitted to UPA after request to submit was received | 57 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of a stationary source to submit a Risk Management Plan to the UPA after the owner or operator has received a notice from the UPA requesting submission of a Risk Management Plan. |  |  | OBSERVATION: Owner/Operator failed to submit a Risk Management Plan (RMP) to the UPA after being notified by the UPA to submit the RMP. CORRECTIVE ACTION: Complete and submit RMP to the UPA by [specify compliance date]. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010016 |  |  | Submission to USEPA: Risk Management Plan - Table 1 or 2 | Failure to submit the RMP information required by the USEPA to the USEPA per the schedule below: 1. Three years after the date on which a regulated substance is first listed under Section 68.130, Part 68, Title 40 of CFR; or 2. The date on which a regulated substance is first present in a process, above the threshold quantity, as listed on Section 2770.5 Table 1 or 2. | 19 CCR 4.5 2745.1(b)(1), 2745.1(b)(2) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 12 | RMP Components and Submission | RMP Submission | Submitted the RMP information required by the USEPA to the USEPA | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to submit the RMP information required by the USEPA to the USEPA per the schedule below: 1. Three years after the date on which a regulated substance is first listed under Section 68.130, Part 68, Title 40 of CFR; or 2. The date on which a regulated substance is first present in a process, above the threshold quantity, as listed on Section 2770.5 Table 1 or 2. |  |  | OBSERVATION: The owner/operator failed to submit the Risk Management Plan information required by the USEPA to the USEPA within three years after the date on which a regulated substance is first listed under Section 68.130, Part 68, Title 40 of CFR. CORRECTIVE ACTION: Submit the Risk Management Plan information required by the USEPA to the USEPA. | OBSERVATION: The owner/operator failed to submit the Risk Management Plan information required by the USEPA to the USEPA prior to the date on which a regulated substance is first present in a process, above the threshold quantity, as listed on Section 2770.5 Table 1 or 2. CORRECTIVE ACTION: Submit the Risk Management Plan information required by the USEPA to the USEPA. | [5 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010017 |  |  | Submission to UPA: Risk Management Plan - Table 1 or 2 | Failure to submit a copy of the USEPA required RMP information according to the time frame set forth in 2745.1(b) to the UPA. | 19 CCR 4.5 2745.1(c) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 13 | RMP Components and Submission | RMP Submission | Submitted the RMP information required by the USEPA to the UPA within required time frame | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to submit a copy of the USEPA required RMP information according to the time frame set forth in 2745.1(b) to the UPA. |  |  | OBSERVATION: The owner/operator failed to submit the Risk Management Plan information required by the USEPA to the UPA within three years after the date on which a regulated substance is first listed under Section 68.130, Part 68, Title 40 of CFR. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan information required by the USEPA to the UPA. | OBSERVATION: The owner/operator failed to submit the RMP information required by the USEPA to the CUPA prior to the date on which a regulated substance is first present in a process, above the threshold quantity, as listed on Section 2770.5 Table 1 or 2. CORRECTIVE ACTION: Submit a copy of the RMP information required by the USEPA to the CUPA. | [5 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010020 |  |  | Submission: Risk Management Plan Classified Information | Failure to exclude classified information from the Risk Management Plan. | 19 CCR 4.5 2745.1(h) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 15 | RMP Components and Submission | RMP Submission | Excluded classified information from the RMP | 44 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to exclude classified information from the Risk Management Plan. |  |  | OBSERVATION: The owner/operator failed to exclude classified information in the Risk Management Plan. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan to the CUPA with an annex for classified information. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010021 |  |  | Risk Management Plan Review Process: Consultation and Review - Certified Complete by Qualified Person | Failure to ensure that the Risk Management Plan is certified complete by a qualified person and the stationary source owner or operator. | 19 CCR 4.5 2745.2(a) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 16 | RMP Components and Submission | RMP Submission | Ensured that the RMP is certified complete by a qualified person and the owner or operator | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that the Risk Management Plan is certified complete by a qualified person and the stationary source owner or operator. |  |  | OBSERVATION: The owner/operator failed to ensure that the Risk Management Plan is certified complete by a qualified person and the stationary source owner or operator. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the Risk Management Plan has been certified complete by a qualified person and the stationary source owner or operator. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010023 |  |  | RMP Certification: Program Level 1 | Failure to submit in the Risk Management Plan the certification statement provided in Section 2735.5(d)(4) | 19 CCR 4.5 2745.9(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 17 | RMP Components and Submission | RMP Certification - Program Level 1 | Submitted in the RMP the required certification statement (Prog 1) | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit in the Risk Management Plan the certification statement provided in Section 2735.5(d)(4) |  |  | OBSERVATION: The owner/operator failed to submit in the Risk Management Plan the certification statement provided in Section 2735.5(d)(4). CORRECTIVE ACTION: Submit the certification statement provided in Section 2735.5(d)(4) to the CUPA. | [6 empty] | Yes | No | No | No
CalARP Program | Administration/Documentation | 5010024 |  |  | RMP Certification: Program Level 2, 3, or 4 | Failure to submit in the Risk Management Plan a single certification that, to the best of the signer’s knowledge, information, and belief formed after reasonable inquiry, the information submitted is true, accurate, and complete. | 19 CCR 4.5 2745.9(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 18 | RMP Components and Submission | RMP Certification - Program Level 2, 3, or 4 | Submitted in the RMP the required certification statement (Prog 2, 3, or 4) | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit in the Risk Management Plan a single certification that, to the best of the signer’s knowledge, information, and belief formed after reasonable inquiry, the information submitted is true, accurate, and complete. |  |  | OBSERVATION: The owner/operator failed to submit in the Risk Management Plan a single certification that, to the best of the signer’s knowledge, information, and belief formed after reasonable inquiry, the information submitted is true, accurate, and complete. CORRECTIVE ACTION: Submit a single certification to the CUPA that, to the best of the signer’s knowledge, information, and belief formed after reasonable inquiry, the information submitted is true, accurate, and complete. | [6 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010025 |  |  | RMP Updates: Table 1 or 2 | Failure to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the UPA as follows: 1. At least once every five years from the date of its initial submission or most recent update required by section 2745.10(a)(2) through (7); 2. No later than three years after a newly regulated substance is first listed by the United States Environmental Protection Agency; 3. No later than the date on which a new regulated substance is first present in an already covered process above a threshold quantity; 4. No later than the date on which a regulated substance is first present above a threshold quantity in a new process; 5. Within six months of a change that requires a revised process hazard analysis or hazard review. 6. Within six months of a change that requires a revised offsite consequence analysis as provided in section 2750.7; 7. Within six months of a change that alters the program level that applied to any covered process. | 19 CCR 4.5 2745.10(a) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 19 | RMP Components and Submission | RMP Updates | Revised, updated, and submitted the RMP to the USEPA and UPA per required timelines (Table 1 or 2) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the UPA as follows: 1. At least once every five years from the date of its initial submission or most recent update required by section 2745.10(a)(2) through (7); 2. No later than three years after a newly regulated substance is first listed by the United States Environmental Protection Agency; 3. No later than the date on which a new regulated substance is first present in an already covered process above a threshold quantity; 4. No later than the date on which a regulated substance is first present above a threshold quantity in a new process; 5. Within six months of a change that requires a revised process hazard analysis or hazard review. 6. Within six months of a change that requires a revised offsite consequence analysis as provided in section 2750.7; 7. Within six months of a change that alters the program level that applied to any covered process. |  |  | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the UPA at least once every five years from the date of its initial submission or most recent update required by Section 2745.10(a)(2) through (7). CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the UPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA no later than three years after a newly regulated substance is first listed by the United States Environmental Protection Agency. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA no later than the date on which on which a new regulated substance is first present in an already covered process above a threshold quantity. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA no later than the date on which a regulated substance is first present above a threshold quantity in a new process. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA within six months of a change that requires a revised process hazard analysis or hazard review. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA within six months of a change that requires a revised offsite consequence analysis as provided in Section 2750.7. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA within six months of a change that alters the program level that applied to any covered process. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010026 |  |  | RMP Updates: Table 3 | Failure to revise, update, and submit the Risk Management Plan to the UPA as follows: 1. At least once every five years from the date of its initial submission or most recent update required by section 2745.10(b)(2) through (7); 2. No later than three years after a newly regulated substance is first listed by the California Office of Emergency Services. 3. No later than the date on which a new regulated substance is first present in an already covered process above a threshold quantity; 4. No later than the date on which a regulated substance is first present above a threshold quantity in a new process; 5. Within six months of a change that requires a revised process hazard analysis or hazard Review. 6. Within six months of a change that requires a revised offsite consequence analysis as provided in section 2750.7; 7. Within six months of a change that alters the program level that applied to any covered process. | 19 CCR 4.5 2745.10(b) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 20 | RMP Components and Submission | RMP Updates | Revised, updated, and submitted the RMP to the USEPA and UPA per required timelines (Table 3) | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to revise, update, and submit the Risk Management Plan to the UPA as follows: 1. At least once every five years from the date of its initial submission or most recent update required by section 2745.10(b)(2) through (7); 2. No later than three years after a newly regulated substance is first listed by the California Office of Emergency Services. 3. No later than the date on which a new regulated substance is first present in an already covered process above a threshold quantity; 4. No later than the date on which a regulated substance is first present above a threshold quantity in a new process; 5. Within six months of a change that requires a revised process hazard analysis or hazard Review. 6. Within six months of a change that requires a revised offsite consequence analysis as provided in section 2750.7; 7. Within six months of a change that alters the program level that applied to any covered process. |  |  | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the UPA at least once every five years from the date of its initial submission or most recent update required by section 2745.10(b)(2) through (7). CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the UPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA no later than three years after a newly regulated substance is first listed by the California Emergency Management Agency. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA no later than the date on which on which a new regulated substance is first present in an already covered process above a threshold quantity. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA no later than the date on which a regulated substance is first present above a threshold quantity in a new process. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA within six months of a change that requires a revised process hazard analysis or hazard review. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA within six months of a change that requires a revised offsite consequence analysis as provided in Section 2750.7. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA within six months of a change that alters the program level that applied to any covered process. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010027 |  |  | RMP Updates: Table 1 or 2 De-registration | Failure to submit a de-registration to the United States Environmental Protection Agency and the UPA within six months indicating that the stationary source is no longer covered | 19 CCR 4.5 2745.10(c) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 21 | RMP Components and Submission | RMP Updates | Submitted a de-registration to the USEPA and UPA within six months of the RS removal. | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a de-registration to the United States Environmental Protection Agency and the UPA within six months indicating that the stationary source is no longer covered |  |  | OBSERVATION: The owner/operator failed to submit a de-registration to the United States Environmental Protection Agency and the UPA within six months indicating that the stationary source is no longer covered. CORRECTIVE ACTION: Submit a copy of the de-registration to the United States Environmental Protection Agency and the UPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010028 |  |  | RMP Updates: Table 3 De-registration | Failure to submit a de-registration to the UPA within six months indicating that the stationary source is no longer covered. | 19 CCR 4.5 2745.10(d) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 22 | RMP Components and Submission | RMP Updates | Submitted a de-registration to the UPA within six months of the RS removal. | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a de-registration to the UPA within six months indicating that the stationary source is no longer covered. |  |  | OBSERVATION: The owner/operator failed to submit a de-registration to the UPA within six months indicating that the stationary source is no longer covered. CORRECTIVE ACTION: Submit a copy of the de-registration to the UPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010029 |  |  | RMP Updates: Change of Owner or Operator | Failure to contact the UPA within 30 days of a change of owner or operator to update the registration information. | 19 CCR 4.5 2745.10(f) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 23 | RMP Components and Submission | RMP Updates | Contacted the UPA within 30 days of a change of owner or operator to update the registration | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to contact the UPA within 30 days of a change of owner or operator to update the registration information. |  |  | OBSERVATION: The owner/operator failed to contact the UPA within 30 days of a change of owner or operator to update the registration information. CORRECTIVE ACTION: Update the registration information and submit a copy to the UPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010030 |  |  | Required RMP Corrections: New Accident History Information | Failure to correct and submit the data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l), for any accidental release meeting the five year accident history reporting criteria of Section 2750.9, with respect to that accident within six months of the release or by the time the Risk Management Plan is updated under Section 2745.10, whichever is earlier. | 19 CCR 4.5 2745.10.5(a) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 24 | RMP Components and Submission | RMP Corrections | Corrected and submitted required RMP data after accident/incident investigation | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to correct and submit the data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l), for any accidental release meeting the five year accident history reporting criteria of Section 2750.9, with respect to that accident within six months of the release or by the time the Risk Management Plan is updated under Section 2745.10, whichever is earlier. |  |  | OBSERVATION: The owner/operator failed to correct and submit the data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l), for any accidental release meeting the five year accident history reporting criteria of Section 2750.9, with respect to that accident within six months of the release. CORRECTIVE ACTION: Submit a copy of the revised data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l) to the UPA. | OBSERVATION: The owner/operator failed to correct and submit the data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l) with respect to that accident by the time the Risk Management Plan is to be updated under Section 2745.10. CORRECTIVE ACTION: Submit a copy of the revised data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l) to the CUPA. | [5 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010031 |  |  | Required RMP Corrections: Emergency Contact Information | Failure to correct and submit the emergency contact information in the Risk Management Plan required under Section 2740.1(d)(6) within one month of any change | 19 CCR 4.5 2745.10.5(b) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 25 | RMP Components and Submission | RMP Corrections | Corrected and submitted the emergency contact information in the RMP within one month of any change | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to correct and submit the emergency contact information in the Risk Management Plan required under Section 2740.1(d)(6) within one month of any change |  |  | OBSERVATION: The owner/operator failed to correct and submit the emergency contact information in the Risk Management Plan required under Section 2740.1(d)(6) within one month of any change. CORRECTIVE ACTION: Correct and submit a copy of the emergency contact information in the Risk Management Plan required under Section 2740.1(d)(6) to the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010032 |  |  | Covered Process Modification: Prenotification | Failure to notify the UPA in writing of the intent to modify the stationary source at least five calendar days before implementing any modifications or no later than 48 hours following the modification if prenotification is not reasonable. | 19 CCR 4.5 2745.11(a)(1) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 26 | RMP Components and Submission | Covered Process Modification | Notified the UPA in writing at least five calendar days before implementing any modifications | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to notify the UPA in writing of the intent to modify the stationary source at least five calendar days before implementing any modifications or no later than 48 hours following the modification if prenotification is not reasonable. |  |  | OBSERVATION: The owner/operator failed to notify the UPA in writing of the intent to modify the stationary source at least five calendar days before implementing any modifications or no later than 48 hours following the modification if prenotification is not reasonable. CORRECTIVE ACTION: Submit a statement to the UPA demonstrating how the owner/operator will notify the UPA in writing of the intent to modify the stationary source at least five calendar days before implementing any modifications or no later than 48 hours following the modification if prenotification is not reasonable. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010033 |  |  | Covered Process Modification: Establish Procedures to Manage Proposed Modification | Failure to establish procedures to manage the proposed modification, which shall be substantially similar to the procedures specified in Sections 2760.6 and 2760.7, and notify the UPA that the procedures have been established. | 19 CCR 4.5 2745.11(a)(2) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 27 | RMP Components and Submission | Covered Process Modification | Established procedures to manage a proposed modification and notified UPA | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to establish procedures to manage the proposed modification, which shall be substantially similar to the procedures specified in Sections 2760.6 and 2760.7, and notify the UPA that the procedures have been established. |  |  | OBSERVATION: The owner/operator failed to establish procedures to manage the proposed modification, which shall be substantially similar to the procedures specified in Sections 2760.6 and 2760.7, and notify the UPA that the procedures have been established. CORRECTIVE ACTION: Establish procedures to manage the proposed modification and notify the UPA in writing that this was completed. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010262 |  |  | Covered Process Modification: Revise Appropriate Documents within 60 Days | Failure to revise the appropriate documents as required pursuant to section 2745.11(a), expeditiously, but not later than 60 days from the date of the stationary source modification. | 19 CCR 4.5 2745.11(b) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 28 | RMP Components and Submission | Covered Process Modification | Revised appropriate documents within 60 days after covered process modification | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to revise the appropriate documents as required pursuant to section 2745.11(a), expeditiously, but not later than 60 days from the date of the stationary source modification. |  |  | OBSERVATION: Owner/operator failed to revise the appropriate documents as required pursuant to section 2745.11(a), expeditiously, but not later than 60 days from the date of the stationary source modification. CORRECTIVE ACTION: Consult with UPA to determine which documents must be revised and complete document revisions. Submit documentation of revisions. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010034 |  |  | Certificate of Occupancy | Failure of a new or modified stationary source to comply with Section 65850.2(b) of the Government Code prior to the issuance of a certificate of occupancy | 19 CCR 4.5 2745.12 | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 29 | RMP Components and Submission | Certificate of Occupancy | Complied with Government Code Section 65850.2(b) prior to issuance of a certificate of occupancy | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a new or modified stationary source to comply with Section 65850.2(b) of the Government Code prior to the issuance of a certificate of occupancy |  |  | OBSERVATION: The owner/operator failed to comply with Section 65850.2(b) of the Government Code prior to the issuance of a certificate of occupancy. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating you have complied with Section 65850.2(b) of the Government Code. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010022 |  |  | Risk Management Plan Review Process: Deficiency Notice | Failure to correct deficiencies within 60 calendar days from receipt of the notification of Risk Management Plan deficiencies. | 19 CCR 4.5 2745.2(b)(1) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 30 | RMP Components and Submission | RMP Review | Corrected deficiencies within 60 calendar days from receipt of the notification of RMP deficiencies | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to correct deficiencies within 60 calendar days from receipt of the notification of Risk Management Plan deficiencies. |  |  | OBSERVATION: The owner/operator failed to correct deficiencies within 60 calendar days from receipt of the notification of Risk Management Plan deficiencies. CORRECTIVE ACTION: Revise and submit a copy of the Risk Management Plan to the CUPA that includes all corrections identified in the deficiency notice. | OBSERVATION: The owner/operator failed to correct deficiencies within 90 calendar days (60 calendar days plus a one time 30 calendar days extension) from receipt of the notification of Risk Management Plan deficiencies. CORRECTIVE ACTION: Revise and submit a copy of the Risk Management Plan to the CUPA that includes all corrections identified in the deficiency notice. | [5 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010008 |  |  | General Requirements: Risk Management Plan Registration | Failure to include a registration in the Risk Management Plan that reflects all covered processes. | 19 CCR 4.5 2735.5(b)(2) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 31 | Registration |  | Included a registration in the RMP that reflects all covered processes | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to include a registration in the Risk Management Plan that reflects all covered processes. |  |  | OBSERVATION: The owner/operator of the stationary source failed to include a registration in the Risk Management Plan that reflects all covered processes. CORRECTIVE ACTION: Submit a copy of the registration to the CUPA that reflects all covered processes. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010012 |  |  | Registration: Table 1 or 2 | Failure to complete the registration information required in 2740.1(d) and submit it with the Risk Management Plan to the United States Environmental Protection Agency, with a copy provided to the UPA. | 19 CCR 4.5 2740.1(a) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 32 | Registration |  | Completed the registration information and submitted it with the RMP to the USEPA and the UPA | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete the registration information required in 2740.1(d) and submit it with the Risk Management Plan to the United States Environmental Protection Agency, with a copy provided to the UPA. |  |  | OBSERVATION: The owner/operator of the stationary source failed to complete the registration information required in Section 2740.1(d) and submit it with the Risk Management Plan to the United States Environmental Protection Agency, with a copy provided to the CUPA. CORRECTIVE ACTION: Complete and submit a copy of the registration information required in Section 2740.1(d) to the USEPA and the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/ Documentation | 5010013 |  |  | Registration: Table 3 | Failure to complete the registration information required in section 2740.1(d) and submit it with the Risk Management Plan to the UPA. | 19 CCR 4.5 2740.1(b) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 33 | Registration |  | Completed the registration information and submitted it with the RMP to the UPA | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete the registration information required in section 2740.1(d) and submit it with the Risk Management Plan to the UPA. |  |  | OBSERVATION: The owner/operator of the stationary source failed to complete the registration information required in Section 2740.1(d) and submit it with the Risk Management Plan to the CUPA. CORRECTIVE ACTION: Complete and submit a copy of the registration information required in section 2740.1(d) to the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010014 |  |  | Registration: UPA Request | Failure to submit a registration to the UPA prior to submittal of the Risk Management Plan upon request. | 19 CCR 4.5 2740.1(c) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 34 | Registration |  | Submitted a registration with a certification of accuracy to the UPA prior to submittal of the RMP | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to submit a registration to the UPA prior to submittal of the Risk Management Plan upon request. |  |  | OBSERVATION: The owner/operator of the stationary source failed to submit a registration with a certification of accuracy to the CUPA (Upon request) prior to submittal of the Risk Management Plan. CORRECTIVE ACTION: Complete and submit a copy of the registration information required in section 2740.1(d) with a certification of accuracy to the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010015 |  |  | Registration: Data | Failure to include the data required in 2740.1 (d)(1) through (d)(20) in the registration. | 19 CCR 4.5 2740.1(d) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 35 | Registration |  | Included the data required in Section 2740.1 (d)(1) through (d)(20) in the registration | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include the data required in 2740.1 (d)(1) through (d)(20) in the registration. |  |  | OBSERVATION: The owner/operator of the stationary source failed to include all the data required in Section 2740.1(d)(1) through (d)(20) in the registration. CORRECTIVE ACTION: Complete and resubmit a copy of the registration including all information required in Section 2740.1(d)(1) through (d)(20) to the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010035 |  |  | Hazard Assessment: Program Level 1 - Worst-Case Release Scenario | Failure to prepare a worst-case release scenario analysis as provided in Section 2750.3 | 19 CCR 4.5 2750.1 | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 36 | Hazard Assessment | General Applicability | Prepared a worst-case release scenario analysis | 47 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a worst-case release scenario analysis as provided in Section 2750.3 |  |  | OBSERVATION: The owner/operator failed to prepare a worst-case release scenario analysis. CORRECTIVE ACTION: Prepare the worst-case release scenario analysis as provided in Section 2750.3 and submit a copy to the UPA. | OBSERVATION: The owner/operator failed to prepare a worst-case release scenario analysis that complies with all requirements in Section 2750.3. CORRECTIVE ACTION: Revise and resubmit a copy of the worst-case release scenario analysis to the CUPA and ensure that it complies with all requirements in Section 2750.3. | [5 empty] | Yes | No | No | No
CalARP Program | Administration/Documentation | 5010036 |  |  | Hazard Assessment: Program Level 1 - Five-Year Accident History | Failure to complete the five-year accident history as provided in Section 2750.9 | 19 CCR 4.5 2750.1 | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 37 | Hazard Assessment | General Applicability | Completed the five-year accident history | 40 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete the five-year accident history as provided in Section 2750.9 |  |  | OBSERVATION: The owner/operator failed to complete the five-year accident history. CORRECTIVE ACTION: Prepare the five-year accident history as provided in Section 2750.9. and submit a copy to the UPA. | OBSERVATION: The owner/operator failed to complete the five-year accident history that complies with all requirements in Section 2750.9. CORRECTIVE ACTION: Revise and resubmit a copy of the five-year accident history to the CUPA and ensure that it complies with all requirements in Section 2750.9. | [5 empty] | Yes | No | No | No
CalARP Program | Administration/Documentation | 5010037 |  |  | Hazard Assessment: Program Level 2, 3, or 4 | Failure to comply with any of the following: 1. Offsite Consequence Analysis Parameters. (19 CCR 4.5 2750.2) 2. Worst-Case Release Scenario Analysis. (19 CCR 4.5 2750.3) 3. Alternative Release Scenario Analysis. (19 CCR 4.5 2750.4) 4. Defining Offsite Impacts to the Population. (19 CCR 4.5 2750.5) 5. Defining Offsite Impacts to the Environment. (19 CCR 4.5 2750.6) 6. Offsite Consequence Analysis Review and Update. (19 CCR 4.5 2750.7) 7. Offsite Consequence Analysis Documentation. (19 CCR 4.5 2750.8) 8. Five-year Accident History. (19 CCR 4.5 2750.9) | 19 CCR 4.5 2750.1 | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 38 | Hazard Assessment | General Applicability | Conducted a hazard assessment meeting the requirements of 2750.2-2750.9 | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to comply with any of the following: 1. Offsite Consequence Analysis Parameters. (19 CCR 4.5 2750.2) 2. Worst-Case Release Scenario Analysis. (19 CCR 4.5 2750.3) 3. Alternative Release Scenario Analysis. (19 CCR 4.5 2750.4) 4. Defining Offsite Impacts to the Population. (19 CCR 4.5 2750.5) 5. Defining Offsite Impacts to the Environment. (19 CCR 4.5 2750.6) 6. Offsite Consequence Analysis Review and Update. (19 CCR 4.5 2750.7) 7. Offsite Consequence Analysis Documentation. (19 CCR 4.5 2750.8) 8. Five-year Accident History. (19 CCR 4.5 2750.9) |  |  | OBSERVATION: The owner/operator failed to conduct a hazard assessment that complies with Sections 2750.2 through 2750.9. CORRECTIVE ACTION: Conduct a hazard assessment that complies with Sections 2750.2 through 2750.9 and submit a copy to the UPA. | OBSERVATION: The owner/operator failed to conduct a hazard assessment that complies with all requirements in Sections 2750.2 through 2750.9. CORRECTIVE ACTION: Revise and resubmit a copy of the hazard assessment to the CUPA and ensure that it complies with all requirements in Sections 2750.2 through 2750.9. | [5 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010119 |  |  | Record Keeping | Failure to maintain records supporting the implementation of 19 CCR 4.5 for five years unless otherwise provided in Article 6. | 19 CCR 4.5 2775.1 | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 39 | Other Requirements | Recordkeeping | Maintained records supporting the implementation of CalARP for five years unless otherwise provided | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain records supporting the implementation of 19 CCR 4.5 for five years unless otherwise provided in Article 6. |  |  | OBSERVATION: The owner/operator failed to maintain records supporting the implementation of 19 CCR 4.5 for five years unless otherwise provided in Article 6 of that chapter. CORRECTIVE ACTION: Submit a copy of the missing records to the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010120 |  |  | Technical Assistance - Coordination | Failure to closely coordinate with the UPA to ensure that appropriate technical standards are applied to the implementation of 19 CCR 4.5. | 19 CCR 4.5 2785.1 (a) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 40 | Other Requirements | Recordkeeping | Coordinated with UPA to ensure appropriate technical standards are applied to implement CalARP | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to closely coordinate with the UPA to ensure that appropriate technical standards are applied to the implementation of 19 CCR 4.5. |  |  | OBSERVATION: The owner/operator failed to closely coordinate with the UPA to ensure that appropriate technical standards are applied to the implementation of 19 CCR 4.5. CORRECTIVE ACTION: Coordinate with the UPA to ensure that appropriate technical standards are applied to the implementation of 19 CCR 4.5. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010121 |  |  | Technical Assistance - Request Assistance | Failure to request assistance from the UPA when necessary to address compliance with 19 CCR 4.5 or safety issues regarding unfamiliar processes. | 19 CCR 4.5 2785.1 (b) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 41 | Other Requirements | Recordkeeping | Requested assistance from the UPA when necessary to address compliance/safety issues with CalARP | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to request assistance from the UPA when necessary to address compliance with 19 CCR 4.5 or safety issues regarding unfamiliar processes. |  |  | OBSERVATION: The owner/operator failed to request assistance from the UPA when necessary to address compliance with 19 CCR 4.5 or safety issues regarding unfamiliar processes. CORRECTIVE ACTION: Coordinate with the UPA to address compliance with 19 CCR 4.5 or safety issues regarding unfamiliar processes. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010115 |  |  | Emergency Response Applicability (Non Responding): Program Level 2 or 3 | Failure of owner or operator of a stationary source whose employees will not respond to accidental releases of regulated substances to meet the following: 1. For stationary sources with any regulated toxic substances held in a process above the threshold quantity, the stationary source is included in the community emergency response plan developed under Section 11003 of Title 42 of the United States Code (USC), is included in the city or county Hazardous Materials Area plans, and/or is included in the business plan program, pursuant to Section 25507 of the Health & Safety Code. The owner or operator must document that response actions have been coordinated with the local fire department and hazardous materials response agencies; 2. For stationary sources with only regulated flammable substances held in a process above the threshold quantity, the owner or operator must document that response actions have been coordinated with the local fire department and hazardous materials response agencies; and, 3. Appropriate mechanisms and written procedures are in place to notify emergency responders when there is a need for a response. | 19 CCR 4.5 2765.1(b) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 42 | Emergency Response Program | Emergency Response Applicability | Stationary source whose employees will not respond to releases met all applicable requirements | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of owner or operator of a stationary source whose employees will not respond to accidental releases of regulated substances to meet the following: 1. For stationary sources with any regulated toxic substances held in a process above the threshold quantity, the stationary source is included in the community emergency response plan developed under Section 11003 of Title 42 of the United States Code (USC), is included in the city or county Hazardous Materials Area plans, and/or is included in the business plan program, pursuant to Section 25507 of the Health & Safety Code. The owner or operator must document that response actions have been coordinated with the local fire department and hazardous materials response agencies; 2. For stationary sources with only regulated flammable substances held in a process above the threshold quantity, the owner or operator must document that response actions have been coordinated with the local fire department and hazardous materials response agencies; and, 3. Appropriate mechanisms and written procedures are in place to notify emergency responders when there is a need for a response. |  |  | OBSERVATION: The owner/operator of a facility that does not respond to accidental releases of regulated substances failed to meet the following: If only regulated toxic substances, is included in the community emergency response plan, is included in the city or county Hazardous Materials Area plans, and/or is included in the business plan program, and/or the owner/operator failed to document that response actions have been coordinated with the local fire department and hazardous materials response agencies; If only regulated flammable substances, the owner or operator failed to document that response actions have been coordinated with the local fire department and hazardous materials response agencies; and/or appropriate mechanisms and written procedures are not in place to notify emergency responders when there is a need for a response. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has met the requirements noted above. | [6 empty] | No | Yes | Yes | No
CalARP Program | Administration/Documentation | 5010116 |  |  | Emergency Response Program (Responding): Program Level 2, 3, or 4 | Failure to develop, implement, and maintain at the stationary source an emergency response program that includes the following elements: 1. Procedures for informing and interfacing with the public and local emergency response agencies about accidental releases, emergency planning, and emergency response. 2. Documentation of proper first-aid and emergency medical treatment necessary to treat accidental human exposures. 3. Procedures and measures for emergency response after an accidental release of a regulated substance. 4. Procedures for the use of emergency response equipment and for its inspection, testing, and maintenance are developed by the stationary source. 5. Training for all employees in relevant procedures and relevant aspects of the Incident Command System. 6. Procedures to review and update the emergency response plan to reflect changes at the stationary source are developed and employees are informed of these changes. | 19 CCR 4.5 2765.2(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 43 | Emergency Response Program | Emergency Response Program - Responding | Responding facility developed and implemented an emergency response program | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement, and maintain at the stationary source an emergency response program that includes the following elements: 1. Procedures for informing and interfacing with the public and local emergency response agencies about accidental releases, emergency planning, and emergency response. 2. Documentation of proper first-aid and emergency medical treatment necessary to treat accidental human exposures. 3. Procedures and measures for emergency response after an accidental release of a regulated substance. 4. Procedures for the use of emergency response equipment and for its inspection, testing, and maintenance are developed by the stationary source. 5. Training for all employees in relevant procedures and relevant aspects of the Incident Command System. 6. Procedures to review and update the emergency response plan to reflect changes at the stationary source are developed and employees are informed of these changes. |  |  | OBSERVATION: The owner/operator failed to develop, implement, and maintain an emergency response (ER) program that addresses the following: procedures for informing and interfacing with the public and local ER agencies about releases, emergency planning, and emergency response; documentation of proper first-aid and emergency medical treatment needed to treat human exposures; procedures and measures for ER after a release of a regulated substance; procedures for the use of ER equipment and for its inspection, testing, and maintenance; training for all employees in procedures and aspects of the Incident Command System relevant to their responsibilities; procedures to review and update the emergency response plan to reflect changes at the stationary source, and how employees are to be informed of these changes. CORRECTIVE ACTION: Develop and submit an emergency response program to the CUPA that addresses all of the requirements noted above. | [6 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010117 |  |  | Emergency Response Program - (Responding): Coordination with the Community ERP - Program Level 2, 3, or 4 | Failure to coordinate the emergency response plan with the community emergency response plan developed under Section 11003 of Title 42 of the United States Code. | 19 CCR 4.5 2765.2(c) | 2020-10-01 | 2024-09-30 | 2024-09-30 | Revised | 44 | Emergency Response Program | Emergency Response Program - Responding | Coordinated the ERP with the community ERP | 42 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to coordinate the emergency response plan with the community emergency response plan developed under Section 11003 of Title 42 of the United States Code. |  |  | OBSERVATION: The owner/operator failed to coordinate the emergency response plan with the community emergency response plan developed under Section 11003 of Title 42 of the United States Code. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator coordinated the emergency response plan with the community emergency response plan developed under Section 11003 of Title 42 of the United States Code. | [6 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010118 |  |  | Emergency Response Program (Responding): Provide requested info to LEPC or ER officials - Program Level 2, 3, or 4 | Failure to promptly provide to the local emergency planning committee or emergency response officials information necessary for developing and implementing the community emergency response plan upon request. | 19 CCR 4.5 2765.2(c) | 2020-10-01 | 2024-09-30 | 2024-09-30 | Revised | 45 | Emergency Response Program | Emergency Response Program - Responding | Provided LEPC or ER officials information for developing and implementing the community ERP | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to promptly provide to the local emergency planning committee or emergency response officials information necessary for developing and implementing the community emergency response plan upon request. |  |  | OBSERVATION: The owner/operator failed to promptly provide to the local emergency planning committee or emergency response officials information necessary for developing and implementing the community emergency response plan upon request. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has provided to the local emergency planning committee or emergency response officials information necessary for developing and implementing the community emergency response plan upon request. | [6 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010038 |  |  | Program Level 2: Safety Information - General | Failure to compile and maintain the following up-to-date safety information related to the regulated substances, processes, and equipment: 1. Material Safety Data Sheets that meet the requirements of Section 5189 of Title 8 of CCR; 2. Maximum intended inventory of equipment in which the regulated substances are stored or processed; 3. Safe upper and lower temperatures, pressures, flows and compositions; 4. Equipment specifications; 5. Codes and standards used to design, build & operate the process. | 19 CCR 4.5 2755.1(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 46 | Program 2 Prevention Program | Safety Information | Compiled and maintained up-to-date safety information related to the RS, processes, and equipment | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to compile and maintain the following up-to-date safety information related to the regulated substances, processes, and equipment: 1. Material Safety Data Sheets that meet the requirements of Section 5189 of Title 8 of CCR; 2. Maximum intended inventory of equipment in which the regulated substances are stored or processed; 3. Safe upper and lower temperatures, pressures, flows and compositions; 4. Equipment specifications; 5. Codes and standards used to design, build & operate the process. |  |  | OBSERVATION: The owner/operator failed to compile and maintain the following up-to-date safety information related to the regulated substances, processes, and equipment: Material Safety Data Sheets related to the regulated substance(s); maximum intended inventory of equipment in which the regulated substances are stored or processed; safe upper and lower temperatures, pressures, flows and compositions; equipment specifications; Codes and standards used to design, build & operate the process. CORRECTIVE ACTION: Submit a copy of the following up-to-date safety information related to the regulated substances, processes, and equipment to the CUPA: Material Safety Data Sheets related to the regulated substance(s); maximum intended inventory of equipment in which the regulated substances are stored or processed; safe upper and lower temperatures, pressures, flows and compositions; equipment specifications; Codes and standards used to design, build & operate the process. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010039 |  |  | Program Level 2: Safety Information - Process Design | Failure to ensure that the process is designed in compliance with recognized and generally accepted good engineering practices. | 19 CCR 4.5 2755.1(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 47 | Program 2 Prevention Program | Safety Information | Ensured the process is designed in compliance with recognized and accepted engineering practices | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that the process is designed in compliance with recognized and generally accepted good engineering practices. |  |  | OBSERVATION: The owner/operator failed to ensure that the process is designed in compliance with recognized and generally accepted good engineering practices. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating you have ensured that the process is designed in compliance with recognized and generally accepted good engineering practices. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010040 |  |  | Program Level 2: Safety Information - Update | Failure to update the safety information if a major change occurs that makes the information inaccurate. | 19 CCR 4.5 2755.1(c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 48 | Program 2 Prevention Program | Safety Information | Updated the safety information when a major change occurs that makes the information inaccurate | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to update the safety information if a major change occurs that makes the information inaccurate. |  |  | OBSERVATION: The owner/operator failed to update the safety information when a major change occurred that made the information inaccurate. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating you have updated the safety information. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010041 |  |  | Program Level 2: Hazard Review - General | Failure to conduct a review of the hazards associated with the regulated substances, process, and procedures that identifies the following: 1. The hazards associated with the process and regulated substances; 2. Opportunities for equipment malfunctions or human errors that could cause an accidental release; 3. The safeguards used or needed to control the hazards or prevent equipment malfunction or human error; 4. Any steps used or needed to detect or monitor releases. | 19 CCR 4.5 2755.2(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 49 | Program 2 Prevention Program | Hazard Review | Conducted a review of the hazards associated with the RS, process, and procedures | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to conduct a review of the hazards associated with the regulated substances, process, and procedures that identifies the following: 1. The hazards associated with the process and regulated substances; 2. Opportunities for equipment malfunctions or human errors that could cause an accidental release; 3. The safeguards used or needed to control the hazards or prevent equipment malfunction or human error; 4. Any steps used or needed to detect or monitor releases. |  |  | OBSERVATION: The owner/operator failed to conduct a review of the hazards associated with the regulated substance(s), process(es), and procedures that identifies: the hazards associated with the process and regulated substances; opportunities for equipment malfunctions or human errors that could cause an accidental release; the safeguards used or needed to control the hazards or prevent equipment malfunction or human error; any steps used or needed to detect or monitor releases. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator conducted a review of the hazards associated with the regulated substance(s), process(es), and procedures that addresses all the requirements noted above. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010042 |  |  | Program Level 2: Hazard Review - Consultation | Failure to consult with the UPA to decide which hazard review methodology is best suited to determine and evaluate the hazards of the process being analyzed. | 19 CCR 4.5 2755.2(b) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 50 | Program 2 Prevention Program | Hazard Review | Consulted with the UPA to decide which hazard review methodology is best suited for the process | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to consult with the UPA to decide which hazard review methodology is best suited to determine and evaluate the hazards of the process being analyzed. |  |  | OBSERVATION: The owner/operator failed to consult with the UPA to decide which hazard review methodology is best suited to determine and evaluate the hazards of the process being analyzed. CORRECTIVE ACTION: Consult with the UPA to decide which hazard review methodology is best suited to determine and evaluate the hazards of the process being analyzed. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010123 |  |  | Program Level 2: Hazard Review - Team | Failure to perform the hazard review by a team familiar with process operations, including at least one employee who has experience and knowledge specific to the process being reviewed. | 19 CCR 4.5 2755.2(c) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 51 | Program 2 Prevention Program | Hazard Review | HR performed by team familiar with process and person with experience/knowledge specific to process | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform the hazard review by a team familiar with process operations, including at least one employee who has experience and knowledge specific to the process being reviewed. |  |  | OBSERVATION: The owner/operator failed to perform the hazard review with a team familiar with process operations, including at least one employee who has experience and knowledge specific to the process being reviewed. CORRECTIVE ACTION: Perform a hazard review with a team familiar with process operations and include at least one employee who has experience and knowledge specific to the process being reviewed. Submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010043 |  |  | Program Level 2: Hazard Review - Design, Fabrication, Operation | Failure to determine whether the process is designed, fabricated, and operated in accordance with applicable standards or rules. | 19 CCR 4.5 2755.2(c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 52 | Program 2 Prevention Program | Hazard Review | Determined the process is designed, fabricated, and operated in accordance with applicable standards | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to determine whether the process is designed, fabricated, and operated in accordance with applicable standards or rules. |  |  | OBSERVATION: The owner/operator failed to determine whether the process(es) /is/are/ designed, fabricated, and operated in accordance with applicable standards or rules. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating you have determined whether the process(es) /is/are/ designed, fabricated, and operated in accordance with applicable standards or rules. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010044 |  |  | Program Level 2: Hazard Review - External Events | Failure to include the consideration of external events, including seismic events. | 19 CCR 4.5 2755.2(d) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 53 | Program 2 Prevention Program | Hazard Review | Included the consideration of external events, including seismic events in the hazard review | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to include the consideration of external events, including seismic events. |  |  | OBSERVATION: The owner/operator failed to include the consideration of external events, including seismic events in the hazard review. CORRECTIVE ACTION: Submit a copy of the hazard review to the CUPA that includes the consideration of external events, including seismic events. | OBSERVATION: The owner/operator failed to include the consideration of seismic events in the hazard review. CORRECTIVE ACTION: Submit a copy of the hazard review to the CUPA that includes the consideration of seismic events. | [5 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010045 |  |  | Program Level 2: Hazard Review - Recommendations/Resolutions | Failure to address the following in the hazard review: 1. Document the results of the hazard review and ensure problems identified are resolved; 2. Complete these actions on a timetable agreed upon with the UPA, or within two and one-half (2.5) years of performing the hazard review, or the next planned turnaround, for those items that require a turnaround; 3. Document the final resolution taken to address each recommendation and actual completion date. | 19 CCR 4.5 2755.2(e) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 54 | Program 2 Prevention Program | Hazard Review | Hazard review results and resolutions documented, and completed within required time frame | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to address the following in the hazard review: 1. Document the results of the hazard review and ensure problems identified are resolved; 2. Complete these actions on a timetable agreed upon with the UPA, or within two and one-half (2.5) years of performing the hazard review, or the next planned turnaround, for those items that require a turnaround; 3. Document the final resolution taken to address each recommendation and actual completion date. |  |  | OBSERVATION: The owner/operator failed to document the results of the hazard review, document final resolutions taken, or complete these actions within required time frame. CORRECTIVE ACTION: Submit a copy of the results of the hazard review to the UPA, including documentation demonstrating that problems identified are being resolved. | OBSERVATION: The owner/operator failed to ensure that problems identified in the hazard review were resolved. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that problems identified in the hazard review are being resolved. | OBSERVATION: The owner/operator failed to document the resolution(s) taken to address the hazard review recommendations). CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the resolutions taken to address the hazard review recommendations have been documented. |  |  |  |  | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010046 |  |  | Program Level 2: Hazard Review - 5 Year Update | Failure to update and revalidate the hazard review at least once every 5 years. | 19 CCR 4.5 2755.2(f) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 55 | Program 2 Prevention Program | Hazard Review | Updated and revalidated the hazard review at least once every 5 years | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to update and revalidate the hazard review at least once every 5 years. |  |  | OBSERVATION: The owner/operator failed to update and revalidate the hazard review at least once every 5 years. CORRECTIVE ACTION: Update and revalidate the hazard review and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010047 |  |  | Program Level 2: Hazard Review - Major Change | Failure to update and revalidate the hazard review whenever a major change in the process occurs. | 19 CCR 4.5 2755.2(f) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 56 | Program 2 Prevention Program | Hazard Review | Updated and revalidated the hazard review whenever a major change in the process occurs | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to update and revalidate the hazard review whenever a major change in the process occurs. |  |  | OBSERVATION: The owner/operator failed to update and revalidate the hazard review resulting from a major change in the process. CORRECTIVE ACTION: Update the hazard review and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010048 |  |  | Program Level 2: Hazard Review - Prestart up | Failure to resolve all issues identified in the hazard review before startup of the changed process. | 19 CCR 4.5 2755.2(f) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 57 | Program 2 Prevention Program | Hazard Review | Resolved all issues identified in the hazard review before startup of the changed process | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to resolve all issues identified in the hazard review before startup of the changed process. |  |  | OBSERVATION: The owner/operator failed to resolve all issues identified in the hazard review before startup of the changed process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that all issues identified in the hazard review have been resolved. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010124 |  |  | Program Level 2: Hazard Review - Revalidation | Failure to revalidate the hazard review only once between full hazard reviews, unless the UPA agrees in writing that a full hazard review is unwarranted. | 19 CCR 4.5 2755.2(g) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 58 | Program 2 Prevention Program | Hazard Review | Hazard review only revalidated once between full hazard reviews unless UPA agrees in writing | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to revalidate the hazard review only once between full hazard reviews, unless the UPA agrees in writing that a full hazard review is unwarranted. |  |  | OBSERVATION: The owner/operator revalidated the hazard review more than once between hazard reviews. CORRECTIVE ACTION: Perform a full hazard review and submit a copy to the UPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/ Documentation | 5010125 |  |  | Program Level 2: Hazard Review - Retention | Failure to retain hazard reviews and updates or revalidations for each process covered by 19 CCR 4.5 section 2755.2, as well as the documented resolution of recommendations described in 19 CCR 4.5 section 2755.2(e) for the life of the process. | 19 CCR 4.5 2755.2(h) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 59 | Program 2 Prevention Program | Hazard Review | Retained all HR's, updates/revalidations, and documented resolution of recommendations | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain hazard reviews and updates or revalidations for each process covered by 19 CCR 4.5 section 2755.2, as well as the documented resolution of recommendations described in 19 CCR 4.5 section 2755.2(e) for the life of the process. |  |  | OBSERVATION: The owner/operator failed to retain hazard reviews and updates/revalidations for each process and documented resolution of recommendations for the life of the process. CORRECTIVE ACTION: Submit any missing hazard reviews and updates/revalidations and documented resolutions to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010049 |  |  | Program Level 2: Operating Procedures - General | Failure to prepare written operating procedures that provide clear instructions or steps for safely conducting activities associated with each covered process consistent with the safety information for that process and address the following: 1. Initial startup; 2. Normal operations; 3. Temporary operations; 4. Emergency shutdown and operations; 5. Normal shutdown; 6. Startup following a normal or emergency shutdown or a major change that requires a hazard review; 7. Consequences of deviations and steps required to correct or avoid deviations; 8. Equipment inspections. | 19 CCR 4.5 2755.3(a), 2755.3(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 60 | Program 2 Prevention Program | Operating Procedures | Prepared written operating procedures that provide clear instructions for each covered process | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare written operating procedures that provide clear instructions or steps for safely conducting activities associated with each covered process consistent with the safety information for that process and address the following: 1. Initial startup; 2. Normal operations; 3. Temporary operations; 4. Emergency shutdown and operations; 5. Normal shutdown; 6. Startup following a normal or emergency shutdown or a major change that requires a hazard review; 7. Consequences of deviations and steps required to correct or avoid deviations; 8. Equipment inspections. |  |  | OBSERVATION: The owner/operator failed to prepare written operating procedures that provide clear instructions or steps for safely conducting activities associated with each covered process consistent with the safety information for that process and address the following: initial startup; normal operations; temporary operations; emergency shutdown and operations; normal shutdown; startup following a normal or emergency shutdown or a major change that requires a hazard review; consequences of deviations and steps required to correct or avoid deviations; equipment inspections. CORRECTIVE ACTION: Submit written operating procedures to the CUPA that address all of the requirements noted above. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010050 |  |  | Program Level 2: Operating Procedures - Update | Failure to ensure that the operating procedures are developed and/or updated, as necessary to reflect current practice, or whenever the tasks or steps to perform on the covered process are found to be inadequate or inaccurate. | 19 CCR 4.5 2755.3(c) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 61 | Program 2 Prevention Program | Operating Procedures | Ensured that operating procedures are developed/updated as necessary | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that the operating procedures are developed and/or updated, as necessary to reflect current practice, or whenever the tasks or steps to perform on the covered process are found to be inadequate or inaccurate. |  |  | OBSERVATION: The owner/operator failed to ensure that the operating procedures are developed and/or updated as necessary to reflect current practice, or whenever the tasks or steps to perform on the covered process are found to be inadequate or inaccurate. CORRECTIVE ACTION: Develop/Update the operating procedures to reflect current practice and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020001 |  |  | Program Level 2: Training - General | Failure to ensure that each employee presently operating a process, and each employee newly assigned to a covered process has been trained or tested competent in the operating procedures provided in Section 2755.3 that pertain to their duties. | 19 CCR 4.5 2755.4(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 62 | Program 2 Prevention Program | Training | Employees operating a process have been trained or tested competent in the operating procedures | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that each employee presently operating a process, and each employee newly assigned to a covered process has been trained or tested competent in the operating procedures provided in Section 2755.3 that pertain to their duties. |  |  | OBSERVATION: The owner/operator failed to ensure that each employee presently operating a process, and each employee newly assigned to a covered process has been trained or tested competent in the operating procedures provided in Section 2755.3 that pertain to their duties. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that each employee presently operating a process, and each employee newly assigned to a covered process has been trained or tested competent in the operating procedures that pertain to their duties. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020002 |  |  | Program Level 2: Training - Refresher | Failure to provide refresher training at least every three years, and more often if necessary, to each employee operating a process to ensure that the employee understands and adheres to the current operating procedures of the process. | 19 CCR 4.5 2755.4(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 63 | Program 2 Prevention Program | Training | Employees operating a process provided refresher training on operating procedures every three years | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide refresher training at least every three years, and more often if necessary, to each employee operating a process to ensure that the employee understands and adheres to the current operating procedures of the process. |  |  | OBSERVATION: The owner/operator failed to provide refresher training at least every three years, and more often if necessary, to each employee operating a process to ensure that the employee understands and adheres to the current operating procedures of the process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that each employee operating a process has received refresher training. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020003 |  |  | Program Level 2: Training - Prestart up | Failure to ensure operators are trained in any updated or new procedures prior to needing to use the procedures. | 19 CCR 4.5 2755.4(d) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 64 | Program 2 Prevention Program | Training | Operators trained in updated or new procedures prior to using the procedures | 76 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure operators are trained in any updated or new procedures prior to needing to use the procedures. |  |  | OBSERVATION: The owner/operator failed to ensure operators are trained in updated or new procedures prior to needing to use the procedures. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the operators are trained in any updated or new procedures. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020011 |  |  | Program Level 2: Training - Documentation | Failure to document initial and refresher training for each employee. | 19 CCR 4.5 2755.4(e) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 65 | Program 2 Prevention Program | Training | Initial and refresher training documented | 41 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document initial and refresher training for each employee. |  |  | OBSERVATION: The owner/operator failed to document initial and refresher training for each employee. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating initial and refresher training for each employees has been conducted. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010051 |  |  | Program Level 2: Maintenance - Procedures | Failure to prepare and implement written procedures to maintain the on-going mechanical integrity of the process equipment. | 19 CCR 4.5 2755.5(a) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 66 | Program 2 Prevention Program | Maintenance | Prepared/Implemented written procedures to maintain the mechanical integrity of process equipment | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare and implement written procedures to maintain the on-going mechanical integrity of the process equipment. |  |  | OBSERVATION: The owner/operator failed to prepare and implement written procedures to maintain the on-going mechanical integrity of the process equipment. CORRECTIVE ACTION: Prepare and implement written procedures to maintain the on-going mechanical integrity of the process equipment and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020004 |  |  | Program Level 2: Maintenance - Training | Failure to train or cause to be trained each employee involved in maintaining the on-going mechanical integrity of the process in: 1. The hazards of the process; 2. How to avoid or correct unsafe conditions; 3. The procedures applicable to the employee’s job tasks. | 19 CCR 4.5 2755.5(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 67 | Program 2 Prevention Program | Maintenance | Employees conducting maintenance are trained on hazards, avoiding unsafe conditions, and procedures | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to train or cause to be trained each employee involved in maintaining the on-going mechanical integrity of the process in: 1. The hazards of the process; 2. How to avoid or correct unsafe conditions; 3. The procedures applicable to the employee’s job tasks. |  |  | OBSERVATION: The owner/operator failed to train or cause to be trained each employee involved in maintaining the on-going mechanical integrity of the process in: the hazards of the process; how to avoid or correct unsafe conditions; the procedures applicable to the employee’s job tasks. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating each employee involved in maintaining the on-going mechanical integrity of the process is trained in: the hazards of the process; how to avoid or correct unsafe conditions; the procedures applicable to the employee’s job tasks. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020005 |  |  | Program Level 2: Maintenance - Contractor Training | Failure to ensure that each contractor can document that their employees are trained to perform the maintenance and appropriate operation procedures developed under section 2755.5(a). | 19 CCR 4.5 2755.5(c) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 68 | Program 2 Prevention Program | Maintenance | Documented that contract employees are trained to perform the maintenance procedures | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that each contractor can document that their employees are trained to perform the maintenance and appropriate operation procedures developed under section 2755.5(a). |  |  | OBSERVATION: The owner/operator failed to ensure that each contractor can document that their employees are trained to perform the maintenance and appropriate operating procedures developed under section 2755.5(a). CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that each contract maintenance employee is trained to perform applicable maintenance and appropriate operating procedures. | [6 empty] | No | Yes | No | No
CalARP Program | Operations/Maintenance | 5030001 |  |  | Program Level 2: Maintenance - Inspections and Tests | Failure to perform or cause to be performed inspections and tests on process equipment that: 1. Follow recognized and generally accepted good engineering practices; 2. The frequency of inspections & tests must be consistent with applicable manufacturer’s recommendations, industry standards or codes, good engineering practices and prior operating experience. | 19 CCR 4.5 2755.5(d) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 69 | Program 2 Prevention Program | Maintenance | Maintenance inspections and tests performed per RAGAGEP, and at proper frequency | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform or cause to be performed inspections and tests on process equipment that: 1. Follow recognized and generally accepted good engineering practices; 2. The frequency of inspections & tests must be consistent with applicable manufacturer’s recommendations, industry standards or codes, good engineering practices and prior operating experience. |  |  | OBSERVATION: The owner/operator failed to perform or cause to be performed inspections and tests on process equipment that: follow recognized and generally accepted good engineering practices; the frequency of inspections & tests must be consistent with applicable manufacturer’s recommendations, industry standards or codes, good engineering practices and prior operating experience. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the owner/operator performed inspections and tests on process equipment that: follow recognized and generally accepted good engineering practices; the frequency of inspections & tests must be consistent with applicable manufacturer’s recommendations, industry standards or codes, good engineering practices and prior operating experience. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/ Documentation | 5010052 |  |  | Program Level 2: Compliance Audits - Triennial Certification | Failure to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 5 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. | 19 CCR 4.5 2755.6(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 70 | Program 2 Prevention Program | Compliance Audits | Certified the evaluation of compliance with Program Level 2 provisions at least every three years | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 5 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. |  |  | OBSERVATION: The owner/operator failed to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 5 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. CORRECTIVE ACTION: Submit a certification to the CUPA that the owner/operator has evaluated compliance with the provisions of 19 CCR 4.5 Article 5 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010053 |  |  | Program Level 2: Compliance Audits - Knowledgeable Person | Failure to conduct the compliance audit by at least one person knowledgeable in the process. | 19 CCR 4.5 2755.6(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 71 | Program 2 Prevention Program | Compliance Audits | Conducted the compliance audit by at least one person knowledgeable in the process | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to conduct the compliance audit by at least one person knowledgeable in the process. |  |  | OBSERVATION: The owner/operator failed to conduct the compliance audit with at least one person knowledgeable in the process. CORRECTIVE ACTION: Conduct the compliance audit with at least one person knowledgeable in the process. Develop a report of the compliance audit findings, including appropriate responses to each of the findings and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010054 |  |  | Program Level 2: Compliance Audits - Report of Audit Findings | Failure to develop a report of the audit findings. | 19 CCR 4.5 2755.6(c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 72 | Program 2 Prevention Program | Compliance Audits | Developed a report of the audit findings | 40 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop a report of the audit findings. |  |  | OBSERVATION: The owner/operator failed to develop a report of the compliance audit findings. CORRECTIVE ACTION: Develop a report of the compliance audit findings, including appropriate responses to each of the findings and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010055 |  |  | Program Level 2: Compliance Audits - Findings/Resolutions | Failure to: 1. Promptly determine and document an appropriate response to each of the findings of the compliance audit; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings. Otherwise these responses shall be completed one and one-half (1.5) years after performing the compliance audit, or the next planned turnaround for items requiring a turnaround (these timelines shall not apply to any compliance audit completed prior to January 1, 2015); 3. Document the actual completion dates when deficiencies were corrected. | 19 CCR 4.5 2755.6(d) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 73 | Program 2 Prevention Program | Compliance Audits | Promptly determined and documented response to audit findings, including correction of deficiencies | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to: 1. Promptly determine and document an appropriate response to each of the findings of the compliance audit; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings. Otherwise these responses shall be completed one and one-half (1.5) years after performing the compliance audit, or the next planned turnaround for items requiring a turnaround (these timelines shall not apply to any compliance audit completed prior to January 1, 2015); 3. Document the actual completion dates when deficiencies were corrected. |  |  | OBSERVATION: The owner/operator failed to promptly determine and document an appropriate response to each of the findings of the compliance audit and document the completion dates when deficiencies have been corrected. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has documented an appropriate response to each of the findings of the compliance audit including completion dates for deficiencies that have been corrected. | OBSERVATION: The owner/operator failed to document actual completion dates when deficiencies identified in the compliance audit were corrected. CORRECTIVE ACTION: Submit the documented completion dates for compliance audit deficiencies that have been corrected. | [5 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010056 |  |  | Program Level 2: Compliance Audits - Report Retention | Failure to retain the two most recent compliance audit reports. | 19 CCR 4.5 2755.6(e) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 74 | Program 2 Prevention Program | Compliance Audits | Retained the two most recent compliance audit reports | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain the two most recent compliance audit reports. |  |  | OBSERVATION: The owner/operator failed to retain the two most recent compliance audit reports. CORRECTIVE ACTION: Submit a copy of the two most recent compliance audit reports to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010057 |  |  | Program Level 2: Incident Investigation - General | Failure to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release. | 19 CCR 4.5 2755.7(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 75 | Program 2 Prevention Program | Incident Investigation | Investigated each incident that resulted or could reasonably have resulted in a catastrophic release | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release. |  |  | OBSERVATION: The owner/operator failed to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release. CORRECTIVE ACTION: Investigate the incident and submit a copy of the investigation findings with recommendations to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010058 |  |  | Program Level 2: Incident Investigation - Prompt Initiation | Failure to initiate an incident investigation as promptly as possible, but not later than 48 hours following the incident. | 19 CCR 4.5 2755.7(b) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 76 | Program 2 Prevention Program | Incident Investigation | Initiated incident investigations within 48 hours of the incident | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to initiate an incident investigation as promptly as possible, but not later than 48 hours following the incident. |  |  | OBSERVATION: The owner/operator failed to initiate an incident investigations within 48 hours of the incident. CORRECTIVE ACTION: Submit a statement to the CUPA demonstrating how incident investigations will be initiated within 48 hours of the incident. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010059 |  |  | Program Level 2: Incident Investigation - Summary | Failure to prepare a summary at the conclusion of the investigation that includes at minimum: 1. Date of incident; 2. Date investigation began; 3. Description of incident; 4. Factors that contributed to the incident; 5. Recommendations resulting from the investigation | 19 CCR 4.5 2755.7(c); 2750.9(b) | 2021-08-02 | 2024-09-30 | 2024-09-30 | Revised | 77 | Program 2 Prevention Program | Incident Investigation | Prepared a summary of the investigation at the conclusion of the investigation | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a summary at the conclusion of the investigation that includes at minimum: 1. Date of incident; 2. Date investigation began; 3. Description of incident; 4. Factors that contributed to the incident; 5. Recommendations resulting from the investigation |  |  | OBSERVATION: The owner/operator failed to prepare a summary of the investigation at the conclusion of the investigation that includes the date of incident; date investigation began; description of incident; factors that contributed to the incident; and recommendations resulting from the investigation. CORRECTIVE ACTION: Prepare and submit a copy of the investigation to the CUPA that includes the date of incident; date investigation began; description of incident; factors that contributed to the incident; and recommendations resulting from the investigation. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010060 |  |  | Program Level 2: Incident Investigation - Findings/Resolutions | Failure to: 1. Establish a system to promptly address and resolve the incident report findings and recommendations; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings and recommendations. Otherwise these resolutions shall be completed no later than one and one-half (1.5) years after completion of the incident investigation, or two (2) years after the date of the incident, whichever is the earlier of the two dates, or the next planned turnaround for those items requiring turnaround. 3. Failure to document resolutions and corrective actions with actual completion dates. | 19 CCR 4.5 2755.7(d) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 78 | Program 2 Prevention Program | Incident Investigation | Addressed and resolved the investigation findings and recommendations and documented resolutions | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to: 1. Establish a system to promptly address and resolve the incident report findings and recommendations; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings and recommendations. Otherwise these resolutions shall be completed no later than one and one-half (1.5) years after completion of the incident investigation, or two (2) years after the date of the incident, whichever is the earlier of the two dates, or the next planned turnaround for those items requiring turnaround. 3. Failure to document resolutions and corrective actions with actual completion dates. |  |  | OBSERVATION: The owner/operator failed to address, resolve, and/or document the investigation findings, recommendations, and resolutions, and/or failed to do so within required time frame. CORRECTIVE ACTION: Address and resolve the investigation findings and recommendations. Submit a copy of the documented resolutions and corrective actions with actual completion dates to the UPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010062 |  |  | Program Level 2: Incident Investigation - Review | Failure to review the findings with all affected personnel whose job tasks are affected by the findings. | 19 CCR 4.5 2755.7(e) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 79 | Program 2 Prevention Program | Incident Investigation | Reviewed the incident investigation findings with all affected personnel | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to review the findings with all affected personnel whose job tasks are affected by the findings. |  |  | OBSERVATION: The owner/operator failed to review the investigation findings with all affected personnel whose job tasks are affected by the findings. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the investigation findings have been reviewed with all affected personnel whose job tasks are affected by the findings. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010063 |  |  | Program Level 2: Incident Investigation - Summary Retention | Failure to retain investigation summaries for five years. | 19 CCR 4.5 2755.7(f) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 80 | Program 2 Prevention Program | Incident Investigation | Retained investigation summaries for five years | 47 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain investigation summaries for five years. |  |  | OBSERVATION: The owner/operator failed to retain investigation summaries for five years. CORRECTIVE ACTION: Submit a copy of the missing investigation summaries for the last five years to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010064 |  |  | Program Level 3: Process Safety Information - Regulated Substance | Failure to compile and maintain up-to-date written process safety information pertaining to the hazards of the regulated substances in the process that includes the following: 1. Toxicity information; 2. Permissible exposure limits; 3. Physical data; 4. Reactivity data and chemical compatibility data during handling, use, and application at the stationary source; 5. Corrosivity data; 6. Thermal and chemical stability data; 7. Hazardous effects of inadvertent mixing of different materials that could foreseeably occur. | 19 CCR 4.5 2760.1(a), (b) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 81 | Program 3 Prevention Program | Process Safety Information | Compiled and maintained up-to-date written PSI pertaining to the hazards of the RS in the process | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to compile and maintain up-to-date written process safety information pertaining to the hazards of the regulated substances in the process that includes the following: 1. Toxicity information; 2. Permissible exposure limits; 3. Physical data; 4. Reactivity data and chemical compatibility data during handling, use, and application at the stationary source; 5. Corrosivity data; 6. Thermal and chemical stability data; 7. Hazardous effects of inadvertent mixing of different materials that could foreseeably occur. |  |  | OBSERVATION: The owner/operator failed to compile and maintain up-to-date written process safety information pertaining to the hazards of the regulated substances in the process that includes: toxicity information; permissible exposure limits; physical data; reactivity data; corrosivity data; thermal and chemical stability data; hazardous effects of inadvertent mixing of different materials that could foreseeably occur. CORRECTIVE ACTION: Compile the up-to-date written process safety information pertaining to the hazards of the regulated substances in the process that includes: toxicity information; permissible exposure limits; physical data; reactivity data; corrosivity data; thermal and chemical stability data; hazardous effects of inadvertent mixing of different materials that could foreseeable occur and submit a copy to the UPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010065 |  |  | Program Level 3: Process Safety Information - Technology | Failure to compile written process safety information concerning the technology of the process that includes the following: 1. A block flow diagram or simplified process flow diagram; 2. Process chemistry; 3. Maximum intended inventory; 4. Safe upper and lower limits for such items as temperatures, pressures, flows or compositions; 5. An evaluation of the consequences of deviations. | 19 CCR 4.5 2760.1(a), (c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 82 | Program 3 Prevention Program | Process Safety Information | Compiled and maintained up-to-date written PSI concerning the technology of the process | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to compile written process safety information concerning the technology of the process that includes the following: 1. A block flow diagram or simplified process flow diagram; 2. Process chemistry; 3. Maximum intended inventory; 4. Safe upper and lower limits for such items as temperatures, pressures, flows or compositions; 5. An evaluation of the consequences of deviations. |  |  | OBSERVATION: The owner/operator failed to compile written process safety information concerning the technology of the process that includes: a block flow diagram or simplified process flow diagram; process chemistry; maximum intended inventory; safe upper and lower limits for such items as temperatures, pressures, flows or compositions; an evaluation of the consequences of deviations. CORRECTIVE ACTION: Compile written process safety information concerning the technology of the process that includes: a block flow diagram or simplified process flow diagram; process chemistry; /maximum intended inventory; safe upper and lower limits for such items as temperatures, pressures, flows or compositions; an evaluation of the consequences of deviations and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010066 |  |  | Program Level 3: Process Safety Information - Equipment | Failure to compile written process safety information pertaining to the equipment in the process that includes the following: 1. Materials of construction; 2. Piping and instrument diagrams (P&IDs); 3. Electrical classification; 4. Relief system design and design basis; 5. Ventilation system design; 6. Design codes and standards employed; 7. Material and energy balances for processes built after June 21, 1999; 8. Safety systems (e.g., interlocks, detection, or suppression systems). | 19 CCR 4.5 2760.1(a), (d)(1) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 83 | Program 3 Prevention Program | Process Safety Information | Compiled and maintained up-to-date written PSI pertaining to the equipment in the process | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to compile written process safety information pertaining to the equipment in the process that includes the following: 1. Materials of construction; 2. Piping and instrument diagrams (P&IDs); 3. Electrical classification; 4. Relief system design and design basis; 5. Ventilation system design; 6. Design codes and standards employed; 7. Material and energy balances for processes built after June 21, 1999; 8. Safety systems (e.g., interlocks, detection, or suppression systems). |  |  | OBSERVATION: The owner/operator failed to compile written process safety information pertaining to the equipment in the process that includes: materials of construction; piping and instrument diagrams (P&IDs); electrical classification; relief system design and design basis; ventilation system design; design codes and standards employed; material and energy balances for processes built after June 21, 1999; safety systems (e.g., interlocks, detection, or suppression systems). CORRECTIVE ACTION: Compile written process safety information pertaining to the equipment in the process that includes: materials of construction; piping and instrument diagrams (P&IDs); electrical classification; relief system design and design basis; ventilation system design; design codes and standards employed; material and energy balances for processes built after June 21, 1999; safety systems (e.g., interlocks, detection, or suppression systems) and submit a copy to the UPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010067 |  |  | Program Level 3: Process Safety Information - Equipment Compliance Documentation | Failure to document that equipment complies with recognized and generally accepted good engineering practices. | 19 CCR 4.5 2760.1(d)(2) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 84 | Program 3 Prevention Program | Process Safety Information | Documented that equipment complies with recognized and generally accepted good engineering practices | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to document that equipment complies with recognized and generally accepted good engineering practices. |  |  | OBSERVATION: The owner/operator failed to document that equipment complies with recognized and generally accepted good engineering practices. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that equipment complies with recognized and generally accepted good engineering practices. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010068 |  |  | Program Level 3: Process Safety Information - Existing Equipment Compliance Documentation | For existing equipment designed and constructed in accordance with codes, standards, or practices that are no longer in general use, the owner or operator has determined and documented that the equipment is designed, maintained, inspected, tested, and operating in a safe manner. | 19 CCR 4.5 2760.1(d)(3) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 85 | Program 3 Prevention Program | Process Safety Information | Documented that equipment is designed, maintained, inspected, tested, and operating in a safe manner | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | For existing equipment designed and constructed in accordance with codes, standards, or practices that are no longer in general use, the owner or operator has determined and documented that the equipment is designed, maintained, inspected, tested, and operating in a safe manner. |  |  | OBSERVATION: The owner/operator failed to determine and document that existing equipment designed and constructed in accordance with codes, standards, or practices that are no longer in general use are designed, maintained, inspected, tested, and operating in a safe manner. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that existing equipment is designed, maintained, inspected, tested, and operated in a safe manner. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010069 |  |  | Program Level 3: Process Hazard Analysis - Initial | Failure to conduct an initial Process Hazard Analysis on the covered processes no later than the date of submittal of the RMP. | 19 CCR 4.5 2760.2(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 86 | Program 3 Prevention Program | Process Hazard Analysis | Conducted an initial PHA on the covered processes no later than the date of submittal of the RMP | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to conduct an initial Process Hazard Analysis on the covered processes no later than the date of submittal of the RMP. |  |  | OBSERVATION: The owner/operator failed to conduct an initial Process Hazard Analysis on the covered processes no later than the date of submittal of the Risk Management Plan. CORRECTIVE ACTION: Conduct a Process Hazard Analysis on the covered process and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010070 |  |  | Program Level 3: Process Hazard Analysis | Failure to perform a Process Hazard Analysis that is appropriate to the complexity of the process and identifies, evaluates, and controls the hazards involved in the process. | 19 CCR 4.5 2760.2(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 87 | Program 3 Prevention Program | Process Hazard Analysis | Performed a PHA that is appropriate for the complexity of the process | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform a Process Hazard Analysis that is appropriate to the complexity of the process and identifies, evaluates, and controls the hazards involved in the process. |  |  | OBSERVATION: The owner/operator failed to perform a Process Hazard Analysis that is appropriate to the complexity of the process and identifies, evaluates, and controls the hazards involved in the process. CORRECTIVE ACTION: Conduct a Process Hazard Analysis on the covered process that is appropriate to the complexity of the process and identifies, evaluates, and controls the hazards involved in the process and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010072 |  |  | Program Level 3: Process Hazard Analysis - Consultation | Failure to work closely with the UPA in deciding which Process Hazard Analysis methodology is best suited to determine the hazards of the process being analyzed. | 19 CCR 4.5 2760.2(b) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 88 | Program 3 Prevention Program | Process Hazard Analysis | Worked with the UPA in deciding which PHA methodology is best to determine the process hazards | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to work closely with the UPA in deciding which Process Hazard Analysis methodology is best suited to determine the hazards of the process being analyzed. |  |  | OBSERVATION: The owner/operator failed to work closely with the UPA in deciding which Process Hazard Analysis methodology is best suited to determine the hazards of the process being analyzed. CORRECTIVE ACTION: Contact the UPA to decide which Process Hazard Analysis methodology is best suited to determine the hazards of the process being analyzed. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010073 |  |  | Program Level 3: Process Hazard Analysis - Methodology | Failure to use one or more of the following methodologies that are appropriate to determine and evaluate the hazards of the process being analyzed: 1. What-If; 2. Checklist; 3. What-If/Checklist; 4. Hazard and Operability Study (HAZOP); 5. Failure Mode and Effects Analysis (FMEA); 6. Fault Tree Analysis; or, 7. An appropriate equivalent methodology. | 19 CCR 4.5 2760.2(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 89 | Program 3 Prevention Program | Process Hazard Analysis | Used one or more methodologies in Section 2760.2(b) to determine and evaluate the process hazards | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to use one or more of the following methodologies that are appropriate to determine and evaluate the hazards of the process being analyzed: 1. What-If; 2. Checklist; 3. What-If/Checklist; 4. Hazard and Operability Study (HAZOP); 5. Failure Mode and Effects Analysis (FMEA); 6. Fault Tree Analysis; or, 7. An appropriate equivalent methodology. |  |  | OBSERVATION: The owner/operator failed to use one or more of the following methodologies that are appropriate to determine and evaluate the hazards of the process being analyzed: what-If; checklist; what-If/Checklist; hazard and Operability Study (HAZOP); failure Mode and Effects Analysis (FMEA); fault Tree Analysis; or an appropriate equivalent methodology. CORRECTIVE ACTION: Conduct a Process Hazard Analysis using one or more of the following methodologies: what-If; checklist; what-If/Checklist; hazard and Operability Study (HAZOP); failure Mode and Effects Analysis (FMEA); fault Tree Analysis; or an appropriate equivalent methodology. Submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010074 |  |  | Program Level 3: Process Hazard Analysis - General | Failure to address the following in the Process Hazard Analysis: 1. The hazards of the process; 2. The identification of any previous incident which had a likely potential for catastrophic consequences; 3. Engineering and administrative controls applicable to the hazards and their interrelationships such as appropriate application of detection methodologies to provide early warning of releases. (Acceptable detection methods might include process monitoring and control instrumentation with alarms, and detection hardware such as hydrocarbon sensors.); 4. Consequences of failure of engineering and administrative controls; 5. Stationary source siting; 6. Human factors; 7. A qualitative evaluation of a range of the possible safety and health effects of failure of controls; and, 8. External events, including seismic events. | 19 CCR 4.5 2760.2(c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 90 | Program 3 Prevention Program | Process Hazard Analysis | PHA addresses hazards, previous incidents, engineering/admin controls, siting, human factors, etc. | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to address the following in the Process Hazard Analysis: 1. The hazards of the process; 2. The identification of any previous incident which had a likely potential for catastrophic consequences; 3. Engineering and administrative controls applicable to the hazards and their interrelationships such as appropriate application of detection methodologies to provide early warning of releases. (Acceptable detection methods might include process monitoring and control instrumentation with alarms, and detection hardware such as hydrocarbon sensors.); 4. Consequences of failure of engineering and administrative controls; 5. Stationary source siting; 6. Human factors; 7. A qualitative evaluation of a range of the possible safety and health effects of failure of controls; and, 8. External events, including seismic events. |  |  | OBSERVATION: The owner/operator failed to address the following in the Process Hazard Analysis: the hazards of the process; the identification of any previous incident which had a likely potential for catastrophic consequences; engineering and administrative controls applicable to the hazards and their interrelationships such as appropriate application of detection methodologies to provide early warning of releases; consequences of failure of engineering and administrative controls; stationary source siting; human factors; a qualitative evaluation of a range of the possible safety and health effects of failure of controls; and external events, including seismic events. CORRECTIVE ACTION: Conduct a Process Hazard Analysis that addresses the requirements noted above and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010075 |  |  | Program Level 3: Process Hazard Analysis - Team Qualifications | Failure to perform the Process Hazard Analysis by a team with expertise in engineering and process operations, including at least one employee who has experience and knowledge specific to the process being evaluated, and one member who is knowledgeable in the specific Process Hazard Analysis methodology being used. | 19 CCR 4.5 2760.2(d) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 91 | Program 3 Prevention Program | Process Hazard Analysis | PHA performed by team with expertise, experience, and knowledge in the process and PHA methodology | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform the Process Hazard Analysis by a team with expertise in engineering and process operations, including at least one employee who has experience and knowledge specific to the process being evaluated, and one member who is knowledgeable in the specific Process Hazard Analysis methodology being used. |  |  | OBSERVATION: The owner/operator failed to perform the Process Hazard Analysis using a team with expertise in engineering and process operations, including at least one employee who has experience and knowledge specific to the process being evaluated, and one member who is knowledgeable in the specific Process Hazard Analysis methodology being used. CORRECTIVE ACTION: Conduct a Process Hazard Analysis using a team with expertise in engineering and process operations, including at least one employee who has experience and knowledge specific to the process being evaluated, and one member who is knowledgeable in the specific Process Hazard Analysis methodology being used and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010076 |  |  | Program Level 3: Process Hazard Analysis - Recommendations/Resolutions | Failure to address the following in the Process Hazard Analysis: 1. Establish a system to address the teams findings and recommendations; 2. Assure that the recommendations are resolved and documented; 3. Document what actions are to be taken; 4. Develop a written schedule of when these actions are to be completed; 5. Complete these actions on a timetable agreed upon with the UPA, or within two and one-half (2.5) years of performing the PHA, or the next planned turnaround, for those items that require a turnaround; 6. Document the final resolution taken to address each recommendation and actual completion date; and 7. Communicate the actions to operating, maintenance and other employees whose work assignments are in the process and who may be affected by the recommendations or actions. | 19 CCR 4.5 2760.2(e) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 92 | Program 3 Prevention Program | Process Hazard Analysis | PHA properly addresses all findings and recommendations and resolutions are completed and documented | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to address the following in the Process Hazard Analysis: 1. Establish a system to address the teams findings and recommendations; 2. Assure that the recommendations are resolved and documented; 3. Document what actions are to be taken; 4. Develop a written schedule of when these actions are to be completed; 5. Complete these actions on a timetable agreed upon with the UPA, or within two and one-half (2.5) years of performing the PHA, or the next planned turnaround, for those items that require a turnaround; 6. Document the final resolution taken to address each recommendation and actual completion date; and 7. Communicate the actions to operating, maintenance and other employees whose work assignments are in the process and who may be affected by the recommendations or actions. |  |  | OBSERVATION: The owner/operator failed to address the following in the Process Hazard Analysis: establish a system to promptly address the team's findings and recommendations; assure that the recommendations are resolved and documented; document what actions are to be taken; develop a written schedule of when these actions are to be completed; complete these actions on a timetable agreed upon with the UPA, or within two and one-half (2.5) years of performing the PHA, or the next planned turnaround, for those items that require a turnaround; document the final resolution taken to address each recommendation and actual completion date; communicate the actions to operating, maintenance and other employees whose work assignments are in the process and who may be affected by the recommendations or actions. CORRECTIVE ACTION: Complete and submit a Process Hazard Analysis to the UPA that addresses the requirements noted above. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010077 |  |  | Program Level 3: Process Hazard Analysis - Update/Revalidation | Failure to update and revalidate the Process Hazard Analysis at least every five years after the completion of the initial Process Hazard Analysis. | 19 CCR 4.5 2760.2(f) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 93 | Program 3 Prevention Program | Process Hazard Analysis | Updated and revalidated the PHA every five years after the completion of the initial PHA | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update and revalidate the Process Hazard Analysis at least every five years after the completion of the initial Process Hazard Analysis. |  |  | OBSERVATION: The owner/operator failed to update and revalidate the Process Hazard Analysis at least every five years after the completion of the initial Process Hazard Analysis. CORRECTIVE ACTION: Update and revalidate the Process Hazard Analysis and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010078 |  |  | Program Level 3: Process Hazard Analysis - Retention | Failure to retain the Process Hazard Analysis and updates/revalidations for each covered process as well as the documented resolution of recommendations for the life of the process. | 19 CCR 4.5 2760.2(g) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 94 | Program 3 Prevention Program | Process Hazard Analysis | Retained all PHAs, updates/revalidations, and documented resolution of recommendations | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain the Process Hazard Analysis and updates/revalidations for each covered process as well as the documented resolution of recommendations for the life of the process. |  |  | OBSERVATION: The owner/operator failed to retain the Process Hazard Analysis and updates/revalidations for each covered process as well as the documented resolution of recommendations for the life of the process. CORRECTIVE ACTION: Obtain the missing Process Hazard Analysis and updates/revalidations for each covered process as well as the documented resolution of recommendations for the life of the process and submit a copy to the CUPA. | OBSERVATION: The owner/operator failed to retain the documented resolution of Process Hazard Analysis recommendations for the life of the process. CORRECTIVE ACTION: Obtain the resolution of the Process Hazard Analysis recommendations for the life of the process and submit a copy to the CUPA. | [5 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010079 |  |  | Program Level 3: Operating Procedures | Failure to develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information. | 19 CCR 4.5 2760.3(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 95 | Program 3 Prevention Program | Operating Procedures | Prepared written operating procedures that provide clear instructions for each covered process | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information. CORRECTIVE ACTION: Develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010080 |  |  | Program Level 3: Operating Procedures - Steps for Each Operating Phase | Failure to develop and implement written operating procedures that address at least the following operating phases: 1. Initial startup; 2. Normal operations; 3. Temporary operations; 4. Emergency shutdown including the conditions under which emergency shutdown is required, and the assignment of shutdown responsibility to qualified operators to ensure that emergency shutdown is executed in a safe and timely manner; 5. Emergency operations; 6. Normal shutdown; 7. Startup following a turnaround, or after an emergency shutdown. | 19 CCR 4.5 2760.3(a)(1) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 96 | Program 3 Prevention Program | Operating Procedures | Developed and implemented written operating procedures that address all operating phases | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop and implement written operating procedures that address at least the following operating phases: 1. Initial startup; 2. Normal operations; 3. Temporary operations; 4. Emergency shutdown including the conditions under which emergency shutdown is required, and the assignment of shutdown responsibility to qualified operators to ensure that emergency shutdown is executed in a safe and timely manner; 5. Emergency operations; 6. Normal shutdown; 7. Startup following a turnaround, or after an emergency shutdown. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address: initial startup; normal operations; temporary operations; emergency shutdown including the conditions under which emergency shutdown is required, and the assignment of shutdown responsibility to qualified operators to ensure that emergency shutdown is executed in a safe and timely manner; emergency operations; normal shutdown; startup following a turnaround, or after an emergency shutdown. CORRECTIVE ACTION: Develop, implement and submit copies of written operating procedures that address the deficiencies noted above. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010081 |  |  | Program Level 3: Operating Procedures - Operating Limits | Failure to develop and implement written operating procedures that address at least the following operating limits: 1. Consequences of deviation; and, 2. Steps required to correct or avoid deviation. | 19 CCR 4.5 2760.3(a)(2) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 97 | Program 3 Prevention Program | Operating Procedures | Written operating procedures address consequences of deviation and steps to avoid deviation | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop and implement written operating procedures that address at least the following operating limits: 1. Consequences of deviation; and, 2. Steps required to correct or avoid deviation. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address the consequences of deviation and the steps required to correct or avoid the deviation. CORRECTIVE ACTION: Develop and implement written operating procedures that address the consequences of deviation and the steps required to correct or avoid the deviation/ and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010082 |  |  | Program Level 3: Operating Procedures - Safety and Health Considerations | Failure to develop and implement written operating procedures that address at least the following safety and health considerations: 1. Properties of, and hazards presented by, the chemicals used in the process; 2. Precautions necessary to prevent exposure, including engineering controls, administrative controls, and personal protective equipment; 3. Control measures to be taken if physical contact or airborne exposure occurs; 4. Quality control for raw materials and control of hazardous chemical inventory levels; 5. Any special or unique hazards. | 19 CCR 4.5 2760.3(a)(3) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 98 | Program 3 Prevention Program | Operating Procedures | Written operating procedures address all required safety and health considerations | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop and implement written operating procedures that address at least the following safety and health considerations: 1. Properties of, and hazards presented by, the chemicals used in the process; 2. Precautions necessary to prevent exposure, including engineering controls, administrative controls, and personal protective equipment; 3. Control measures to be taken if physical contact or airborne exposure occurs; 4. Quality control for raw materials and control of hazardous chemical inventory levels; 5. Any special or unique hazards. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address: properties of, and hazards presented by, the chemicals used in the process; precautions necessary to prevent exposure, including engineering controls, administrative controls, and personal protective equipment; control measures to be taken if physical contact or airborne exposure occurs; quality control for raw materials and control of hazardous chemical inventory levels; any special or unique hazards. CORRECTIVE ACTION: Develop, implement, and submit copy of written operating procedures that address the deficiencies noted above. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010083 |  |  | Program Level 3: Operating Procedures - Safety Systems and their Functions | Failure to develop and implement written operating procedures that address safety systems and their functions. | 19 CCR 4.5 2760.3(a)(4) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 99 | Program 3 Prevention Program | Operating Procedures | Written operating procedures address safety systems and their functions | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop and implement written operating procedures that address safety systems and their functions. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address safety systems and their functions. CORRECTIVE ACTION: Develop and implement written operating procedures that address safety systems and their functions and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010084 |  |  | Program Level 3: Operating Procedures - Accessible | Failure to make operating procedures readily accessible to employees who work in or maintain a process. | 19 CCR 4.5 2760.3(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 100 | Program 3 Prevention Program | Operating Procedures | Operating procedures are readily accessible to employees who work in or maintain a process | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to make operating procedures readily accessible to employees who work in or maintain a process. |  |  | OBSERVATION: The owner/operator failed to make operating procedures readily accessible to employees who work in or maintain a process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating operating procedures are readily accessible to employees who work in or maintain a process. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010085 |  |  | Program Level 3: Operating Procedures - Review | Failure to review operating procedures as often as necessary to assure that they reflect current operating practice, including changes that result from changes in process chemicals, technology, and equipment, and changes to stationary sources. | 19 CCR 4.5 2760.3(c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 101 | Program 3 Prevention Program | Operating Procedures | Reviewed operating procedures to assure they reflect current operating practice | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to review operating procedures as often as necessary to assure that they reflect current operating practice, including changes that result from changes in process chemicals, technology, and equipment, and changes to stationary sources. |  |  | OBSERVATION: The owner/operator failed to review operating procedures as often as necessary to assure that they reflect current operating practice, including changes that result from changes in process chemicals, technology, and equipment, and changes to stationary sources. CORRECTIVE ACTION: Review and update the operating procedures to assure that they reflect current operating practice and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010086 |  |  | Program Level 3: Operating Procedures - Annual Certification | Failure to certify annually that the operating procedures are current and accurate. | 19 CCR 4.5 2760.3(c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 102 | Program 3 Prevention Program | Operating Procedures | Certified annually that the operating procedures are current and accurate | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to certify annually that the operating procedures are current and accurate. |  |  | OBSERVATION: The owner/operator failed to certify annually that the operating procedures are current and accurate. CORRECTIVE ACTION: Review and update the operating procedures to assure that they reflect current operating practice. Certify that the operating procedures are current and accurate and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010087 |  |  | Program Level 3: Operating Procedures - Safe Work Practices | Failure to develop and implement safe work practices to provide for the control of hazards during operations such as: 1. Logout/tagout; 2. Confined space entry; 3. Opening process equipment or piping; and 4. Control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel. | 19 CCR 4.5 2760.3(d) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 103 | Program 3 Prevention Program | Operating Procedures | Developed and implemented safe work practices to provide control of hazards during operations | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop and implement safe work practices to provide for the control of hazards during operations such as: 1. Logout/tagout; 2. Confined space entry; 3. Opening process equipment or piping; and 4. Control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel. |  |  | OBSERVATION: The owner/operator failed to develop and implement safe work practices to provide for the control of hazards during operations including: lockout/tagout; confined space entry; opening process equipment or piping; and control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel. CORRECTIVE ACTION: Develop and implement safe work practices to provide for the control of hazards during operations including: lockout/tagout; confined space entry; opening process equipment or piping; and control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Training | 5020006 |  |  | Program Level 3: Training - Initial | Failure to train each employee presently involved in operating a process, and each employee before being involved in operating a newly assigned process on the following: 1. Overview of the process; 2. Operating procedures; 3. Safety & health hazards; 4. Emergency operations including shutdown; 5. Safe work practices applicable to the employee's job tasks. | 19 CCR 4.5 2760.4(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 104 | Program 3 Prevention Program | Training | Trained employees on process overview, procedures, safety, emer. ops, and safe work practices | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to train each employee presently involved in operating a process, and each employee before being involved in operating a newly assigned process on the following: 1. Overview of the process; 2. Operating procedures; 3. Safety & health hazards; 4. Emergency operations including shutdown; 5. Safe work practices applicable to the employee's job tasks. |  |  | OBSERVATION: The owner/operator failed to train each employee presently involved in operating a process, and each employee before being involved in operating a newly assigned process on the following: overview of the process; operating procedures; safety & health hazards; emergency operations including shutdown; safe work practices applicable to the employee's job tasks. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating each employee presently involved in operating a process has been trained on the following: overview of the process; operating procedures; safety & health hazards; emergency operations including shutdown; safe work practices applicable to the employee's job tasks. | [6 empty] | No | No | Yes | No
CalARP Program | Training | 5020007 |  |  | Program Level 3: Training - Refresher | Failure to provide refresher training at least every three years, and more often if necessary, to each employee involved in operating a process to assure that the employee understands & adheres to the current operating procedures of the process. | 19 CCR 4.5 2760.4(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 105 | Program 3 Prevention Program | Training | Employees operating a process provided refresher training on operating procedures every three years | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide refresher training at least every three years, and more often if necessary, to each employee involved in operating a process to assure that the employee understands & adheres to the current operating procedures of the process. |  |  | OBSERVATION: The owner/operator failed to provide refresher training at least every three years, and more often if necessary, to each employee involved in operating a process to assure that the employee understands & adheres to the current operating procedures of the process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that each employee involved in operating a process has received refresher training. | [6 empty] | No | No | Yes | No
CalARP Program | Training | 5020008 |  |  | Program Level 3: Training - Documentation | Failure to prepare a training record which contains: 1. Identity of the Employee; 2. Date of training; 3. Means used to verify that the employee understood the training. | 19 CCR 4.5 2760.4(c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 106 | Program 3 Prevention Program | Training | Training records identify the employee, training date, and means to verify training was understood | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a training record which contains: 1. Identity of the Employee; 2. Date of training; 3. Means used to verify that the employee understood the training. |  |  | OBSERVATION: The owner/operator failed to prepare a training record which contains the identity of the employee; date of training; means used to verify that the employee understood the training. CORRECTIVE ACTION: Submit a copy of the training record to the CUPA which contains the identity of the employee; date of training; means used to verify that the employee understood the training. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010088 |  |  | Program Level 3: Mechanical Integrity - Procedures | Failure to establish and implement written procedures to maintain the on-going integrity of the process equipment. | 19 CCR 4.5 2760.5(b) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 107 | Program 3 Prevention Program | Mechanical Integrity | Established and implemented written procedures to maintain the integrity of process equipment | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to establish and implement written procedures to maintain the on-going integrity of the process equipment. |  |  | OBSERVATION: The owner/operator failed to establish and implement written procedures to maintain the on-going integrity of the process equipment. CORRECTIVE ACTION: Establish and implement written procedures to maintain the on-going integrity of the process equipment and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Training | 5020009 |  |  | Program Level 3: Mechanical Integrity - Training | Failure to train each employee involved in maintaining the on-going integrity of process equipment on the following: 1. Overview of the process and its hazards. 2. Procedures applicable to the employee’s job tasks to assure that the employee can perform the job tasks in a safe manner. | 19 CCR 4.5 2760.5(c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 108 | Program 3 Prevention Program | Mechanical Integrity | Employees conducting mechanical integrity trained on process overview/hazards & safety procedures | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to train each employee involved in maintaining the on-going integrity of process equipment on the following: 1. Overview of the process and its hazards. 2. Procedures applicable to the employee’s job tasks to assure that the employee can perform the job tasks in a safe manner. |  |  | OBSERVATION: The owner/operator failed to train each employee involved in maintaining the on-going integrity of process equipment on the following: overview of the process and its hazards; procedures applicable to the employee’s job tasks to assure that the employee can perform the job tasks in a safe manner. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that each employee involved in maintaining the on-going integrity of process equipment is trained on the following: overview of the process and its hazards; procedures applicable to the employee’s job tasks to assure that the employee can perform the job tasks in a safe manner. | [6 empty] | No | No | Yes | No
CalARP Program | Operations/Maintenance | 5030002 |  |  | Program Level 3: Mechanical Integrity - Inspection and Testing | Failure to ensure the following: 1. Inspections and tests are performed on process equipment; 2. Inspection and testing procedures follow recognized and generally accepted good engineering practices; 3. The frequency of inspections and tests of process equipment is consistent with applicable manufacturers’ recommendations and good engineering practices, and more frequently if determined to be necessary by prior operating experience; 4. Each inspection or test that has been performed on process equipment is documented and includes the date of inspection or test, name of the person who performed the inspection or test, serial number or other identifier of the equipment inspected or tested, description of the inspection or test performed, and the results of the inspection or test. | 19 CCR 4.5 2760.5(d) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 109 | Program 3 Prevention Program | Mechanical Integrity | Mechanical integrity inspections/testing performed per RAGAGEP, at proper frequency, and documented | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure the following: 1. Inspections and tests are performed on process equipment; 2. Inspection and testing procedures follow recognized and generally accepted good engineering practices; 3. The frequency of inspections and tests of process equipment is consistent with applicable manufacturers’ recommendations and good engineering practices, and more frequently if determined to be necessary by prior operating experience; 4. Each inspection or test that has been performed on process equipment is documented and includes the date of inspection or test, name of the person who performed the inspection or test, serial number or other identifier of the equipment inspected or tested, description of the inspection or test performed, and the results of the inspection or test. |  |  | OBSERVATION: The owner/operator failed to implement the following: inspections and tests are performed on process equipment; inspection and testing procedures follow recognized and generally accepted good engineering practices; the frequency of inspections and tests of process equipment is consistent with applicable manufacturers’ recommendations and good engineering practices, and more frequently if determined to be necessary by prior operating experience; each inspection or test that has been performed on process equipment is documented and includes the date of inspection or test, name of the person who performed the inspection or test, serial number or other identifier of the equipment inspected or tested, description of the inspection or test performed, and the results of the inspection or test. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has corrected the violations noted above. | [6 empty] | No | No | Yes | No
CalARP Program | Operations/Maintenance | 5030003 |  |  | Program Level 3: Mechanical Integrity - Equipment Deficiencies | Failure to correct deficiencies in equipment that are outside acceptable limits before further use or in a safe and timely manner when necessary means are taken to assure safe operation. | 19 CCR 4.5 2760.5(e) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 110 | Program 3 Prevention Program | Mechanical Integrity | Corrected deficiencies in equipment that are outside acceptable limits | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to correct deficiencies in equipment that are outside acceptable limits before further use or in a safe and timely manner when necessary means are taken to assure safe operation. |  |  | OBSERVATION: The owner/operator failed to correct deficiencies in equipment that are outside acceptable limits before further use or in a safe and timely manner when necessary means are taken to assure safe operation. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has corrected deficiencies in the equipment that is outside acceptable limits. | [6 empty] | No | No | Yes | No
CalARP Program | Operations/Maintenance | 5030004 |  |  | Program Level 3: Mechanical Integrity - Quality Assurance | Failure to ensure: 1. In the construction of new plants and equipment that equipment as it is fabricated is suitable for the process application for which it will be used. 2. Appropriate checks and inspections are performed to assure that equipment is installed properly and consistent with design specifications and the manufacturer's instructions. 3. Maintenance materials, spare parts, and equipment are suitable for the process application for which they will be used. | 19 CCR 4.5 2760.5(f) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 111 | Program 3 Prevention Program | Mechanical Integrity | Complied with quality assurance requirements: equipment & maint. material suitability & inspections | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure: 1. In the construction of new plants and equipment that equipment as it is fabricated is suitable for the process application for which it will be used. 2. Appropriate checks and inspections are performed to assure that equipment is installed properly and consistent with design specifications and the manufacturer's instructions. 3. Maintenance materials, spare parts, and equipment are suitable for the process application for which they will be used. |  |  | OBSERVATION: The owner/operator failed to assure the following: in the construction of new plants and equipment that equipment as it is fabricated is suitable for the process application for which it will be used; appropriate checks and inspections are performed to assure that equipment is installed properly and consistent with design specifications and the manufacturer's instructions; maintenance materials, spare parts, and equipment are suitable for the process application for which they will be used. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has assured the following: appropriate checks and inspections are performed to assure that equipment is installed properly and consistent with design specifications and the manufacturer's instructions; maintenance materials, spare parts, and equipment are suitable for the process application for which they will be used. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010089 |  |  | Program Level 3: Management of Change - Procedures | Failure to establish and implement written procedures to manage changes (except for “replacements in kind”) to process chemicals, technology, equipment, and procedures, and changes to stationary sources that affect a covered process. | 19 CCR 4.5 2760.6(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 112 | Program 3 Prevention Program | Management of Change | Established and implemented written procedures to manage changes to a covered process | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to establish and implement written procedures to manage changes (except for “replacements in kind”) to process chemicals, technology, equipment, and procedures, and changes to stationary sources that affect a covered process. |  |  | OBSERVATION: The owner/operator failed to establish and implement written procedures to manage changes (except for “replacements in kind”) to process chemicals, technology, equipment, and procedures, and changes to stationary sources that affect a covered process. CORRECTIVE ACTION: Establish and implement written procedures to manage changes (except for “replacements in kind”) to process chemicals, technology, equipment, and procedures, and changes to stationary sources that affect a covered process and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010090 |  |  | Program Level 3: Management of Change - Procedures | Failure to ensure the following considerations are addressed in the Management of Change procedures prior to any change: 1. The technical basis for the proposed change; 2. Impact of change on safety and health; 3. Modifications to and/or development of new operating and maintenance procedures; 4. Necessary time period for the change; 5. Authorization requirements for the proposed change. | 19 CCR 4.5 2760.6(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 113 | Program 3 Prevention Program | Management of Change | MOC procedures address tech basis for change, H&S impact, procedures, time needed & authorization | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure the following considerations are addressed in the Management of Change procedures prior to any change: 1. The technical basis for the proposed change; 2. Impact of change on safety and health; 3. Modifications to and/or development of new operating and maintenance procedures; 4. Necessary time period for the change; 5. Authorization requirements for the proposed change. |  |  | OBSERVATION: The owner/operator failed to ensure the following considerations are addressed in the Management of Change procedures prior to any change: the technical basis for the proposed change; impact of change on safety and health; modifications to and/or development of new operating and maintenance procedures; necessary time period for the change; authorization requirements for the proposed change. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the following considerations are addressed in the Management of Change procedures prior to any change: the technical basis for the proposed change; impact of change on safety and health; modifications to and/or development of new operating and maintenance procedures; necessary time period for the change; authorization requirements for the proposed change. | [6 empty] | No | No | Yes | No
CalARP Program | Training | 5020010 |  |  | Program Level 3: Management of Change - Training | Failure to ensure employees involved in operating a process and maintenance and contract employees whose job tasks would be affected by a change in the process are informed and trained in the change prior to start-up of the process or affected part of the process. | 19 CCR 4.5 2760.6(c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 114 | Program 3 Prevention Program | Management of Change | Employees involved in operating and maintaining a process are informed and trained in any changes | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure employees involved in operating a process and maintenance and contract employees whose job tasks would be affected by a change in the process are informed and trained in the change prior to start-up of the process or affected part of the process. |  |  | OBSERVATION: The owner/operator failed to ensure employees involved in operating a process and maintenance and contract employees whose job tasks would be affected by a change in the process are informed and trained in the change prior to start-up of the process or affected part of the process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that employees involved in operating a process and maintenance and contract employees whose job tasks would be affected by a change in the process are informed and trained in the change. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010091 |  |  | Program Level 3: Management of Change - Process Safety Information | Failure to update process safety information if a management of change occurred that resulted in a change in the process safety information. | 19 CCR 4.5 2760.6(d) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 115 | Program 3 Prevention Program | Management of Change | Updated PSI when MOC resulted in a change to PSI | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update process safety information if a management of change occurred that resulted in a change in the process safety information. |  |  | OBSERVATION: The owner/operator failed to update process safety information when a management of change occurred that resulted in a change in the process safety information. CORRECTIVE ACTION: Update process safety information affected by the management of change and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010092 |  |  | Program Level 3: Management of Change - Operating Procedures | Failure to update operating procedures or practices if a management of change occurred that resulted in a change in the operating procedures or practices and/or resulted in a change in the written procedures to maintain the ongoing integrity of process equipment required by Section 2760.5, such procedures or practices shall be updated prior to start-up of the process. | 19 CCR 4.5 2760.6(e) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 116 | Program 3 Prevention Program | Management of Change | Updated operating/maintenance procedures or practices prior to startup if MOC resulted in a change | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update operating procedures or practices if a management of change occurred that resulted in a change in the operating procedures or practices and/or resulted in a change in the written procedures to maintain the ongoing integrity of process equipment required by Section 2760.5, such procedures or practices shall be updated prior to start-up of the process. |  |  | OBSERVATION: The owner/operator failed to update operating procedures or practices when a management of change occurred that resulted in a change in the procedures or practices. CORRECTIVE ACTION: Update operating procedures or practices affected by the management of change and submit a copy to the CUPA. | OBSERVATION: The owner/operator failed to update written procedures to maintain the ongoing integrity of process equipment when a management of change occurred that resulted in a change in the procedures. CORRECTIVE ACTION: Update procedures to maintain the ongoing integrity of process equipment affected by the management of change and submit a copy to the CUPA. | [5 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010093 |  |  | Program Level 3: Pre-Startup Safety Review | Failure to perform a pre-startup safety review for new stationary sources and for modified stationary sources when the modification is significant enough to require a change in the process safety information. | 19 CCR 4.5 2760.7(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 117 | Program 3 Prevention Program | Pre-Startup Review | Performed a pre-startup safety review when the modification required a change in the PSI | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform a pre-startup safety review for new stationary sources and for modified stationary sources when the modification is significant enough to require a change in the process safety information. |  |  | OBSERVATION: The owner/operator failed to perform a pre-startup safety review for a new stationary source when the modification is significant enough to require a change in the process safety information. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the following pre-startup safety requirements have been completed: construction and equipment was in accordance with design specifications; safety, operating, maintenance & emergency procedures are in place and are adequate; for new stationary sources, a PHA has been performed and recommendations have been resolved or implemented before startup, and modified stationary sources meet the requirements contained in the MOC; training of each employee involved in operating a process had been completed. | OBSERVATION: The owner/operator failed to perform a pre-startup safety review for a modified stationary source when the modification is significant enough to require a change in the process safety information. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the following pre-startup safety requirements have been completed: construction and equipment was in accordance with design specifications; safety, operating, maintenance & emergency procedures are in place and are adequate; for new stationary sources, a PHA has been performed and recommendations have been resolved or implemented before startup, and modified stationary sources meet the requirements contained in the MOC; training of each employee involved in operating a process had been completed. | [5 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010094 |  |  | Program Level 3: Pre-Startup Safety Review - General Requirements | Failure to ensure that the pre-startup safety review confirms, as a verification check, independent of the MOC process, the following prior to the introduction of a regulated substances to a process: 1. Construction and equipment is in accordance with design specifications. 2. Safety, operating, maintenance & emergency procedures are in place and are adequate. 3. For new stationary sources, a PHA has been performed and recommendations have been resolved or implemented before startup, and modified stationary sources meet the requirements contained in the MOC, Section 2760.6. 4. Training of each employee involved in operating a process had been completed. | 19 CCR 4.5 2760.7(b) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 118 | Program 3 Prevention Program | Pre-Startup Review | Pre-startup safety review addresses requirements in Section 2760.7(b) prior to introduction of a RS | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that the pre-startup safety review confirms, as a verification check, independent of the MOC process, the following prior to the introduction of a regulated substances to a process: 1. Construction and equipment is in accordance with design specifications. 2. Safety, operating, maintenance & emergency procedures are in place and are adequate. 3. For new stationary sources, a PHA has been performed and recommendations have been resolved or implemented before startup, and modified stationary sources meet the requirements contained in the MOC, Section 2760.6. 4. Training of each employee involved in operating a process had been completed. |  |  | OBSERVATION: The owner/operator failed to ensure that the pre-startup safety review confirmed the following prior to the introduction of a regulated substances to a process: construction and equipment is in accordance with design specifications; safety, operating, maintenance & emergency procedures are in place and are adequate; for new stationary sources, a PHA has been performed and recommendations have been resolved or implemented before startup, and modified stationary sources meet the requirements contained in the MOC; training of each employee involved in operating a process had been completed. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you have addressed all of the deficiencies noted. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/ Documentation | 5010095 |  |  | Program Level 3: Compliance Audits - Certification | Failure of the owner or operator to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 6 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. | 19 CCR 4.5 2760.8(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 119 | Program 3 Prevention Program | Compliance Audits | Certified and evaluated compliance with the provisions of this article at least every three years | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the owner or operator to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 6 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. |  |  | OBSERVATION: The owner/operator failed to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 6 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. CORRECTIVE ACTION: Submit a certification to the CUPA that the owner/operator has evaluated compliance with the provisions of 19 CCR 4.5 Article 6 at least every three years to verify that the procedures and practices developed under chapter 19 CCR 4.5 are adequate and are being followed. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010096 |  |  | Program Level 3: Compliance Audits - Knowledgeable Person | Failure to ensure that the compliance audit is conducted by at least one person knowledgeable in the process. | 19 CCR 4.5 2760.8(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 120 | Program 3 Prevention Program | Compliance Audits | Compliance audit conducted by at least one person knowledgeable in the process | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that the compliance audit is conducted by at least one person knowledgeable in the process. |  |  | OBSERVATION: The owner/operator failed to ensure that the compliance audit is conducted by at least one person knowledgeable in the process. CORRECTIVE ACTION: Conduct the compliance audit with at least one person knowledgeable in the process. Develop a report of the compliance audit findings, including appropriate responses to each of the findings and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010097 |  |  | Program Level 3: Compliance Audits - Report | Failure to develop and have available for review, a report of the scope, methods used, results and findings of the audit. | 19 CCR 4.5 2760.8(c) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 121 | Program 3 Prevention Program | Compliance Audits | Developed and made available, a report of the scope, methods used, results and findings of the audit | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and have available for review, a report of the scope, methods used, results and findings of the audit. |  |  | OBSERVATION: The owner/operator failed to develop and have available for review, a report of the scope, methods used, results and findings of the audit. CORRECTIVE ACTION: Develop a report of the scope, methods used, results and findings of the audit and submit a copy to the UPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010098 |  |  | Program Level 3: Compliance Audits - Findings/Resolutions | Failure to: 1. Promptly determine and document an appropriate response to each of the findings of the compliance audit; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings. Otherwise these responses shall be completed one and one-half (1.5) years after performing the compliance audit, or the next planned turnaround for items requiring a turnaround (these timelines shall not apply to any compliance audit completed prior to January 1, 2015); 3. Document the actual completion dates when deficiencies were corrected. | 19 CCR 4.5 2760.8(d) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 122 | Program 3 Prevention Program | Compliance Audits | Promptly determined and documented response to audit findings, including correction of deficiencies | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to: 1. Promptly determine and document an appropriate response to each of the findings of the compliance audit; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings. Otherwise these responses shall be completed one and one-half (1.5) years after performing the compliance audit, or the next planned turnaround for items requiring a turnaround (these timelines shall not apply to any compliance audit completed prior to January 1, 2015); 3. Document the actual completion dates when deficiencies were corrected. |  |  | OBSERVATION: The owner/operator failed to determine and document an appropriate response to each of the findings of the compliance audit and document the actual completion date when deficiencies were corrected, and/or failed to do so within the required time frame. CORRECTIVE ACTION: Document an appropriate response to each of the findings of the compliance audit, including documented completion dates when deficiencies were corrected and submit a copy to the UPA. | OBSERVATION: The owner/operator failed to document actual completion dates when deficiencies identified in the compliance audit were corrected. CORRECTIVE ACTION: Document actual completion dates when deficiencies identified in the compliance audit were corrected and submit a copy to the CUPA. | [5 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010099 |  |  | Program Level 3: Compliance Audits - Retention | Failure to retain the two most recent compliance audit reports. | 19 CCR 4.5 2760.8(e) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 123 | Program 3 Prevention Program | Compliance Audits | Retained the two most recent compliance audit reports | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain the two most recent compliance audit reports. |  |  | OBSERVATION: The owner/operator failed to retain the two most recent compliance audit reports conducted. CORRECTIVE ACTION: Submit a copy of the two most recent compliance audit reports to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010100 |  |  | Program Level 3: Incident Investigation | Failure to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release of a regulated substance. | 19 CCR 4.5 2760.9(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 124 | Program 3 Prevention Program | Incident Investigation | Investigated each incident that resulted or could reasonably have resulted in a catastrophic release | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release of a regulated substance. |  |  | OBSERVATION: The owner/operator failed to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release. CORRECTIVE ACTION: Investigate the incident and submit a copy of the investigation findings with recommendations to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010101 |  |  | Program Level 3: Incident Investigation - Promptness | Failure to initiate an incident investigation as promptly as possible, but not later than 48 hours following the incident. | 19 CCR 4.5 2760.9(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 125 | Program 3 Prevention Program | Incident Investigation | Initiated incident investigations within 48 hours of the incident | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to initiate an incident investigation as promptly as possible, but not later than 48 hours following the incident. |  |  | OBSERVATION: The owner/operator failed to initiate an incident investigations within 48 hours of the incident. CORRECTIVE ACTION: Submit a statement of the CUPA demonstrating how incident investigations will be initiated within 48 hours of the incident. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010102 |  |  | Program Level 3: Incident Investigation - Team/Knowledgeable Person | Failure to establish an incident investigation team that consists of at least one person knowledgeable in the process involved, including a contract employee if the incident involved work of the contractor, and other persons with appropriate knowledge and experience to thoroughly investigate and analyze the incident. | 19 CCR 4.5 2760.9(c) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 126 | Program 3 Prevention Program | Incident Investigation | Incident investigation team consists of a person with knowledge and experience in the process | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to establish an incident investigation team that consists of at least one person knowledgeable in the process involved, including a contract employee if the incident involved work of the contractor, and other persons with appropriate knowledge and experience to thoroughly investigate and analyze the incident. |  |  | OBSERVATION: The owner/operator failed to establish an incident investigation team that consists of at least one person knowledgeable in the process involved, including a contract employee if the incident involved work of the contractor, and other persons with appropriate knowledge and experience to thoroughly investigate and analyze the incident. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that an incident investigation team has been established and consists of at least one person knowledgeable in the process involved, including a contract employee if the incident involved work of the contractor, and other persons with appropriate knowledge and experience to thoroughly investigate and analyze the incident. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010103 |  |  | Program Level 3: Incident Investigation - Report | Failure to prepare a report at the conclusion of the investigation which includes at a minimum: 1. Date the investigation began; 2. A description of the incident, including all of the data required under 2750.9(b); and, 3. Recommendations resulting from the investigation. | 19 CCR 4.5 2760.9(d) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 127 | Program 3 Prevention Program | Incident Investigation | Prepared an incident investigation report that includes the date, description and recommendations | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a report at the conclusion of the investigation which includes at a minimum: 1. Date the investigation began; 2. A description of the incident, including all of the data required under 2750.9(b); and, 3. Recommendations resulting from the investigation. |  |  | OBSERVATION: The owner/operator failed to prepare a report at the conclusion of the investigation that includes the date the investigation began; A description of the incident, including all of the data required under 2750.9(b); and recommendations resulting from the investigation. CORRECTIVE ACTION: Prepare and submit a copy of the report of the investigation to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010104 |  |  | Program Level 3: Incident Investigation - Findings/Resolutions | Failure to: 1. Establish a system to promptly address and resolve the incident report findings and recommendations; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings and recommendations. Otherwise these resolutions shall be completed no later than one and one-half (1.5) years after completion of the incident investigation, or two (2) years after the date of the incident, whichever is the earlier of the two dates, or the next planned turnaround for those items requiring turnaround. 3. Failure to document resolutions and corrective actions with actual completion dates. | 19 CCR 4.5 2760.9(e) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Revised | 128 | Program 3 Prevention Program | Incident Investigation | Established a system to promptly address and resolve the investigation findings and recommendations | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to: 1. Establish a system to promptly address and resolve the incident report findings and recommendations; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings and recommendations. Otherwise these resolutions shall be completed no later than one and one-half (1.5) years after completion of the incident investigation, or two (2) years after the date of the incident, whichever is the earlier of the two dates, or the next planned turnaround for those items requiring turnaround. 3. Failure to document resolutions and corrective actions with actual completion dates. |  |  | OBSERVATION: The owner/operator failed to establish a system to address and resolve the incident report findings and recommendations, including documentation of the resolutions and corrective actions with actual completion dates, and/or failed to resolve the findings and recommendations within the required time frame. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating a system to promptly address and resolve the incident report findings and recommendations has been established. Address and resolve the investigation findings and recommendations and submit a copy of documented resolutions and corrective actions with actual completion dates to the UPA. | OBSERVATION: The owner/operator failed to document the incident investigation report resolutions and corrective actions with actual completion dates. CORRECTIVE ACTION: Address and resolve the investigation findings and recommendations and submit a copy of documented resolutions and corrective actions with actual completion dates to the CUPA. | [5 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010105 |  |  | Program Level 3: Incident Investigation - Affected Personnel | Failure to review the incident investigation report with all affected personnel whose job tasks are relevant to the incident findings including contract employees where applicable. | 19 CCR 4.5 2760.9(f) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 129 | Program 3 Prevention Program | Incident Investigation | Reviewed the incident investigation report with all affected personnel | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to review the incident investigation report with all affected personnel whose job tasks are relevant to the incident findings including contract employees where applicable. |  |  | OBSERVATION: The owner/operator failed to review the incident investigation report with all affected personnel whose job tasks are relevant to the incident findings including contract employees where applicable. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the incident investigation report has been reviewed with all affected personnel whose job tasks are relevant to the incident findings including contract employees where applicable. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010106 |  |  | Program Level 3: Incident Investigation - Retention | Failure to retain the incident investigation reports for five years. | 19 CCR 4.5 2760.9(g) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 130 | Program 3 Prevention Program | Incident Investigation | Retained the incident investigation reports for five years | 58 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain the incident investigation reports for five years. |  |  | OBSERVATION: The owner/operator failed to retain investigation reports for five years. CORRECTIVE ACTION: Submit a copy of the missing investigation reports for the last five years to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010107 |  |  | Program Level 3: Employee Participation - Plan | Failure to develop a written plan of action regarding the implementation of employee participation. | 19 CCR 4.5 2760.10(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 131 | Program 3 Prevention Program | Employee Participation | Developed a written plan of action regarding the implementation of employee participation | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop a written plan of action regarding the implementation of employee participation. |  |  | OBSERVATION: The owner/operator failed to develop a written plan of action regarding the implementation of employee participation. CORRECTIVE ACTION: Develop and submit a written plan of action regarding the implementation of employee participation to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010108 |  |  | Program Level 3: Employee Participation - Employee Consultation | Failure to consult with employees and their representatives on the conduct and development of the Process Hazard Analysis and on the development of the other elements of process safety management. | 19 CCR 4.5 2760.10(b) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 132 | Program 3 Prevention Program | Employee Participation | Consulted with employees/representatives on conduct and development of the PHA and PSM elements | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to consult with employees and their representatives on the conduct and development of the Process Hazard Analysis and on the development of the other elements of process safety management. |  |  | OBSERVATION: The owner/operator failed to consult with employees and their representatives on the conduct and development of the Process Hazard Analysis and on the development of the other elements of process safety management. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has consulted with employees and their representatives on the conduct and development of the Process Hazard Analysis and on the development of the other elements of process safety management. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010109 |  |  | Program Level 3: Employee Participation - Access | Failure to provide employees and their representatives with access to the Process Hazards Analysis and to all other information required to be developed under 19 CCR Chapter 4.5. | 19 CCR 4.5 2760.10(c) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 133 | Program 3 Prevention Program | Employee Participation | Provided employees/representatives with access to the PHA and all other CalARP information | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide employees and their representatives with access to the Process Hazards Analysis and to all other information required to be developed under 19 CCR Chapter 4.5. |  |  | OBSERVATION: The owner/operator failed to provide employees and their representatives with access to the Process Hazards Analysis and all other information required to be developed under Title 19, Division 2, Chapter 4.5. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has provided employees and their representatives with access to the Process Hazards Analysis and all other information required to be developed under Title 19, Division 2, Chapter 4.5. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010110 |  |  | Program Level 3: Hot Work Permit | Failure to issue a hot work permit for hot work operations conducted on or near a covered process. | 19 CCR 4.5 2760.11(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 134 | Program 3 Prevention Program | Hot Work Permit | Issued a hot work permit for hot work operations conducted on or near a covered process | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to issue a hot work permit for hot work operations conducted on or near a covered process. |  |  | OBSERVATION: The owner/operator failed to issue a hot work permit for hot work operations conducted on or near a covered process. CORRECTIVE ACTION: Submit a statement to the CUPA demonstrating the owner/operator has reviewed the fire prevention and protection requirements in 8 CCR 5189 (Process Safety Management of Acutely Hazardous Materials) and will issue hot work permits for all future hot work operations. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010111 |  |  | Program Level 3: Hot Work Permit - General Requirements | Failure to ensure the hot work permit documents the following: 1. The fire prevention and protection requirements in 8 CCR 5189 (Process Safety Management of Acutely Hazardous Materials) have been implemented prior to beginning the hot work operations. 2. The date(s) authorized for hot work. 3. The object on which hot work is to be performed identified. | 19 CCR 4.5 2760.11(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 135 | Program 3 Prevention Program | Hot Work Permit | Hot work permit documents the requirements of 8 CCR 5189, date of work, & object being worked on | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure the hot work permit documents the following: 1. The fire prevention and protection requirements in 8 CCR 5189 (Process Safety Management of Acutely Hazardous Materials) have been implemented prior to beginning the hot work operations. 2. The date(s) authorized for hot work. 3. The object on which hot work is to be performed identified. |  |  | OBSERVATION: The owner/operator failed to ensure the hot work permit documents the following: fire prevention and protection requirements in 8 CCR 5189 (Process Safety Management of Acutely Hazardous Materials) have been implemented prior to beginning the hot work operations; date(s) authorized for hot work; object on which hot work is to be performed identified. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating future hot work permits document the following: fire prevention and protection requirements in 8 CCR 5189 (Process Safety Management of Acutely Hazardous Materials) have been implemented prior to beginning the hot work operations; date(s) authorized for hot work; object on which hot work is to be performed identified. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010112 |  |  | Program Level 3: Hot Work Permit - Retention | Failure to keep the hot work permit on file until completion of the hot work operations. | 19 CCR 4.5 2760.11(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 136 | Program 3 Prevention Program | Hot Work Permit | Hot work permit kept on file until completion of the hot work operations | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to keep the hot work permit on file until completion of the hot work operations. |  |  | OBSERVATION: The owner/operator failed to keep the hot work permit on file until completion of the hot work operations. CORRECTIVE ACTION: Submit a statement to the CUPA demonstrating the hot work permit will be kept on file until completion of the hot work operations. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010113 |  |  | Program Level 3: Contractors | Failure to perform the following: 1. Obtain and evaluate information regarding the contract owner or operator’s safety performance and programs when selecting a contractor. 2. Inform the contract owner or operator of the known potential fire, explosion, or toxic release hazards related to the contractor’s work and the process. 3. Explain to the contract owner or operator the applicable provisions of Article 7 (Emergency Response Program). 4. Develop and implement safe work practices consistent with the Section 2760.3(d) (operating procedures), to control the entrance, presence, and exit of the contract owner or operator and contract employees in covered process areas. | 19 CCR 4.5 2760.12(b) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 137 | Program 3 Prevention Program | Contractors | Complied with all contractor requirements | 41 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform the following: 1. Obtain and evaluate information regarding the contract owner or operator’s safety performance and programs when selecting a contractor. 2. Inform the contract owner or operator of the known potential fire, explosion, or toxic release hazards related to the contractor’s work and the process. 3. Explain to the contract owner or operator the applicable provisions of Article 7 (Emergency Response Program). 4. Develop and implement safe work practices consistent with the Section 2760.3(d) (operating procedures), to control the entrance, presence, and exit of the contract owner or operator and contract employees in covered process areas. |  |  | OBSERVATION: The owner/operator failed to do one or more of the following: Obtain and evaluate information regarding the contract owner or operator’s safety performance and programs when selecting a contractor; Inform the contract owner or operator of the known potential fire, explosion, or toxic release hazards related to the contractor’s work and the process; Explain to the contract owner or operator the applicable provisions of Article 7 (Emergency Response Program); Develop and implement safe work practices consistent with the Section 2760.3(d) (operating procedures), to control the entrance, presence, and exit of the contract owner or operator and contract employees in covered process areas. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has corrected the deficiencies noted. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010114 |  |  | Program Level 3: Contractors - Performance Evaluation | Failure to periodically evaluate and document the evaluation of the performance of the contract owner or operator in fulfilling the following: 1. Each contract employee is trained in the work practices necessary to safely perform his or her job. 2. Each contract employee is instructed in the known potential fire, explosion, or toxic release hazards related to his or her job and the process, and the applicable provisions of the emergency action plan. 3. Document that each contract employee has received and understood the training required by this section. 4. Prepare a training record which contains the identity of the contract employee, date of training, and the means used to verify that the employee understood the training. 5. Each contract employee follows the safety rules of the stationary source including the safe work practices required by Section 2760.3(d) (operating procedures). 6. Advise the owner or operator of any unique hazards presented by the contract owner or operator’s work, or of any hazards found by the contract owner or operator’s work. | 19 CCR 4.5 2760.12(b)(5) | 2022-07-01 | 2024-09-30 | 2024-09-30 | Revised | 138 | Program 3 Prevention Program | Contractors | Periodically evaluated the performance of the contract owner or operator and documented evaluation | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to periodically evaluate and document the evaluation of the performance of the contract owner or operator in fulfilling the following: 1. Each contract employee is trained in the work practices necessary to safely perform his or her job. 2. Each contract employee is instructed in the known potential fire, explosion, or toxic release hazards related to his or her job and the process, and the applicable provisions of the emergency action plan. 3. Document that each contract employee has received and understood the training required by this section. 4. Prepare a training record which contains the identity of the contract employee, date of training, and the means used to verify that the employee understood the training. 5. Each contract employee follows the safety rules of the stationary source including the safe work practices required by Section 2760.3(d) (operating procedures). 6. Advise the owner or operator of any unique hazards presented by the contract owner or operator’s work, or of any hazards found by the contract owner or operator’s work. |  |  | OBSERVATION: Owner/operator failed to periodically evaluate and document the evaluation of the contractor's performance for the following: contract employees are trained in the work practices to safely perform his or her job; each contract employee is instructed in the known potential fire, explosion, or toxic release hazards related to the job and process, and the applicable provisions of the emergency action plan; documentation that each employee received and understood the training; records with the identity of the contract employee, date of training, and the means used to verify employee understood the training; contract employees follow the safety rules and safe work practices required by §2760.3(d); advise the owner/operator of any hazards presented by the contractor’s work, or of any hazards found by the contract owner or operator’s work. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has evaluated the performance of the contract owner or operator as described above. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010127 |  |  | Program level 4: Process Safety Information - Compilation | Failure to develop and maintain a compilation of written process safety information before conducting any PHA, Hierarchy of Hazard Control Analysis, Safeguard Protection Analysis, or Damage Mechanism Review, as required. | 19 CCR 4.5 2762.1(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 139 | Program 4 Prevention Program | Process Safety Information | Compiled written process safety information before a PHA, HCA, SPA, as required | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and maintain a compilation of written process safety information before conducting any PHA, Hierarchy of Hazard Control Analysis, Safeguard Protection Analysis, or Damage Mechanism Review, as required. |  |  | OBSERVATION: Owner/Operator failed to develop and maintain a compilation of written process safety information before conducting any PHA, Hierarchy of Hazard Control Analysis, Safeguard Protection Analysis, or Damage Mechanism Review. CORRECTIVE ACTION: Owner/operator will establish revise written procedures to ensure the compilation of written process safety information before conducting any PHA, Hierarchy of Hazard Control Analysis, Safeguard Protection Analysis, or Damage Mechanism Review; compile the process safety information as required in 2762.1; submit documentation to UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010128 |  |  | Program level 4: Process Safety Information - Hazards | Failure to ensure information pertaining to hazards of substances used in, present in or produced by the process includes at least the following: (1) Toxicity information, including acute and chronic health hazards; (2) California Permissible exposure limits (PELs); (3) For regulated substances: American Conference of Governmental Industrial Hygienists (ACGIH) Emergency Response Planning Guideline values, U.S. EPA Acute Exposure Guideline Levels (AEGLs), and the California Office of Environmental Health Hazard Assessment (OEHHA) acute and eight-hour Reference Exposure Levels (RELs); (4) Physical data; (5) Corrosion data; (6) Thermal and chemical stability data; (7) Reactivity data; and (8) Hazardous effects of incompatible mixtures that could foreseeably occur. | 19 CCR 4.5 2762.1(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 140 | Program 4 Prevention Program | Process Safety Information | Compiled info on hazards of substances used in, present in, or produced as required | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure information pertaining to hazards of substances used in, present in or produced by the process includes at least the following: (1) Toxicity information, including acute and chronic health hazards; (2) California Permissible exposure limits (PELs); (3) For regulated substances: American Conference of Governmental Industrial Hygienists (ACGIH) Emergency Response Planning Guideline values, U.S. EPA Acute Exposure Guideline Levels (AEGLs), and the California Office of Environmental Health Hazard Assessment (OEHHA) acute and eight-hour Reference Exposure Levels (RELs); (4) Physical data; (5) Corrosion data; (6) Thermal and chemical stability data; (7) Reactivity data; and (8) Hazardous effects of incompatible mixtures that could foreseeably occur. |  |  | OBSERVATION: Owner/operator failed to compile and maintain up-to-date written process safety information pertaining to the hazards of the regulated substances in the process that includes: toxicity information; for regulated substances, ACGIH Emergency Response Planning Guideline values, US EPA Acute Exposure Guideline Levels, California OEHHA acute and eight - hour Reference Exposure Levels, California Permissible exposure limits; physical data; reactivity data; corrosivity data; thermal and chemical stability data; hazardous effects of inadvertent mixing of different materials that could foreseeably occur. CORRECTIVE ACTION: Compile up-to-date written process safety information for the hazards of hazardous substances that includes: toxicity information; permissible exposure limits; physical data; reactivity data; corrosivity data; thermal and chemical stability data; hazardous effects of inadvertent mixing of different materials; submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010129 |  |  | Program level 4: Process Safety Information - Technology | Failure to ensure information pertaining to the technology of the process includes at least the following items: (1) A block flow diagram or simplified process flow diagram; (2) Process chemistry; (3) Maximum intended inventory; (4) Safe upper and lower limits for process variables such as temperatures, pressures, flows, levels, and compositions; and, (5) The consequences of deviations, including chemical mixing or reactions that may affect the safety and health of employees or the public. | 19 CCR 4.5 2762.1(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 141 | Program 4 Prevention Program | Process Safety Information | Compiled Information on the technology of the process as required | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure information pertaining to the technology of the process includes at least the following items: (1) A block flow diagram or simplified process flow diagram; (2) Process chemistry; (3) Maximum intended inventory; (4) Safe upper and lower limits for process variables such as temperatures, pressures, flows, levels, and compositions; and, (5) The consequences of deviations, including chemical mixing or reactions that may affect the safety and health of employees or the public. |  |  | OBSERVATION: Owner/operator failed to compile written process safety information concerning the technology of the process that includes: a block flow diagram or simplified process flow diagram; process chemistry; maximum intended inventory; safe upper and lower limits for such items as temperatures, pressures, flows or compositions; an evaluation of the consequences of deviations that may affect the safety and health of employees or the public. CORRECTIVE ACTION: Compile written process safety information concerning the technology of the process that includes: a block flow diagram or simplified process flow diagram; process chemistry; maximum intended inventory; safe upper and lower limits for such items as temperatures, pressures, flows or compositions; an evaluation of the consequences of deviations that may affect the safety and health of employees and the public and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010130 |  |  | Program level 4: Process Safety Information - Process Equipment | Failure to ensure information pertaining to the process equipment at least includes the following information : (1) Materials of construction; (2) Piping and instrument diagrams (P&IDs); (3) Electrical classification; (4) Relief system design and design basis; (5) Ventilation system design; (6) Design codes and standards employed, including design conditions and operating limits; (7) Material and energy balances for processes built after June 21, 1999 and previously covered under Program 3, and material and energy balances for all other processes as of the effective date of Article 6.5; (8) Safety systems, such as interlocks, detection and suppression systems; and (9) Electrical supply and distribution systems. | 19 CCR 4.5 2762.1(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 142 | Program 4 Prevention Program | Process Safety Information | Compiled Information on process equipment as required | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure information pertaining to the process equipment at least includes the following information : (1) Materials of construction; (2) Piping and instrument diagrams (P&IDs); (3) Electrical classification; (4) Relief system design and design basis; (5) Ventilation system design; (6) Design codes and standards employed, including design conditions and operating limits; (7) Material and energy balances for processes built after June 21, 1999 and previously covered under Program 3, and material and energy balances for all other processes as of the effective date of Article 6.5; (8) Safety systems, such as interlocks, detection and suppression systems; and (9) Electrical supply and distribution systems. |  |  | OBSERVATION: Owner/operator failed to compile written information on process equipment including: materials of construction; P&IDs; electrical classification; relief system design/design basis; ventilation system design; design codes & standards - design conditions & operating limits; material & energy balances for processes built after June 21, 1999 & under Program 3, material & energy balances of all other processes; safety systems (e.g., interlocks, detection, or suppression systems); electrical supply/distribution systems. CORRECTIVE ACTION: Owner/operator will compile process safety info for equipment including: construction materials; P&IDs; electrical classification; relief system design/design basis; ventilation system design; design codes & standards; material & energy balances for processes after June 21, 1999 & Program 3; safety systems (e.g., interlocks, detection, or suppression systems), electrical supply/distribution systems. & submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010131 |  |  | Program level 4: Process Safety Information - Equipment Compliance Documentation | Failure to document that process equipment complies with recognized and generally accepted good engineering practices (RAGAGEP), where RAGAGEP has been established for that process equipment, or with other more protective internal practices that ensure safe operation. Failure to document that the equipment is designed, constructed, installed, maintained, inspected, tested and operated in a safe manner for installation of new process equipment for which no RAGAGEP exists. | 19 CCR 4.5 2762.1(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 143 | Program 4 Prevention Program | Process Safety Information | Compiled Info on equipment with RAGAGEP - protective internal practice | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document that process equipment complies with recognized and generally accepted good engineering practices (RAGAGEP), where RAGAGEP has been established for that process equipment, or with other more protective internal practices that ensure safe operation. Failure to document that the equipment is designed, constructed, installed, maintained, inspected, tested and operated in a safe manner for installation of new process equipment for which no RAGAGEP exists. |  |  | OBSERVATION: Owner/operator failed to document the following: (1) that equipment complies with recognized and generally accepted good engineering practices (RAGAGEP); (2) more protective internal practice that ensures safe operation; (3) failure to document that new process equipment for which no RAGAGEP exists is designed, constructed, installed, maintained, inspected, tested and operated in a safe manner. CORRECTIVE ACTION: Owner/operator will demonstrate that equipment complies with recognized and generally accepted good engineering practices or a protective internal practice that ensures safe operation and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010132 |  |  | Program level 4: Process Safety Information - Existing Equipment Compliance Documentation | Failure to document that the equipment is designed, constructed, installed, maintained, inspected, tested and operated in a safe manner for existing process equipment that was designed and constructed in accordance with codes, standards, or practices that are no longer in general use. | 19 CCR 4.5 2762.1(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 144 | Program 4 Prevention Program | Process Safety Information | Compiled information on compliance of existing equipment | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document that the equipment is designed, constructed, installed, maintained, inspected, tested and operated in a safe manner for existing process equipment that was designed and constructed in accordance with codes, standards, or practices that are no longer in general use. |  |  | OBSERVATION: Owner/operator failed to determine and document that existing equipment designed and constructed in accordance with codes, standards, or practices that are no longer in general use are designed, maintained, inspected, tested, and operating in a safe manner. CORRECTIVE ACTION: Owner/operator will determine and document that existing equipment are designed, maintained, inspected, tested, operated in a safe manner, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010133 |  |  | Program level 4: Process Hazard Analysis (PHA) - General | Failure to perform and document an effective PHA appropriate to the complexity of each process in order to identify, evaluate, and control hazards associated with each process. Failed to cover all modes of operation, as set forth in subsection 2762.3 (a)(1), in the PHA. Failed to determine and document the priority order for conducting PHAs based on the extent of process hazards, the number of potentially affected people, the age of the process and the process operating history. | 19 CCR 4.5 2762.2(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 145 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Performed and documented effective PHA appropriate to the complexity of each process | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform and document an effective PHA appropriate to the complexity of each process in order to identify, evaluate, and control hazards associated with each process. Failed to cover all modes of operation, as set forth in subsection 2762.3 (a)(1), in the PHA. Failed to determine and document the priority order for conducting PHAs based on the extent of process hazards, the number of potentially affected people, the age of the process and the process operating history. |  |  | OBSERVATION: Owner/operator failed to perform an effective PHA including: a PHA appropriate to the complexity of each process including each process not previously addressed under Program 3 within three years and address all modes of operation as set forth in subsection 2762.3 (a)(1); failed to determine and document a priority order for conducting PHA's based on the process hazards, number of potentially affected people, the age of the process, and the process operating history. CORRECTIVE ACTION: Owner/operator shall develop a written process for prioritizing PHAs based on the process hazards, the number of affected people, the age of the process, and operating history. Owner/Operator shall perform an effective PHA and document the PHA findings and recommendations and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010134 |  |  | Program level 4: Process Hazard Analysis (PHA) - Methodology | Failure to work with the UPA in selecting and using at least one of the following methods: (1) What-If; (2) Checklist; (3) What-If / Checklist; (4) Hazard and Operability Study (HAZOP); (5) Failure Mode and Effects Analysis (FMEA); (6) Fault Tree Analysis; (7) Other PHA methods recognized by engineering organizations or governmental agencies. | 19 CCR 4.5 2762.2(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 146 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Worked with the UPA in selecting and using at least one of the approved PHA methods | 83 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to work with the UPA in selecting and using at least one of the following methods: (1) What-If; (2) Checklist; (3) What-If / Checklist; (4) Hazard and Operability Study (HAZOP); (5) Failure Mode and Effects Analysis (FMEA); (6) Fault Tree Analysis; (7) Other PHA methods recognized by engineering organizations or governmental agencies. |  |  | OBSERVATION: Owner/operator failed to work with the UPA in selecting and using one of the following methods for performing the PHA: (1) What-if; (2) Checklist; (3) What if/Checklist; (4) Hazard and Operability Study (HAZOP); (5) Failure Mode Effects Analysis (FMEA); (6) Fault Tree Analysis; (7) Other PHA methods recognized by engineering organizations or governmental agencies. CORRECTIVE ACTION: Owner/Operator shall contact and coordinate with the UPA before selecting and using a PHA methodology. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010135 |  |  | Program level 4: Process Hazard Analysis (PHA) - Elements | Failure to ensure the PHA addresses: (1) The hazards of the process; (2) Previous publicly documented incidents in the petroleum refinery and petrochemical industry sector that are relevant to the PHA; (3) Damage Mechanism Review reports pursuant to subsection 2762.5(e) that are applicable to the process units; (4) Hierarchy of Hazard Control Analysis reports pursuant to section 2762.13 that are applicable to the process units; (5) A review of Management of Change documents completed since the last PHA that apply to the process unit. (6) Potential consequences of failures of process equipment; (7) Facility siting, including the placement of processes, equipment, buildings, employee occupancies and work stations in order to effectively protect employees and the public from process safety hazards; (8) Human factors as required under section 2762.15; (9) A qualitative evaluation of the types, severity, and likelihood of possible incidents that could result from a failure of a process or of process equipment; (10) The potential effects of external events, including seismic events, if applicable; and (11) The findings of incident investigations relevant to the process. | 19 CCR 4.5 2762.2(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 147 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Ensured the PHA addresses hazards, incidents, DMRs, HCAs, MOCs, failure potential, siting, etc | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PHA addresses: (1) The hazards of the process; (2) Previous publicly documented incidents in the petroleum refinery and petrochemical industry sector that are relevant to the PHA; (3) Damage Mechanism Review reports pursuant to subsection 2762.5(e) that are applicable to the process units; (4) Hierarchy of Hazard Control Analysis reports pursuant to section 2762.13 that are applicable to the process units; (5) A review of Management of Change documents completed since the last PHA that apply to the process unit. (6) Potential consequences of failures of process equipment; (7) Facility siting, including the placement of processes, equipment, buildings, employee occupancies and work stations in order to effectively protect employees and the public from process safety hazards; (8) Human factors as required under section 2762.15; (9) A qualitative evaluation of the types, severity, and likelihood of possible incidents that could result from a failure of a process or of process equipment; (10) The potential effects of external events, including seismic events, if applicable; and (11) The findings of incident investigations relevant to the process. |  |  | OBSERVATION: Owner/operator failed to ensure the PHA addresses: (1) The hazards of the process; (2) Incidents in the petroleum industry or petrochemical industry relevant to the PHA; (3) DMR reports applicable to the process units; (4) HCA reports applicable to the process units; (5) A review of MOC documents that have been completed since the last PHA applicable to the process units; (6) Consequences of failures of process equipment; (7) Facility siting, including the placement of processes, equipment, buildings, employee occupancies and work stations to effectively protect employees and the public: (8) Human factors; (9) A qualitative evaluation of the types, severity, and likelihood of possible incidents that could result from a failure of a process or of process equipment; (10) The potential effects of external events; & (11) Applicable incident investigation findings. CORRECTIVE ACTION: Owner/operator shall perform an effective PHA and submit documentations to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010136 |  |  | Program level 4: Process Hazard Analysis (PHA) - Team Qualifications | Failure to ensure the PHA is performed by a team with expertise in engineering and process operations and to include at least one operating employee who currently works or provides training in the unit, and has experience and knowledge specific to the process being evaluated. Failure to have the team also include one member with expertise in the specific PHA method being used. Failure to have the team consult with individuals with expertise in damage mechanisms, process chemistry, and control systems, as necessary. Failure to provide for employee participation in this process, pursuant to section 2762.10. | 19 CCR 4.5 2762.2(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 148 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | PHA is performed by a team with expertise and complies with requirements | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PHA is performed by a team with expertise in engineering and process operations and to include at least one operating employee who currently works or provides training in the unit, and has experience and knowledge specific to the process being evaluated. Failure to have the team also include one member with expertise in the specific PHA method being used. Failure to have the team consult with individuals with expertise in damage mechanisms, process chemistry, and control systems, as necessary. Failure to provide for employee participation in this process, pursuant to section 2762.10. |  |  | OBSERVATION: Owner/operator failed to perform the Process Hazard Analysis using a team with expertise in engineering and process operations, including at least one employee who has experience and knowledge specific to the process being evaluated, and one member who is knowledgeable in the specific Process Hazard Analysis methodology being used. CORRECTIVE ACTION: Conduct a Process Hazard Analysis using a team with expertise in engineering and process operations, including at least one employee selected pursuant to the employee participation process specified in 2762.10 who has experience and knowledge specific to the process being evaluated, one member who is knowledgeable in the specific Process Hazard Analysis methodology being used, consult with individuals knowledgeable in damage mechanisms, process chemistry, and control systems and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010137 |  |  | Program level 4: Process Hazard Analysis (PHA) - SPA | Failure to perform a Safeguard Protection Analysis (SPA) pursuant to section 2762.2.1 for each scenario in the PHA that identifies the potential for a major incident. Failure to append SPA recommendations to the PHA report, upon completion of the SPA. | 19 CCR 4.5 2762.2(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 149 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Ensured SPA is performed for scenarios in PHA identifying major incidents | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform a Safeguard Protection Analysis (SPA) pursuant to section 2762.2.1 for each scenario in the PHA that identifies the potential for a major incident. Failure to append SPA recommendations to the PHA report, upon completion of the SPA. |  |  | OBSERVATION: Owner/operator failed to perform a Safeguard Protection Analysis pursuant to section 2762.2.1 for each major incident that identified the potential for a major incident. Failure to append the Safeguard Protection Analysis to the PHA report upon completion. CORRECTIVE ACTION: Owner/Operator will conduct Safeguard Protection Analysis for each scenario identified in the PHA with the potential of a major incident as an appendix and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010138 |  |  | Program level 4: Process Hazard Analysis (PHA) - HCA | Failure to conduct in a timely manner a Hierarchy of Hazard Control Analysis pursuant to section 2762.13 for all recommendations made by the PHA team for each scenario that identifies the potential for a major incident. | 19 CCR 4.5 2762.2(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 150 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Used HCA for recommendations for scenarios identifying major incidents | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to conduct in a timely manner a Hierarchy of Hazard Control Analysis pursuant to section 2762.13 for all recommendations made by the PHA team for each scenario that identifies the potential for a major incident. |  |  | OBSERVATION: Owner/operator failed to perform a Hierarchy of Hazard Control Analysis pursuant to 2762.13 for all recommendations made by the PHA team for recommendations made for scenario that identifies the potential for a major incident. CORRECTIVE ACTION: Owner/operator will conduct a Hierarchy of Hazard Control Analysis for recommendations for each scenario identified in the PHA with the potential of a major incident and provide documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010139 |  |  | Program level 4: Process Hazard Analysis (PHA) -Recommendation Documentation | Failure to ensure the team documents its findings and recommendations in a report, made available in the respective work area for review by any person working in that area. | 19 CCR 4.5 2762.2(g) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 151 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Written recommendations & report available in work area for review | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the team documents its findings and recommendations in a report, made available in the respective work area for review by any person working in that area. |  |  | OBSERVATION: Owner/operator failed to ensure the PHA team documents its findings and recommendations in a report made available in the respective work area for review by any person working in that area. CORRECTIVE ACTION: Owner/operator will establish or revise their written procedures to ensure PHA report available for review in the respective work area. Owner/operator will ensure that all PHA findings and recommendations are in a report made available in the respective work area for review by and person working in that area and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010140 |  |  | Program level 4: Process Hazard Analysis (PHA) - Report Contents | Failure to ensure the PHA report include: (1) the method, analyses and factors considered by the PHA team; (2) the findings of the PHA team; and (3) the PHA team's recommendations. | 19 CCR 4.5 2762.2(h) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 152 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Ensured PHA includes methods, analyses, findings, and recommendations | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PHA report include: (1) the method, analyses and factors considered by the PHA team; (2) the findings of the PHA team; and (3) the PHA team's recommendations. |  |  | OBSERVATION: Owner/operator failed to ensure the PHA report include the method, analyses, factors considered by the PHA team, findings of the team and the team's recommendations. CORRECTIVE ACTION: Owner/operator will establish or revise their written procedures and also revise the deficient PHA report to include the method, analyses, factors considered by the team, the findings of the team, and the team's recommendations and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010141 |  |  | Program level 4: Process Hazard Analysis (PHA) -Corrective Action Work Process | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the PHA team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. | 19 CCR 4.5 2762.2(i) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 153 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Followed corrective action work process on findings and recommendations | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the PHA team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. |  |  | OBSERVATION: Owner/operator failed to follow the corrective action work process documented in subsections 2762.16(d) and (e) when resolving the PHA team's findings and recommendations, determining action items for implementation, tracking completion, and documentation of closeout. CORRECTIVE ACTION: Owner/operator will establish or revise written procedures to ensure they follow the corrective action work process documented specified subsections 2762.16(d) and (e) when resolving PHA team's finding and recommendations, determining action items for implementation, tracking completion dates, and documentation of closeout and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010142 |  |  | Program level 4: Process Hazard Analysis (PHA) - Revalidation | Failure to update and revalidate a written PHA at least once every five (5) years in accordance with the requirements of section 2762.2, to ensure that the PHA is consistent with the current process. | 19 CCR 4.5 2762.2(j) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 154 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Ensured written PHA is updated or reevaluated every five years | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update and revalidate a written PHA at least once every five (5) years in accordance with the requirements of section 2762.2, to ensure that the PHA is consistent with the current process. |  |  | OBSERVATION: Owner/operator failed to update and reevaluate a written PHA at least one every five years according to the requirements of 2762.2 to ensure that the PHA is consistent with the current process. CORRECTIVE ACTION: Owner/operator will update and reevaluate the PHA reports which have not been reevaluated in the past five years, establish or modify written procedures to ensure that PHA reports are reviewed every five years, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010143 |  |  | Program level 4: Process Hazard Analysis (PHA) - Retention | Failure to retain for the life of the process all PHAs and PHA updates and revalidations for each process covered by section 2762.2. Failure to have information contain the documented resolution of recommendations as appendices described in subsections 2762.16 (d) and (e). | 19 CCR 4.5 2762.2(k) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 155 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Retained PHA and all PHA updates for process life | 50 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain for the life of the process all PHAs and PHA updates and revalidations for each process covered by section 2762.2. Failure to have information contain the documented resolution of recommendations as appendices described in subsections 2762.16 (d) and (e). |  |  | OBSERVATION: Owner/operator failed to retain for the life of the process of all PHA reports and PHA update and reevaluation reports for each process covered by section 2762.2. CORRECTIVE ACTION: Owner/operator will retain for the life of the process all PHA reports, PHA update and reevaluation reports, establish or modify written procedures to ensure that PHA reports are retained for the life of each process, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010144 |  |  | Program level 4: Safeguard Protection Analysis - Safeguards | Failure to ensure a SPA team performs a written SPA, for each scenario where a PHA identifies the potential for a major incident, to determine: (1) the effectiveness of existing individual safeguards; (2) the combined effectiveness of all existing safeguards for each failure scenario in the PHA; (3) the individual and combined effectiveness of safeguards recommended in the PHA; and (4) the individual and combined effectiveness of additional or alternative safeguards that may be needed. | 19 CCR 4.5 2762.2.1(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 156 | Program 4 Prevention Program | Safeguard Protection Analysis | Ensured a SPA team performs a SPA for each major incident scenario | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure a SPA team performs a written SPA, for each scenario where a PHA identifies the potential for a major incident, to determine: (1) the effectiveness of existing individual safeguards; (2) the combined effectiveness of all existing safeguards for each failure scenario in the PHA; (3) the individual and combined effectiveness of safeguards recommended in the PHA; and (4) the individual and combined effectiveness of additional or alternative safeguards that may be needed. |  |  | OBSERVATION: Owner/operator failed to ensure a SPA team performs a written SPA for each scenario where a PHA identifies the potential for a major incident, to determine: the effectiveness of existing individual safeguards; the combined effectiveness of all safeguard of each failure scenario; individual and combined effectiveness of safeguards recommended in PHA; the individual and combined effectiveness of additional or alternative safeguards. CORRECTIVE ACTION: Owner/operator will ensure that SPA team performs written SPA for each scenario where a PHA identifies the potential for a incident, to determine: the effectiveness individual safeguards; the combined effectiveness of all existing safeguards, individual and combined effectiveness of safeguards recommended in PHA, individual and combined effectiveness of additional or alternative safeguards that may be needed, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010145 |  |  | Program level 4: Safeguard Protection Analysis - IPLs | Failure to ensure all independent protection layers (IPLs) for each failure scenario shall be independent of each other and independent of initiating causes. | 19 CCR 4.5 2762.2.1(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 157 | Program 4 Prevention Program | Safeguard Protection Analysis | IPL have failure scenario independent of each other & initiating causes as required | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure all independent protection layers (IPLs) for each failure scenario shall be independent of each other and independent of initiating causes. |  |  | OBSERVATION: Owner/operator failed to ensure that when performing SPA that independent protection layers for each failure scenario were independent of each other and of initiating causes. CORRECTIVE ACTION: Owner/operator will prepare or revise the SPA so it includes independent protection layers that are independent of each other and of the initiating causes and establish or revise written procedures to ensure that independent protection layers are independent of initiating causes, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010146 |  |  | Program level 4: Safeguard Protection Analysis - Methodology | Failure to ensure the SPA use a quantitative or semi-quantitative method, such as Layer of Protection Analysis (LOPA) or an equally effective method. Failure to ensure the risk reduction obtainable by each IPL is based on site-specific failure rate data, or in the absence of such data, industry failure rate data for each device, system, or human factor. | 19 CCR 4.5 2762.2.1(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 158 | Program 4 Prevention Program | Safeguard Protection Analysis | Used quantitative, semi-quantitative SPA method, site-specific/industry standard failure rate used | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the SPA use a quantitative or semi-quantitative method, such as Layer of Protection Analysis (LOPA) or an equally effective method. Failure to ensure the risk reduction obtainable by each IPL is based on site-specific failure rate data, or in the absence of such data, industry failure rate data for each device, system, or human factor. |  |  | OBSERVATION: Owner/operator failed to ensure that the SPA used a quantitative method such as Layer of Protection Analysis or an equally effective method. Owner/Operator failed to ensure the risk reduction obtainable by each IPL is based on site-specific failure rate date, or in absence of such date, industry failure rate date for each device, system, or human factor. CORRECTIVE ACTION: Owner/operator will ensure that a quantitative or semiquantitative method such as Layer of Protection Analysis or an equally effective method is used to ensure risk reduction obtainable by each IPL is based on site specific failure rate data or in absence of this data, industry failure rate date for each device, system, human factor, and provide documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010147 |  |  | Program level 4: Safeguard Protection Analysis - Completion Timeline | Failure to complete all SPAs for the PHA within six (6) months of completion of the PHA. | 19 CCR 4.5 2762.2.1(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 159 | Program 4 Prevention Program | Safeguard Protection Analysis | SPAs completed for the PHA within six-months of completion of the PHA | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete all SPAs for the PHA within six (6) months of completion of the PHA. |  |  | OBSERVATION: Owner/operator failed to ensure that SPAs for the PHA were completed within six (6) months of completion of the PHA. CORRECTIVE ACTION: Owner/operator will ensure that SPAs for the PHA are completed within six (6) months of completion of the PHA, establish or revise a written procedure to ensure that the SPA are completed within the six month time period of PHA completion, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010148 |  |  | Program level 4: Safeguard Protection Analysis - Team Qualifications | Failure to ensure SPA is performed by a team with expertise in engineering and process operations and the team include at least one operating employee who has experience and knowledge specific to the process being evaluated. Failure to ensure the team also include one member knowledgeable in the specific SPA methodology being used. Failure to ensure the team consult with individuals with expertise in damage mechanisms, process chemistry, or an engineer specializing in controls systems and instrumentation, as necessary. Failure to provide for employee participation in this process, pursuant to section 2762.10. | 19 CCR 4.5 2762.2.1(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 160 | Program 4 Prevention Program | Safeguard Protection Analysis | SPA team has expertise in engineering, process operations, & employee as required | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure SPA is performed by a team with expertise in engineering and process operations and the team include at least one operating employee who has experience and knowledge specific to the process being evaluated. Failure to ensure the team also include one member knowledgeable in the specific SPA methodology being used. Failure to ensure the team consult with individuals with expertise in damage mechanisms, process chemistry, or an engineer specializing in controls systems and instrumentation, as necessary. Failure to provide for employee participation in this process, pursuant to section 2762.10. |  |  | OBSERVATION: Owner/operator failed to ensure that SPA is performed by a team with expertise in engineering and process operations that includes at least one operating employee who has experience and knowledge specific to the process being evaluated, one member knowledgeable in specific SPA methodology being used, consult with individuals in damage mechanisms, process chemistry, controls, instrumentation, and have employee participation. CORRECTIVE ACTION: Owner/operator will ensure that SPA is performed by a team with expertise in engineering, process operation including one operating employee who has experience and knowledge specific to the process being evaluated, one member knowledgeable in specific SPA methodology being used, consult with individuals with expertise in damage mechanisms, process chemistry, control systems, instrumentation, include employee participation, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010149 |  |  | Program level 4: Safeguard Protection Analysis - Team Documentation Requirements | Failure to ensure the SPA team documents the following: (1) potential initiating events and their likelihood and possible consequences, including equipment failures, human errors, loss of flow control, loss of pressure control, loss of temperature control, loss of level control, excess reaction or other conditions that may lead to a loss of containment; (2) the risk reduction achieved by each IPL for each initiating event; (3) necessary maintenance and testing to ensure that all IPLs function as designed; and (4) recommendations to address any deficiencies identified by the SPA. | 19 CCR 4.5 2762.2.1(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 161 | Program 4 Prevention Program | Safeguard Protection Analysis | SPA team documented initiating events, risk reduction of IPLs, maintenance needed, recommendations | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the SPA team documents the following: (1) potential initiating events and their likelihood and possible consequences, including equipment failures, human errors, loss of flow control, loss of pressure control, loss of temperature control, loss of level control, excess reaction or other conditions that may lead to a loss of containment; (2) the risk reduction achieved by each IPL for each initiating event; (3) necessary maintenance and testing to ensure that all IPLs function as designed; and (4) recommendations to address any deficiencies identified by the SPA. |  |  | OBSERVATION: Owner/operator failed to ensure the SPA team documents initiating events, likelihood, consequences including equipment failures, human errors, loss of flow control, loss of pressure control, loss of temperature control, loss of level control, excess reaction, loss of containment, risk reduction of IPL for each initiating event, maintenance & testing of each IPL so all IPLs function as designed, & recommendations for deficiencies identified by the SPA. CORRECTIVE ACTION: Owner/operator will ensure that SPA team documents potential initiating events: the likelihood, possible consequences as specified in 2762.2.1(f); the risk reduction achieved by each IPL for each initiating event; necessary maintenance and testing that the IPLs function as designed; recommendations to address any deficiencies identified by Safeguard Protection Analysis by revising deficient SPA documents, establishing or revising written procedures, and providing documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010150 |  |  | Program level 4: Safeguard Protection Analysis - Recommendations Annex | Failure to append the SPA findings and recommendations to the PHA report. | 19 CCR 4.5 2762.2.1(g) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 162 | Program 4 Prevention Program | Safeguard Protection Analysis | Ensured SPA findings and recommendations are appended to PHA report | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to append the SPA findings and recommendations to the PHA report. |  |  | OBSERVATION: Owner/operator failed to append the SPA findings and recommendations to the PHA report. CORRECTIVE ACTION: Owner/operator will ensure that SPA findings and recommendations are appended to the PHA report by revising the PHA report to include the SPA findings and recommendations, establishing or revising written procedures on SPA preparation, and submit documentation to UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010151 |  |  | Program level 4: Safeguard Protection Analysis - Corrective Action Work Process | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the SPA team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. | 19 CCR 4.5 2762.2.1(h) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 163 | Program 4 Prevention Program | Safeguard Protection Analysis | Used corrective action process for SPA teams findings & recommendations | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the SPA team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. |  |  | OBSERVATION: Owner/operator failed to follow the corrective action work process documented in subsections 2762.16(d) and (e) when resolving the PHA team's findings and recommendations, determining action items for implementation, tracking completion, and documentation of closeout. CORRECTIVE ACTION: Owner/operator will establish or revise written procedures to ensure they follow the corrective action work process documented specified subsections 2762.16(d) and (e) when resolving PHA team's finding and recommendations, determining action items for implementation, tracking completion dates, and documentation of closeout, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010152 |  |  | Program level 4: Safeguard Protection Analysis - Retention | Failure to retain all SPA documentation for the life of the process. | 19 CCR 4.5 2762.2.1(i) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 164 | Program 4 Prevention Program | Safeguard Protection Analysis | Retained SPA documentation for the life of the process | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain all SPA documentation for the life of the process. |  |  | OBSERVATION: Owner/operator failed to retain all SPA documentation for the life of the process. CORRECTIVE ACTION: Owner/operator will establish or revise written procedures to ensure SPA documentation is retained for the life of the process, will prepare a revised SPA for the process, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010153 |  |  | Program level 4: Operating Procedures - General | Failure to develop and implement effective written operating procedures with clear instructions for safely conducting activities involved in each process with the process safety information. | 19 CCR 4.5 2762.3(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 165 | Program 4 Prevention Program | Operating Procedures | Developed and implemented clear and effective SOPS for safe operations of the process based on PSI | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement effective written operating procedures with clear instructions for safely conducting activities involved in each process with the process safety information. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information. CORRECTIVE ACTION: Develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010154 |  |  | Program level 4: Operating Procedures -Steps for each Operating Phase | Failure to develop and implement written operating procedures that address the steps for each operating phase or mode of operation: (A) Startup; (B) Normal operations; (C) Temporary operations as the need arises; (D) Emergency shutdown, including the conditions under which emergency shutdown is required, provisions granting the authority of the qualified operator to shut down the operation or process, and the assignment of responsibilities to qualified operators in order to ensure that emergency shutdown is executed in a safe and timely manner; (E) Normal shutdown; and, (F) Startup following a turnaround, a planned or unplanned shutdown, or after an emergency shutdown. | 19 CCR 4.5 2762.3(a)(1) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 166 | Program 4 Prevention Program | Operating Procedures | Developed and implemented written SOPs that address the steps of each phase or mode of operation | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement written operating procedures that address the steps for each operating phase or mode of operation: (A) Startup; (B) Normal operations; (C) Temporary operations as the need arises; (D) Emergency shutdown, including the conditions under which emergency shutdown is required, provisions granting the authority of the qualified operator to shut down the operation or process, and the assignment of responsibilities to qualified operators in order to ensure that emergency shutdown is executed in a safe and timely manner; (E) Normal shutdown; and, (F) Startup following a turnaround, a planned or unplanned shutdown, or after an emergency shutdown. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address: initial startup; normal operations; temporary operations; emergency shutdown including the conditions under which emergency shutdown is required, and the assignment of shutdown responsibility to qualified operators to ensure that emergency shutdown is executed in a safe and timely manner; emergency operations; normal shutdown; startup following a turnaround, or after an emergency shutdown. CORRECTIVE ACTION: Develop, implement and submit copies of written operating procedures that address the deficiencies noted above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010155 |  |  | Program level 4: Operating Procedures - Operating Limits | Failure to develop and implement written operating procedures that address the operating limits: (A) Consequences of deviation(s); and, (B) Steps required to correct or avoid deviation(s). | 19 CCR 4.5 2762.3(a)(2) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 167 | Program 4 Prevention Program | Operating Procedures | Developed & implemented SOPS that address consequences of deviation & corrective actions/avoidance | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement written operating procedures that address the operating limits: (A) Consequences of deviation(s); and, (B) Steps required to correct or avoid deviation(s). |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address the consequences of deviation and the steps required to correct or avoid the deviation. CORRECTIVE ACTION: Develop and implement written operating procedures that address the consequences of deviation and the steps required to correct or avoid the deviation/ and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010156 |  |  | Program level 4: Operating Procedures - Safety and Health Considerations | Failure to develop and implement written operating procedures that address safety and health considerations: (A) Properties of, and hazards presented by, the chemicals used in the process; (B) Precautions necessary to prevent exposure, including passive, active and procedural safeguards; and personal protective equipment; (C) Protective measures to be taken if physical contact or inhalation exposure occurs; (D) Safety procedures for opening process equipment; (E) Verification of the composition and properties of raw materials and control of hazardous chemical inventory levels; and, (F) Any special or unique hazards. | 19 CCR 4.5 2762.3(a)(3) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 168 | Program 4 Prevention Program | Operating Procedures | Developed & implemented SOPS that address safety & health considerations | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement written operating procedures that address safety and health considerations: (A) Properties of, and hazards presented by, the chemicals used in the process; (B) Precautions necessary to prevent exposure, including passive, active and procedural safeguards; and personal protective equipment; (C) Protective measures to be taken if physical contact or inhalation exposure occurs; (D) Safety procedures for opening process equipment; (E) Verification of the composition and properties of raw materials and control of hazardous chemical inventory levels; and, (F) Any special or unique hazards. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address: properties of, and hazards presented by, the chemicals used in the process; precautions necessary to prevent exposure, including engineering controls, administrative controls, and personal protective equipment; control measures to be taken if physical contact or airborne exposure occurs; quality control for raw materials and control of hazardous chemical inventory levels; any special or unique hazards. CORRECTIVE ACTION: Develop, implement, and submit copy of written operating procedures that address the deficiencies noted above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010157 |  |  | Program level 4: Operating Procedures - Safety Systems and their Functions | Failure to develop and implement written operating procedures that address safety systems and their functions. | 19 CCR 4.5 2762.3(a)(4) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 169 | Program 4 Prevention Program | Operating Procedures | Developed and implemented SOPS that address safety systems and their functions | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement written operating procedures that address safety systems and their functions. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address safety systems and their functions. CORRECTIVE ACTION: Develop and implement written operating procedures that address safety systems and their functions and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010158 |  |  | Program level 4: Operating Procedures - Emergency Operations | Failure to ensure operating procedures include emergency operations for each process, including any response to the over-pressurizing or overheating of equipment or piping, and the handling of leaks, spills, releases and discharges. Failure to ensure operating procedures are consistent with the procedures developed as required by subsection 2762.3 (a)(1)(D) and to provide that only qualified operators may initiate these operations and that prior to allowing employees in the vicinity of a leak, release or discharge, at a minimum do one of the following: (1) Shutdown and depressurize all process operations where a leak, release or discharge is occurring; or(2) Isolate any vessel, piping, and equipment where a leak, spill or discharge is occurring; or (3) Follow established criteria for handling leaks, spills, or discharges that are designed to provide a level of protection that is functionally equivalent to, or safer than, shutting down or isolating the process. | 19 CCR 4.5 2762.3(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 170 | Program 4 Prevention Program | Operating Procedures | Ensured that SOPS include emergency operations for each process | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure operating procedures include emergency operations for each process, including any response to the over-pressurizing or overheating of equipment or piping, and the handling of leaks, spills, releases and discharges. Failure to ensure operating procedures are consistent with the procedures developed as required by subsection 2762.3 (a)(1)(D) and to provide that only qualified operators may initiate these operations and that prior to allowing employees in the vicinity of a leak, release or discharge, at a minimum do one of the following: (1) Shutdown and depressurize all process operations where a leak, release or discharge is occurring; or(2) Isolate any vessel, piping, and equipment where a leak, spill or discharge is occurring; or (3) Follow established criteria for handling leaks, spills, or discharges that are designed to provide a level of protection that is functionally equivalent to, or safer than, shutting down or isolating the process. |  |  | OBSERVATION: The owner/operator failed to ensure that SOPS include emergency operations for each process to include any response to the over pressurizing or overheating of equipment or piping, and the handling of leaks, spills, releases and discharges performed by a qualified operator to initiate at a minimum of the following operations: (1) Shutdown and depressurize all process operations where a leak, release or discharge is occurring; or (2) Isolate any vessel, piping, and equipment where a leak, spill or discharge is occurring; or (3) Follow established criteria for handling leaks, spills, or discharges that are designed to provide a level of protection that is functionally equivalent to, or safer than, shutting down or isolating the process. CORRECTIVE ACTION: Develop and implement written SOPS to include emergency operations for each process meeting the requirements of this section 2762.3(b) and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010159 |  |  | Program level 4: Operating Procedures - Accessibility | Failure to ensure a copy of the operating procedures is readily accessible to employees who work in or near the process area and to any other person who works in or near the process area or who maintains a process. | 19 CCR 4.5 2762.3(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 171 | Program 4 Prevention Program | Operating Procedures | Ensured SOPS are readily accessible to employees who work near or maintains process area | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure a copy of the operating procedures is readily accessible to employees who work in or near the process area and to any other person who works in or near the process area or who maintains a process. |  |  | OBSERVATION: The owner/operator failed to make operating procedures readily accessible to employees who work in or maintain a process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating operating procedures are readily accessible to employees who work in or maintain a process. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010160 |  |  | Program level 4: Operating Procedures - Review, MOC, Certification | Failure to review and update the operating procedures as often as necessary to ensure that they reflect current safe operating practices. Failure to ensure operating procedures include any changes that result from alterations in process chemicals, technology, personnel, process equipment, or other changes to the stationary source. Failure to ensure changes to operating procedures are managed in accordance with the MOC requirements in section 2762.6. Failure to certify annually that operating procedures are current and accurate. | 19 CCR 4.5 2762.3(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 172 | Program 4 Prevention Program | Operating Procedures | Reviewed and certified SOPS at least annually to reflect all current operations are correct | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to review and update the operating procedures as often as necessary to ensure that they reflect current safe operating practices. Failure to ensure operating procedures include any changes that result from alterations in process chemicals, technology, personnel, process equipment, or other changes to the stationary source. Failure to ensure changes to operating procedures are managed in accordance with the MOC requirements in section 2762.6. Failure to certify annually that operating procedures are current and accurate. |  |  | OBSERVATION: The owner/operator failed to review and update the operating procedures as often as necessary to ensure that they reflect current safe operating practices. Failed to ensure operating procedures include any changes that result from alterations in process chemicals, technology, personnel, process equipment, or other changes to the stationary source. Failed to ensure changes to operating procedures are managed in accordance with the MOC requirements in section 2762.6. Failed to certify annually that operating procedures are current and accurate. CORRECTIVE ACTION: Review and update the operating procedures to assure that they reflect current operating practice. Certify that the operating procedures are current and accurate and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010161 |  |  | Program level 4: Operating Procedures - Safe Work Practices | Failure to develop, implement, and maintain safe work practices to prevent or control hazards during specific activities, such as: 1. Opening process equipment or piping; 2. Tasks requiring lock-out/tag-out procedures; 3. Confined space entry; 4. Handling, controlling, and stopping leaks, spills, releases and discharges; and 5. Control over entry into hazardous work areas by maintenance, contractor, laboratory, or other support personnel. | 19 CCR 4.5 2762.3(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 173 | Program 4 Prevention Program | Operating Procedures | Developed and implemented safe work practices to provide control of hazards during operations | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement, and maintain safe work practices to prevent or control hazards during specific activities, such as: 1. Opening process equipment or piping; 2. Tasks requiring lock-out/tag-out procedures; 3. Confined space entry; 4. Handling, controlling, and stopping leaks, spills, releases and discharges; and 5. Control over entry into hazardous work areas by maintenance, contractor, laboratory, or other support personnel. |  |  | OBSERVATION: The owner/operator failed to develop and implement safe work practices to provide for the control of hazards during operations including: logout/tagout; confined space entry; opening process equipment or piping; and control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel. CORRECTIVE ACTION: Develop and implement safe work practices to provide for the control of hazards during operations including: logout/tagout; confined space entry; opening process equipment or piping; and control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020012 |  |  | Program level 4: Training - Initial | (1) Failure to train each employee involved in operating a process, and each operating employee prior to working in a newly assigned process, in an overview of the process and in the operating procedures as specified in section 2762.3. Failure to include material on the specific safety and health hazards applicable to the employee's job tasks, procedures, including emergency operations and shutdown, and safe work practices applicable to the employee's job tasks. (2) Failure to train each employee involved in maintaining the on-going integrity of process equipment in an overview of that process and its hazards and in the procedures applicable to the employee's job tasks to assure that the employee can perform the job tasks in a safe manner. | 19 CCR 4.5 2762.4(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 174 | Program 4 Prevention Program | Training | Trained employees involved in operating a process on requirements in Section 2762.4 | 83 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | (1) Failure to train each employee involved in operating a process, and each operating employee prior to working in a newly assigned process, in an overview of the process and in the operating procedures as specified in section 2762.3. Failure to include material on the specific safety and health hazards applicable to the employee's job tasks, procedures, including emergency operations and shutdown, and safe work practices applicable to the employee's job tasks. (2) Failure to train each employee involved in maintaining the on-going integrity of process equipment in an overview of that process and its hazards and in the procedures applicable to the employee's job tasks to assure that the employee can perform the job tasks in a safe manner. |  |  | OBSERVATION: The owner/operator failed to train each employee presently involved in operating a process, and each employee before being involved in operating a newly assigned process on the following: overview of the process; operating procedures; safety & health hazards; emergency operations including shutdown; safe work practices applicable to the employee's job tasks. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating each employee presently involved in operating a process has been trained on the following: overview of the process; operating procedures; safety & health hazards; emergency operations including shutdown; safe work practices applicable to the employee's job tasks. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020013 |  |  | Program level 4: Training - Refresher and Supplemental | (1) Failure to ensure at least once every three years, and more often if necessary, refresher and supplemental training is provided to each employee involved in operating a process in order to ensure the employee understands and adheres to the current operating procedures of the process. Failure to determine the appropriate frequency and content of refresher training, in consultation with the employees involved in operating the process. (2) Failure to provide effective refresher and supplemental training at least once every three years, and more often if necessary, to each maintenance employee to ensure that each employee understands and adheres to current maintenance procedures. | 19 CCR 4.5 2762.4(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 175 | Program 4 Prevention Program | Training | Performed effective refresher training at least every 3 years or more often if necessary | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | (1) Failure to ensure at least once every three years, and more often if necessary, refresher and supplemental training is provided to each employee involved in operating a process in order to ensure the employee understands and adheres to the current operating procedures of the process. Failure to determine the appropriate frequency and content of refresher training, in consultation with the employees involved in operating the process. (2) Failure to provide effective refresher and supplemental training at least once every three years, and more often if necessary, to each maintenance employee to ensure that each employee understands and adheres to current maintenance procedures. |  |  | OBSERVATION: The owner/operator failed to effectively train employees in operating a process in order to ensure employee understands and adheres to the current operating/maintenance procedures of the process at least once every 3 years or as often as necessary. CORRECTIVE ACTION: Conduct training and provide documentation to CUPA that employees understand and adheres to current operating/maintenance procedures of the process and establishes consistent training frequency at least every 3 years or as often as necessary. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020014 |  |  | Program level 4: Training - Certification Record | Failure to ensure that each employee involved in operating a process has received, understood and successfully completed training as specified by section 2762.4. Failure to prepare, after the initial or refresher training, a certification record containing the identity of the employee, the date(s) of training, the means used to verify that the employee understood the training, and the signature(s) of the person administering the training. | 19 CCR 4.5 2762.4(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 176 | Program 4 Prevention Program | Training | Documented training records identifying employee, training date, & verification of competency | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that each employee involved in operating a process has received, understood and successfully completed training as specified by section 2762.4. Failure to prepare, after the initial or refresher training, a certification record containing the identity of the employee, the date(s) of training, the means used to verify that the employee understood the training, and the signature(s) of the person administering the training. |  |  | OBSERVATION: The owner/operator failed to prepare a certification record containing the identity of the employee, the date(s) of training, the means used to verify that the employee understood the training, and the signature(s) of the person administering the training. CORRECTIVE ACTION: Establish record keeping forms to meet the requirements of this section, perform training, and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020015 |  |  | Program level 4: Training - Requirements and Testing | Failure to develop and implement an effective written program that includes (1) the requirements that an employee must meet in order to be designated as qualified, and (2) employee testing procedures to verify understanding and to ensure competency in job skill levels and work practices that protect employee and public safety and health. | 19 CCR 4.5 2762.4(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 177 | Program 4 Prevention Program | Training | Developed and implemented qualifications/competency program for designated employees | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement an effective written program that includes (1) the requirements that an employee must meet in order to be designated as qualified, and (2) employee testing procedures to verify understanding and to ensure competency in job skill levels and work practices that protect employee and public safety and health. |  |  | OBSERVATION: The owner/operator failed to develop and implement an effective written program that includes (1) the requirements that an employee must meet in order to be designated as qualified, and (2) employee testing procedures to verify understanding and to ensure competency in job skill levels and work practices that protect employee and public safety and health. CORRECTIVE ACTION: Develop and implement and effective written program that meet the requirements of this section and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020016 |  |  | Program level 4: Training - Program 4 Elements | Failure to develop and implement an effective training program to ensure that all affected employees are aware of and understand all Program 4 elements described in Article 6.5. Failure to complete the initial training required in section 2762.4 within twenty-four (24) months following the effective date of section 2762.4. Employees and employee representatives participating in a specialized team pursuant to 2762.13 shall be trained in the Program elements relevant to that team. | 19 CCR 4.5 2762.4(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 178 | Program 4 Prevention Program | Training | Developed, implemented, and completed initial/refresher training for program 4 elements | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement an effective training program to ensure that all affected employees are aware of and understand all Program 4 elements described in Article 6.5. Failure to complete the initial training required in section 2762.4 within twenty-four (24) months following the effective date of section 2762.4. Employees and employee representatives participating in a specialized team pursuant to 2762.13 shall be trained in the Program elements relevant to that team. |  |  | OBSERVATION: The owner/operator failed to develop and implement an effective training program to ensure that all affected employees are aware of and understand all Program 4 elements described in Article 6.5 within 24 months of the effective date of section 2762.4. CORRECTIVE ACTION: Develop and implement training program and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020017 |  |  | Program level 4: Training - Employee Participation | Failure to provide for employee participation in developing and implementing the training program, pursuant to section 2762.10. | 19 CCR 4.5 2762.4(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 179 | Program 4 Prevention Program | Training | Provided employee participation to develop and implement training program | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide for employee participation in developing and implementing the training program, pursuant to section 2762.10. |  |  | OBSERVATION: The owner/operator failed to provide employee participation in developing and implementing the training program per section 2762.10. CORRECTIVE ACTION: Establish employee participation program in developing and implementing training programs and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010162 |  |  | Program level 4: Mechanical Integrity - Written Procedures | Failure to develop, implement, and maintain effective written procedures to ensure the ongoing integrity of process equipment. (1) Failure to ensure the procedures provide clear instructions for safely conducting maintenance activities on process equipment, consistent with the Process Safety Information. (2) Failure to ensure the procedures and inspection documents developed under subsection 2762.5 are readily accessible to employees and employee representatives pursuant to section 2762.10. | 19 CCR 4.5 2762.5(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 180 | Program 4 Prevention Program | Mechanical Integrity | Developed, implemented, & maintained accessible SOPS on mechanical integrity/maintenance | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement, and maintain effective written procedures to ensure the ongoing integrity of process equipment. (1) Failure to ensure the procedures provide clear instructions for safely conducting maintenance activities on process equipment, consistent with the Process Safety Information. (2) Failure to ensure the procedures and inspection documents developed under subsection 2762.5 are readily accessible to employees and employee representatives pursuant to section 2762.10. |  |  | OBSERVATION: The owner/operator failed to develop, implement, and maintain effective written procedures to ensure the ongoing integrity of process equipment that provide clear instructions for safely conducting maintenance activities on process equipment, consistent with the Process Safety Information and are readily accessible to employees and employee representatives pursuant to section 2762.10. CORRECTIVE ACTION: Develop, implement, and maintain effective written procedures to ensure the ongoing integrity of process equipment that provide clear instructions for safely conducting maintenance activities on process equipment, consistent with the Process Safety Information and are readily accessible to employees and employee representatives pursuant to section 2762.10 and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Operations/Maintenance | 5030006 |  |  | Program level 4: Mechanical Integrity - Inspection and Testing | (1) Failure to ensure inspections and tests are performed on process equipment, using procedures that meet or exceed recognized and generally accepted good engineering practices (RAGAGEP). (2) Failure to ensure the frequency of inspections and tests of process equipment are consistent with (1) the applicable manufacturers' recommendations, (2) RAGAGEP, or (3) internal practices that are more protective than (1) or (2). Failure to ensure inspections and tests are conducted more frequently if necessary, based on the operating experience with the process equipment. (3) Failure to retain a certification record to document that each inspection and test has been performed in accordance with subsection 2762.5. Failure to ensure the certification record identifies the date of the inspection; the name of the person who performed the inspection or test; a description of the inspection or test performed; the results of the inspection or test; and the serial number or other identifier of the equipment on which the inspection or test was performed. | 19 CCR 4.5 2762.5(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 181 | Program 4 Prevention Program | Mechanical Integrity | Performed & documented inspections/tests per RAGAGEP/manufacturers/internal practices | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | (1) Failure to ensure inspections and tests are performed on process equipment, using procedures that meet or exceed recognized and generally accepted good engineering practices (RAGAGEP). (2) Failure to ensure the frequency of inspections and tests of process equipment are consistent with (1) the applicable manufacturers' recommendations, (2) RAGAGEP, or (3) internal practices that are more protective than (1) or (2). Failure to ensure inspections and tests are conducted more frequently if necessary, based on the operating experience with the process equipment. (3) Failure to retain a certification record to document that each inspection and test has been performed in accordance with subsection 2762.5. Failure to ensure the certification record identifies the date of the inspection; the name of the person who performed the inspection or test; a description of the inspection or test performed; the results of the inspection or test; and the serial number or other identifier of the equipment on which the inspection or test was performed. |  |  | OBSERVATION: The owner/operator failed to ensure frequency of inspections and tests are performed on process equipment per RAGAGP, manufacturer's recommendations, internal practices that are more protective, or are based on operating experience that is more frequent if necessary with retained certification of record to document that each inspection and test has been performed in accordance with subsection 2762.5. CORRECTIVE ACTION: Establish and implement program for inspections and tests performed on process equipment per RAGAGP, manufacturer's recommendations, internal practices that are more protective, or are based on operating experience that is more frequent if necessary with retained certification of record to document that each inspection and test has been performed in accordance with subsection 2762.5 and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Operations/Maintenance | 5030007 |  |  | Program level 4: Mechanical Integrity - Equipment Deficiencies | Failure to correct equipment deficiencies to ensure safe operation of process equipment. Failure to ensure repair methodologies are consistent with RAGAGEP or more protective internal practices. | 19 CCR 4.5 2762.5(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 182 | Program 4 Prevention Program | Mechanical Integrity | Corrected equipment deficiencies for safe operation of process equipment per RAGAGEP/higher | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to correct equipment deficiencies to ensure safe operation of process equipment. Failure to ensure repair methodologies are consistent with RAGAGEP or more protective internal practices. |  |  | OBSERVATION: The owner/operator failed to correct equipment deficiencies to ensure safe operation of process equipment consistent with repair methodologies that are consistent with RAGAGEP or more protective internal practices. CORRECTIVE ACTION: Correct equipment deficiencies to ensure safe operation of process equipment consistent with repair methodologies that are consistent with RAGAGEP or more protective internal practices and submit documentation to CUPA | [6 empty] | No | No | No | Yes
CalARP Program | Operations/Maintenance | 5030008 |  |  | Program level 4: Mechanical Integrity - Quality Assurance | (1) Failure to ensure that all process equipment at a minimum complies with the criteria established in subsection 2762.1(d). Failure to ensure that all process equipment is: (1) suitable for the process application for which it is or will be used; (2) fabricated from the proper materials of construction; (3) designed, constructed, installed, maintained, inspected, tested, operated and replaced in compliance with the manufacturer's and any other design specifications and all applicable codes and standards. (2) Failure to ensure and document newly installed process equipment or existing process equipment for which no RAGAGEP exists, are designed, built, installed, maintained, inspected, tested and operated in a safe manner. (3) Failure to conduct regularly scheduled checks and inspections as necessary to ensure that the requirements of paragraph (1) are met. (4) Failure to ensure that maintenance materials, spare parts and equipment meet design specifications and applicable codes. (5) Failure to establish a process for evaluating new or updated equipment codes and standards and implementing changes as appropriate to ensure safe operation. | 19 CCR 4.5 2762.5(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 183 | Program 4 Prevention Program | Mechanical Integrity | Complied with design specifications of codes/standards, RAGAGEP, or higher protective practices | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | (1) Failure to ensure that all process equipment at a minimum complies with the criteria established in subsection 2762.1(d). Failure to ensure that all process equipment is: (1) suitable for the process application for which it is or will be used; (2) fabricated from the proper materials of construction; (3) designed, constructed, installed, maintained, inspected, tested, operated and replaced in compliance with the manufacturer's and any other design specifications and all applicable codes and standards. (2) Failure to ensure and document newly installed process equipment or existing process equipment for which no RAGAGEP exists, are designed, built, installed, maintained, inspected, tested and operated in a safe manner. (3) Failure to conduct regularly scheduled checks and inspections as necessary to ensure that the requirements of paragraph (1) are met. (4) Failure to ensure that maintenance materials, spare parts and equipment meet design specifications and applicable codes. (5) Failure to establish a process for evaluating new or updated equipment codes and standards and implementing changes as appropriate to ensure safe operation. |  |  | OBSERVATION: The owner/operator failed to comply with one of more of the following: (1) Ensure that all process equipment, at a minimum, complies with the criteria established in subsection 2762.1(d), including, but not limited to, ensuring that all process equipment is: (a) suitable for the process application for which it is or will be used, (b) fabricated from the proper materials of construction, (c) designed, constructed, installed, maintained, inspected, tested, operated and replaced in compliance with the manufacturer's and any other design specifications and all applicable codes and standards; (2) Ensure and document that newly installed process equipment or existing process equipment for which no RAGAGEP exists, are designed, built, installed, maintained, inspected, tested and operated in a safe manner. (3) Conduct regularly scheduled checks and inspections as necessary to ensure that the requirements of paragraph (1) are met. (4) Ensure that maintenance materials, spare parts and equipment meet design specifications and applicable codes. (5) Establish a process for evaluating new or updated equipment codes and standards and implementing changes as appropriate to ensure safe operation. CORRECTIVE ACTION: Ensure that facility is in compliance with all requirements described above and provide documentation to CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010163 |  |  | Program level 4: Mechanical Integrity - Damage Mechanism Review | Failure to complete a Damage Mechanism Review (DMR) for each process for which a damage mechanism exists. Failure to document the rationale for the determination that no damage mechanism exists, where no DMR is performed. Failure to determine and document the priority order for conducting the DMR based on process operating history, PHA schedule and inspection records. Failure to complete no less than 50 percent of the initial DMRs within three (3) years of the effective date of Article 6.5, and the remainder within five (5) years of the effective date of Article 6.5. | 19 CCR 4.5 2762.5(e)(1) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 184 | Program 4 Prevention Program | Mechanical Integrity | Completed and documented DMR for each process within required time frames. | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete a Damage Mechanism Review (DMR) for each process for which a damage mechanism exists. Failure to document the rationale for the determination that no damage mechanism exists, where no DMR is performed. Failure to determine and document the priority order for conducting the DMR based on process operating history, PHA schedule and inspection records. Failure to complete no less than 50 percent of the initial DMRs within three (3) years of the effective date of Article 6.5, and the remainder within five (5) years of the effective date of Article 6.5. |  |  | OBSERVATION: The owner/operator failed to complete a DMR for each process for which a damage mechanism exists; document rationale for the determination that no damage mechanism exists, where no DMR is performed; or document the priority order for conducting the DMR based on operating history/PHA schedule/inspection records within the time frame specified within this section. CORRECTIVE ACTION: Complete DMR with appropriate documentation specified within this section for each process and provide to CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010164 |  |  | Program level 4: Mechanical Integrity - DMR Update | Failure to update a DMR at least once every five (5) years consistent with the requirements of Section 2762.5. | 19 CCR 4.5 2762.5(e)(2) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 185 | Program 4 Prevention Program | Mechanical Integrity | Updated DMR at least once every 5 years | 39 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update a DMR at least once every five (5) years consistent with the requirements of Section 2762.5. |  |  | OBSERVATION: The owner/operator failed to update a DMR at least once every five (5) years consistent with the requirements of section 2762.5. CORRECTIVE ACTION: Update DMR and establish procedures to consistently update DMR at least once every five (5) years and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010165 |  |  | Program level 4: Mechanical Integrity - DMR Review | Failure to review a DMR as part of a major change on a process for which a damage mechanism exists, prior to approval of the change. Failure to conduct a DMR for a major change that may introduce a damage mechanism, prior to approval of the change. Failure to review the most recent DMR(s) that are relevant to the investigation, as part of an incident investigation pursuant to section 2762.9, where a damage mechanism is identified as a contributing factor. Failure to conduct and complete a DMR prior to implementation of corrective actions pursuant to section 2762.16(d) and (e), where a DMR has not been performed on the processes that are relevant to the investigation. | 19 CCR 4.5 2762.5(e)(3) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 186 | Program 4 Prevention Program | Mechanical Integrity | Reviewed or conducted DMR for major change, if relevant to incident invest., or corrective action | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to review a DMR as part of a major change on a process for which a damage mechanism exists, prior to approval of the change. Failure to conduct a DMR for a major change that may introduce a damage mechanism, prior to approval of the change. Failure to review the most recent DMR(s) that are relevant to the investigation, as part of an incident investigation pursuant to section 2762.9, where a damage mechanism is identified as a contributing factor. Failure to conduct and complete a DMR prior to implementation of corrective actions pursuant to section 2762.16(d) and (e), where a DMR has not been performed on the processes that are relevant to the investigation. |  |  | OBSERVATION: Owner/operator failed to review a DMR as part of a major change on a process for which a damage mechanism exists or failed to conduct a DMR for a major change that may introduce a damage mechanism, prior to approval of the change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has reviewed and/or conducted the required DMRs as described above. | OBSERVATION: Owner/operator failed to review the most recent DMR(s) that are relevant to the investigation, as part of an incident investigation pursuant to Section 2762.9, where a damage mechanism is identified as a contributing factor. Owner/operator failed to conduct and complete a DMR prior to implementation of corrective actions pursuant to Section 2762.16(d) and (e), where a DMR has not been performed on the processes that are relevant to the investigation. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has conducted the required DMRs as described above. | [5 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010166 |  |  | Program level 4: Mechanical Integrity - DMR Availability | Failure to ensure the DMR for a process unit is available to the team performing a PHA for that process unit. | 19 CCR 4.5 2762.5(e)(4) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 187 | Program 4 Prevention Program | Mechanical Integrity | Ensured that DMR for a process unit was available to the team performing PHA for that unit | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the DMR for a process unit is available to the team performing a PHA for that process unit. |  |  | OBSERVATION: Owner/operator failed to make the DMR for a process unit available to the team performing a PHA for that process unit. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the owner/operator will ensure that DMRs will be available when performing a PHA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010167 |  |  | Program level 4: Mechanical Integrity - Team Qualifications | Failure to ensure the DMR is performed by a team with expertise in engineering, operation of the processes under review, equipment and pipe inspection, and damage and failure mechanisms. Failure to ensure the team also includes one member knowledgeable in the specific DMR method being used. Failure to provide for employee participation in this process, pursuant to section 2762.10. | 19 CCR 4.5 2762.5(e)(5) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 188 | Program 4 Prevention Program | Mechanical Integrity | DMR(s) were conducted by a team with appropriate expertise and employee participation was addressed | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the DMR is performed by a team with expertise in engineering, operation of the processes under review, equipment and pipe inspection, and damage and failure mechanisms. Failure to ensure the team also includes one member knowledgeable in the specific DMR method being used. Failure to provide for employee participation in this process, pursuant to section 2762.10. |  |  | OBSERVATION: Owner/operator failed to ensure the following: the DMR was performed by a team with expertise in engineering, process operation (specific to the process under review), equipment and pipe inspection, damage and failure mechanisms; the team performing the DMR included one member knowledgeable in the specific DMR method being used; provided for employee participation in the DMR process, pursuant to section 2762.10. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has corrected the deficiencies noted above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010168 |  |  | Program level 4: Mechanical Integrity - DMR Elements | Failure to ensure the DMR for each process unit includes: (A) Assessment of Process Flow Diagrams (PFDs); (B) Identification of all potential damage mechanisms pursuant to subsection 2762.5 (e)(7) ; (C) Determination that the materials of construction are appropriate for their application and are resistant to potential damage mechanisms; (D) A discussion of the conditions that cause the damage mechanism and how rapidly the damage may progress; (E) Methods to prevent or mitigate damage; (F) Review of operating parameters to identify operating conditions that could accelerate damage or that could minimize or eliminate damage | 19 CCR 4.5 2762.5(e)(6) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 189 | Program 4 Prevention Program | Mechanical Integrity | DMRs include PFD assess, pot. damage mech's, mat's of construction, causal conditions, prevention | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the DMR for each process unit includes: (A) Assessment of Process Flow Diagrams (PFDs); (B) Identification of all potential damage mechanisms pursuant to subsection 2762.5 (e)(7) ; (C) Determination that the materials of construction are appropriate for their application and are resistant to potential damage mechanisms; (D) A discussion of the conditions that cause the damage mechanism and how rapidly the damage may progress; (E) Methods to prevent or mitigate damage; (F) Review of operating parameters to identify operating conditions that could accelerate damage or that could minimize or eliminate damage |  |  | OBSERVATION: Owner/operator failed to ensure that DMRs for each process unit includes: an assessment of Process Flow Diagrams (PFDs); identification of all potential damage mechanisms pursuant to subsection 2762.5(e)(7); determination that the materials of construction are appropriate for their application and are resistant to potential damage mechanisms; a discussion of the conditions that cause the damage mechanism and how rapidly the damage may progress; methods to prevent or mitigate damage; a review of operating parameters to identify operating conditions that could accelerate damage or that could minimize or eliminate damage. CORRECTION ACTION: Submit documentation to the UPA demonstrating the owner/operator has included the items listed above in each DMR. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010169 |  |  | Program level 4: Mechanical Integrity - Damage Mechanism Types | Failure to ensure damage mechanisms, for the purposes of section 2762.5, include, but are not limited to; (A) Mechanical loading failures, such as ductile fracture, brittle fracture, mechanical fatigue, and buckling; (B) Erosion, such as abrasive wear, adhesive wear, and fretting; (C) Corrosion, such as uniform corrosion, localized corrosion, and pitting; (D) Thermal-related failures, such as creep, metallurgical transformation, and thermal fatigue; (E) Cracking, such as stress-corrosion cracking; and (F) Embrittlement, such as high-temperature hydrogen attack. | 19 CCR 4.5 2762.5(e)(7) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 190 | Program 4 Prevention Program | Mechanical Integrity | DMRs include mech. load failure, erosion, corrosion, thermal issues, cracking, and embrittlement | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure damage mechanisms, for the purposes of section 2762.5, include, but are not limited to; (A) Mechanical loading failures, such as ductile fracture, brittle fracture, mechanical fatigue, and buckling; (B) Erosion, such as abrasive wear, adhesive wear, and fretting; (C) Corrosion, such as uniform corrosion, localized corrosion, and pitting; (D) Thermal-related failures, such as creep, metallurgical transformation, and thermal fatigue; (E) Cracking, such as stress-corrosion cracking; and (F) Embrittlement, such as high-temperature hydrogen attack. |  |  | OBSERVATION: Owner/operator failed to ensure that the following damage mechanisms, for the purposes of Section 2762.5, include at a minimum: mechanical loading failures,; erosion; corrosion; pitting; thermal-related failures; cracking; and embrittlement. CORRECTIVE ACTION Submit documentation to the UPA demonstrating the owner/operator has addressed the damage mechanisms above in each DMR. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010170 |  |  | Program level 4: Mechanical Integrity - DMR Assessment | Failure to ensure DMRs include: 1. An assessment of previous experience with the process including the inspection history and all damage mechanism data; 2. A review of industry-wide experience with the process; and 3. Applicable standards, codes and practices. | 19 CCR 4.5 2762.5(e)(8) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 191 | Program 4 Prevention Program | Mechanical Integrity | DMRs included previous inspection data, industry data, and applicable standards, codes and practices | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure DMRs include: 1. An assessment of previous experience with the process including the inspection history and all damage mechanism data; 2. A review of industry-wide experience with the process; and 3. Applicable standards, codes and practices. |  |  | OBSERVATION: Owner/operator failed to ensure DMRs include an assessment of previous experience with the process including inspection history and all damage mechanism data; a review of industry-wide experience with the process; and applicable standards, codes and practices. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has included the items listed above in each DMR. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010171 |  |  | Program level 4: Mechanical Integrity - DMR Report | Failure to ensure the team prepare a written DMR, at the conclusion of the analysis, that includes; (A) The process unit(s) reviewed; (B) Damage mechanisms analyzed; (C) Results of the analyses conducted according to subsection 2762.5 (e)(7); (D) Recommendations for temporary mitigation; (E) Recommendations for prevention. | 19 CCR 4.5 2762.5(e)(9) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 192 | Program 4 Prevention Program | Mechanical Integrity | Developed a complete written DMR report | 39 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the team prepare a written DMR, at the conclusion of the analysis, that includes; (A) The process unit(s) reviewed; (B) Damage mechanisms analyzed; (C) Results of the analyses conducted according to subsection 2762.5 (e)(7); (D) Recommendations for temporary mitigation; (E) Recommendations for prevention. |  |  | OBSERVATION: Owner/operator failed to prepare a written DMR that includes: the process unit(s) reviewed; damage mechanisms analyzed; results of the analyses conducted according to subsection 2762.5(e)(7); recommendations for temporary mitigation; recommendations for prevention. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has included the items listed above in each DMR. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010172 |  |  | Program level 4: Mechanical Integrity - DMR Report Review | Failure to provide and, upon request, review the report with all operating, maintenance, and other personnel, whose work assignments are within the process unit covered in the DMR. | 19 CCR 4.5 2762.5(e)(10) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 193 | Program 4 Prevention Program | Mechanical Integrity | DMRs provided to and/or reviewed with personnel working in the process covered by the DMRs | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide and, upon request, review the report with all operating, maintenance, and other personnel, whose work assignments are within the process unit covered in the DMR. |  |  | OBSERVATION: Owner/operator failed to provide and, upon request, review the DMR reports with all operating, maintenance, and other personnel whose work assignments are within the process unit. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has shared the DMR reports with personnel whose work assignments are within the applicable process units. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010173 |  |  | Program level 4: Mechanical Integrity - Corrective Action Work Process | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the DMR team's findings and recommendations, determining corrective action for implementation, tracking to completion, and documentation of closeout. | 19 CCR 4.5 2762.5(e)(11) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 194 | Program 4 Prevention Program | Mechanical Integrity | Followed corrective action work process for resolving DMR team recommendations, tracking, & closeout | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the DMR team's findings and recommendations, determining corrective action for implementation, tracking to completion, and documentation of closeout. |  |  | OBSERVATION: Owner/operator failed to follow the corrective action work process documented in subsections 2762.16(d-e) when resolving the DMR team's findings and recommendations, determining corrective action for implementation, tracking to completion, and documentation of closeout. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has complied with the items listed above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010174 |  |  | Program level 4: Mechanical Integrity - DMR Retention | Failure to retain DMR reports for the life of the process unit. | 19 CCR 4.5 2762.5(e)(12) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 195 | Program 4 Prevention Program | Mechanical Integrity | Retained DMR reports for the life of the process unit | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain DMR reports for the life of the process unit. |  |  | OBSERVATION: Owner/operator failed to retain DMR reports for the life of the process unit. CORRECTIVE ACTION: Obtain the missing DMRs for each covered process as well as the documented resolution of recommendations for the life of the process and submit a copy to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010175 |  |  | Program level 4: Management of Change - Written Procedures | Failure to develop, implement and maintain effective written Management of Change (MOC) procedures to manage changes in process chemicals, technology, procedures, process equipment, and facilities. Failure to also develop, implement and maintain written Management of Organizational Change (MOOC) procedures to manage changes in personnel or organizational issues. The MOC procedure shall include provisions for temporary repairs, including temporary piping or equipment repairs. | 19 CCR 4.5 2762.6(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 196 | Program 4 Prevention Program | Management of Change | Developed, implemented and maintained effective written MOC and MOOC procedures | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement and maintain effective written Management of Change (MOC) procedures to manage changes in process chemicals, technology, procedures, process equipment, and facilities. Failure to also develop, implement and maintain written Management of Organizational Change (MOOC) procedures to manage changes in personnel or organizational issues. The MOC procedure shall include provisions for temporary repairs, including temporary piping or equipment repairs. |  |  | OBSERVATION: Owner/operator failed to develop, implement and maintain effective written MOC procedures to manage changes in process chemicals, technology, procedures, process equipment, facilities, and temporary repairs including temporary piping or equipment repairs. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating effective written MOC procedures which address the items listed above. | OBSERVATION: Owner/operator failed to develop, implement and maintain effective written MOOC procedure to manage changes in personnel or organizational issues. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating an effective written MOOC procedure. | [5 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010176 |  |  | Program level 4: Management of Change - Criteria | Failure to ensure the MOC procedures address and document the following items prior to any change: (1) The technical basis for the proposed change;(2) Potential process safety impacts of the change; (3) Modifications to operating and maintenance procedures or development of new operating and maintenance procedures; (4) The time period required for the change; and (5) Authorization requirements for the proposed change. | 19 CCR 4.5 2762.6(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 197 | Program 4 Prevention Program | Management of Change | MOC procedures addressed and documented the required items prior to any change | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the MOC procedures address and document the following items prior to any change: (1) The technical basis for the proposed change;(2) Potential process safety impacts of the change; (3) Modifications to operating and maintenance procedures or development of new operating and maintenance procedures; (4) The time period required for the change; and (5) Authorization requirements for the proposed change. |  |  | OBSERVATION: Owner/operator failed to ensure the MOC procedures address and document the following items prior to any change: technical basis for the proposed change, potential process safety impacts of the change, modifications to operating and maintenance procedures or development of new operating and maintenance procedures, the time period required for the change, and authorization requirements for the proposed change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the MOC procedure has been revised to require the items listed above to be addressed and documented. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010177 |  |  | Program level 4: Management of Change - DMR and HCA | Failure to review or conduct a DMR pursuant to subsection 2762.5(e), and perform a Hierarchy of Hazard Control Analysis (HCA) pursuant to section 2762.13, prior to implementation of a major change. Failure to include the findings of the DMR and recommendations of the HCA in the MOC documentation. | 19 CCR 4.5 2762.6(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 198 | Program 4 Prevention Program | Management of Change | DMR reviewed and HCA conducted before a major change implementation with documented recommendations | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to review or conduct a DMR pursuant to subsection 2762.5(e), and perform a Hierarchy of Hazard Control Analysis (HCA) pursuant to section 2762.13, prior to implementation of a major change. Failure to include the findings of the DMR and recommendations of the HCA in the MOC documentation. |  |  | OBSERVATION: Owner/operator failed to review or conduct a DMR and/or HCA prior to implementation of a major change and include the findings of the DMR and recommendations of the HCA in the MOC documentation. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the appropriate DMRs and HCAs were conducted for each major change and that the findings of the DMRs and recommendations of the HCAs were included in the MOC documentation. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010178 |  |  | Program level 4: Management of Change - Qualified Personnel and Appropriate Methods | Failure to use qualified personnel and appropriate methods for MOCs based upon hazard, complexity and type of change. | 19 CCR 4.5 2762.6(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 199 | Program 4 Prevention Program | Management of Change | Qualified personnel and appropriate methods used in MOCs | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to use qualified personnel and appropriate methods for MOCs based upon hazard, complexity and type of change. |  |  | OBSERVATION: Owner/operator failed to use qualified personnel and appropriate methods for MOCs based on hazard, complexity and type of change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that deficient MOCs were reevaluated by qualified personnel and used the appropriate methods based on the hazard, complexity and type of change. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010179 |  |  | Program level 4: Management of Change - Employee Participation | Failure to provide for employee participation, pursuant to section 2762.10. | 19 CCR 4.5 2762.6(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 200 | Program 4 Prevention Program | Management of Change | Provided for employee participation in the MOC process | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide for employee participation, pursuant to section 2762.10. |  |  | OBSERVATION: Owner/operator failed to provide for employee participation in the MOC process. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that deficient MOCs were reevaluated with employee participation. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010180 |  |  | Program level 4: Management of Change - Training | Failure to ensure employees involved in the process as well as maintenance workers whose job tasks will be affected by a change, are informed of, and effectively trained in the change in a timely manner, prior to implementation of the change. Failure to make the MOC documentation available to and require effective training in the change prior to implementation of the change, pursuant to section 2762.12, for contractors and employees of contractors who are operating the process and whose job tasks are affected by a change. | 19 CCR 4.5 2762.6(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 201 | Program 4 Prevention Program | Management of Change | Affected employees/contractors informed of and trained on process changes prior to implementation | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure employees involved in the process as well as maintenance workers whose job tasks will be affected by a change, are informed of, and effectively trained in the change in a timely manner, prior to implementation of the change. Failure to make the MOC documentation available to and require effective training in the change prior to implementation of the change, pursuant to section 2762.12, for contractors and employees of contractors who are operating the process and whose job tasks are affected by a change. |  |  | OBSERVATION: Owner/operator failed to ensure employees involved in the process as well as maintenance workers whose job tasks will be affected by a change, are informed of, and effectively trained in the change in a timely manner, prior to implementation of the change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that, for MOCs not meeting the training requirements, employees and maintenance workers have been informed of and effectively trained in the change. | OBSERVATION: Owner/operator failed to ensure contractors and employees of contractors operating the process whose job tasks will be affected by a change, are provided the MOC documentation and are effectively trained in the change in a timely manner, prior to implementation of the change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that, for MOCs not meeting the training requirements, contractors and employees of contractors have been provided the necessary MOC documentation and effectively trained in the change. | [5 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010181 |  |  | Program level 4: Management of Change - Process Safety Information | Failure to update information as soon as possible for a change covered by section 2762.6 that results in a change to the Process Safety Information required by section 2762.1. | 19 CCR 4.5 2762.6(g) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 202 | Program 4 Prevention Program | Management of Change | Process safety information updated as soon as possible when affected by a process change | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update information as soon as possible for a change covered by section 2762.6 that results in a change to the Process Safety Information required by section 2762.1. |  |  | OBSERVATION: Owner/operator failed to update information as soon as possible for a change that resulted in a change to the Process Safety Information. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that Process Safety Information has been updated as necessary for each deficient MOC. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010182 |  |  | Program level 4: Management of Change - Operating Procedures | Failure to update procedures prior to the start-up of the process for a change covered by section 2762.6 that results in a change to the Operating Procedures required by section 2762.3, or results in a change in the written procedures to maintain the ongoing integrity of process equipment required by section 2762.5. | 19 CCR 4.5 2762.6(h) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 203 | Program 4 Prevention Program | Management of Change | Operating and maintenance procedures updated prior to start-up when affected by a process change | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update procedures prior to the start-up of the process for a change covered by section 2762.6 that results in a change to the Operating Procedures required by section 2762.3, or results in a change in the written procedures to maintain the ongoing integrity of process equipment required by section 2762.5. |  |  | OBSERVATION: Owner/operator failed to update procedures prior to the start-up of the process for a change that resulted in a change to operating or maintenance procedures. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that operating and maintenance procedures have been updated as necessary for each deficient MOC. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010183 |  |  | Program level 4: Management of Change - Organizational Change | Failure to develop, implement, and maintain effective written procedures to manage organizational change. | 19 CCR 4.5 2762.6(i) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 204 | Program 4 Prevention Program | Management of Change | Developed, implemented, and maintained effective written organizational change procedures | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement, and maintain effective written procedures to manage organizational change. |  |  | OBSERVATION: Owner/operator failed to develop, implement, and maintain effective written procedures to manage organizational changes. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that effective written procedures to manage organizational changes have been developed, implemented, and will be maintained. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010184 |  |  | Program level 4: Management of Change - MOOC Assessment | Failure to designate a team to conduct a Management of Organizational Change (MOOC) assessment prior to reducing staffing levels, reducing classification levels of employees, changing shift duration, or substantively increasing employee responsibilities at or above 15%. Failure to ensure this requirement also applies to using contractors in permanent positions. | 19 CCR 4.5 2762.6(j) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 205 | Program 4 Prevention Program | Management of Change | Designated MOOC team to assess organizational changes | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to designate a team to conduct a Management of Organizational Change (MOOC) assessment prior to reducing staffing levels, reducing classification levels of employees, changing shift duration, or substantively increasing employee responsibilities at or above 15%. Failure to ensure this requirement also applies to using contractors in permanent positions. |  |  | OBSERVATION: Owner/operator failed to designate a team to conduct a Management of Organizational Change (MOOC) assessment prior to reducing staffing levels, reducing classification levels of employees or contractors in permanent positions, changing shift duration, or substantively increasing employee or permanent contractor responsibilities at or above 15%. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that a team conducted a MOOC assessment prior to implementing any of the items listed above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010185 |  |  | Program level 4: Management of Change - MOOC Assessment Requirements | Failure to ensure the MOOC is in writing and includes a description of the change being proposed; the makeup of the team responsible for assessing the proposed change; the factors evaluated by the team; the rationale for the team’s decision to implement or not implement the change; and the team’s findings and recommendations. (1) Failure to ensure that the job function descriptions are current and accurate for all positions potentially affected by the change prior to conducting the MOOC. (2) Failure to provide for employee participation pursuant to section 2762.10. (3) Failure to include an assessment of human factors, pursuant to section 2762.15, for All MOOC analyses. (4) Failure to ensure the stationary source manager, or his or her designee, certify based on information and belief formed after reasonable inquiry that the MOOC assessment is accurate and that the proposed organizational change(s) meets the requirements of section 2762.6. | 19 CCR 4.5 2762.6(k) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 206 | Program 4 Prevention Program | Management of Change | MOOC documentation included assessment requirements | 52 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the MOOC is in writing and includes a description of the change being proposed; the makeup of the team responsible for assessing the proposed change; the factors evaluated by the team; the rationale for the team’s decision to implement or not implement the change; and the team’s findings and recommendations. (1) Failure to ensure that the job function descriptions are current and accurate for all positions potentially affected by the change prior to conducting the MOOC. (2) Failure to provide for employee participation pursuant to section 2762.10. (3) Failure to include an assessment of human factors, pursuant to section 2762.15, for All MOOC analyses. (4) Failure to ensure the stationary source manager, or his or her designee, certify based on information and belief formed after reasonable inquiry that the MOOC assessment is accurate and that the proposed organizational change(s) meets the requirements of section 2762.6. |  |  | OBSERVATION: Owner/operator failed to ensure the MOOC is in writing and includes a description of the change being proposed; the makeup of the team responsible for assessing the proposed change; the factors evaluated by the team; the rationale for the team's decision to implement or not implement the change; and the team's findings and recommendations. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that MOOC documentation has been developed and includes the items listed above. | OBSERVATION: Owner/operator failed to ensure that job function descriptions are current and accurate for all positions potentially affected by the change prior to conducting the MOOC. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that job function descriptions for positions potentially affected by the MOOC are complete and accurate. | OBSERVATION: Owner/operator failed to provide for employee participation in the MOOC process. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that MOOCs were reevaluated with employee participation. | OBSERVATION: Owner/operator failed to include an assessment of human factors for all MOOC analyses. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that a human factors assessment was conducted for all deficient MOOC analyses. | OBSERVATION: Owner/operator failed to ensure the stationary source manager, or his or her designee, certify based on information and belief formed after reasonable inquiry that the MOOC assessment is accurate and that the proposed organizational change(s) meets the MOOC requirements. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the stationary source manager, or his or her designee, certified the MOOC assessment as accurate and that the proposed organizational change(s) meet the MOOC requirements. |  |  | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010186 |  |  | Program level 4: Management of Change - Informing Affected Employees | Failure to inform all employees potentially affected by the change prior to implementing a change. | 19 CCR 4.5 2762.6(l) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 207 | Program 4 Prevention Program | Management of Change | Informed affected employees of changes prior to implementation | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to inform all employees potentially affected by the change prior to implementing a change. |  |  | OBSERVATION: Owner/operator failed to inform all employees potentially affected by the organizational change prior to implementing the change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that all potentially affected employees are informed of the organizational change. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010187 |  |  | Program level 4: Pre-Startup Safety Review - General Requirements | Failure to perform a pre-startup safety review (PSSR) for new processes, for modified processes if the modification necessitates a change in the Process Safety Information, and for partial and unplanned shutdowns. Failure to also conduct a PSSR for all turnaround work performed on a process. | 19 CCR 4.5 2762.7(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 208 | Program 4 Prevention Program | Pre-Startup Safety Review | PSSRs performed for new and modified processes with changes to PSI, partial and unplanned shutdowns | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform a pre-startup safety review (PSSR) for new processes, for modified processes if the modification necessitates a change in the Process Safety Information, and for partial and unplanned shutdowns. Failure to also conduct a PSSR for all turnaround work performed on a process. |  |  | OBSERVATION: Owner/operator failed to perform a PSSR for new processes, for modified processes if the modification necessitates a change in the PSI, for partial and unplanned shutdowns, and for all turnaround work performed on a process. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that PSSRs have been completed for the items listed above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010188 |  |  | Program level 4: Pre-Startup Safety Review - Verification Check | Failure to confirm, as a verification check, independent of the management of change process, that prior to the introduction of highly hazardous materials to a process: (1) Construction, maintenance, and repair work has been performed in accordance with design specifications; (2) Process equipment has been maintained and is operable in accordance with design specifications; (3) Effective safety, operating, maintenance, and emergency procedures are in place; (4) For new process units, a PHA, HCA, DMR, and SPA have each been performed as applicable pursuant to Article 6.5, and recommendations have been implemented or resolved before start-up. For new or modified processes, all changes have been implemented in accordance with the requirements contained in the MOC, section 2762.6; and, (5) Training of each operating employee and maintenance employee affected by the change has been completed. | 19 CCR 4.5 2762.7(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 209 | Program 4 Prevention Program | Pre-Startup Safety Review | Independently verified the required items prior to change implementation | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to confirm, as a verification check, independent of the management of change process, that prior to the introduction of highly hazardous materials to a process: (1) Construction, maintenance, and repair work has been performed in accordance with design specifications; (2) Process equipment has been maintained and is operable in accordance with design specifications; (3) Effective safety, operating, maintenance, and emergency procedures are in place; (4) For new process units, a PHA, HCA, DMR, and SPA have each been performed as applicable pursuant to Article 6.5, and recommendations have been implemented or resolved before start-up. For new or modified processes, all changes have been implemented in accordance with the requirements contained in the MOC, section 2762.6; and, (5) Training of each operating employee and maintenance employee affected by the change has been completed. |  |  | OBSERVATION: Owner/operator failed to confirm, as a verification check, independent of the management of change process, that prior to the introduction of highly hazardous materials to a process: construction, maintenance, and repair work has been performed in accordance with design specifications; process equipment has been maintained and is operable in accordance with design specifications; effective safety, operating, maintenance, and emergency procedures are in place; for new process units, a PHA, HCA, DMR, and SPA have each been performed as applicable pursuant to Article 6.5, and recommendations have been implemented or resolved before start-up; for new or modified processes, all changes have been implemented per the MOC; training of operating maintenance employees affected by the change has been completed. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that a verification check independent of the MOC has been completed for the items listed above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010189 |  |  | Program level 4: Pre-Startup Safety Review - Employee Representative | Failure to designate as the employee representative, pursuant to section 2762.10, an operating employee who currently works in the unit and has expertise and experience in the process being started. | 19 CCR 4.5 2762.7(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 210 | Program 4 Prevention Program | Pre-Startup Safety Review | Designated an operating employee as employee representative for PSSRs | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to designate as the employee representative, pursuant to section 2762.10, an operating employee who currently works in the unit and has expertise and experience in the process being started. |  |  | OBSERVATION: Owner/operator failed to designate as the employee representative an operating employee who currently works in the unit and has expertise and experience in the process being started. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that an appropriate operating employee was designated as the employee representative for the PSSR process. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010190 |  |  | Program level 4: Compliance Audits - Certification | Failure to conduct an effective compliance audit and certify every three (3) years that the procedures and practices developed under Article 6.5 have been evaluated to verify they are in compliance with the provisions of Article 6.5, and are being followed. | 19 CCR 4.5 2762.8(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 211 | Program 4 Prevention Program | Compliance Audits | Conducted effective compliance audit and certified every three years in compliance with Article 6.5 | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to conduct an effective compliance audit and certify every three (3) years that the procedures and practices developed under Article 6.5 have been evaluated to verify they are in compliance with the provisions of Article 6.5, and are being followed. |  |  | OBSERVATION: Owner/operator failed to certify that they have evaluated compliance with the provisions of Article 6.5 at least every three years to verify that the procedures and practices developed under Article 6.5 are adequate and are being followed. CORRECTIVE ACTION: Submit a certification to the CUPA that the owner/operator has evaluated compliance with the provisions of Article 6.5 at least every three years to verify that the procedures and practices developed under Article 6.5 are adequate and are followed. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010191 |  |  | Program level 4: Compliance Audits - Knowledgeable Person | Failure to ensure the compliance audit is conducted by at least one person knowledgeable in the requirements of the Article 6.5 section under review. | 19 CCR 4.5 2762.8(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 212 | Program 4 Prevention Program | Compliance Audits | Conducted compliance audit by a person knowledgeable in the requirements of Article 6.5 | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the compliance audit is conducted by at least one person knowledgeable in the requirements of the Article 6.5 section under review. |  |  | OBSERVATION: Owner/operator failed to ensure that the compliance audit is conducted by at least one person knowledgeable of the requirements of Article 6.5 under review. CORRECTIVE ACTION: Conduct the compliance audit with at least one person knowledgeable of the requirements of Article 6.5 under review. Develop a report of the compliance audit findings, including appropriate responses to each of the findings and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010192 |  |  | Program level 4: Compliance Audits - Report | Failure to prepare a written report of the compliance audit that includes the scope, methods used, questions asked to assess each program element along with findings and recommendations of the compliance audit. Failure to ensure the written report also documents the qualifications of those persons performing the compliance audit. Failure to make the report available to employees and employee representatives, in accordance with section 2762.10. Failure to respond in writing within 60 calendar days to any written employee or employee representative comments on the written audit report. | 19 CCR 4.5 2762.8(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 213 | Program 4 Prevention Program | Compliance Audits | Prepared a compliance audit written report, documented team qualif's, made available to employees | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a written report of the compliance audit that includes the scope, methods used, questions asked to assess each program element along with findings and recommendations of the compliance audit. Failure to ensure the written report also documents the qualifications of those persons performing the compliance audit. Failure to make the report available to employees and employee representatives, in accordance with section 2762.10. Failure to respond in writing within 60 calendar days to any written employee or employee representative comments on the written audit report. |  |  | OBSERVATION: Owner/operator failed to: Prepare a written report of the compliance audit assessing each program element along with findings of the audit; ensure the report documents the qualifications of those persons performing the audit; make the report available to employees and employee representatives, in accordance with section 2762.10; and/or respond in writing within 60 calendar days to any written employee or employee representative comments on the written audit report. CORRECTIVE ACTION: Prepare a written report of the compliance audit that includes the scope, methods used, questions asked to assess each program element along with findings and recommendations of the compliance audit. Ensure the written report also documents the qualifications of those persons performing the compliance audit. Make the report available to employees and employee representatives. Respond in writing to any written employee or employee representative comments on the written audit report. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010193 |  |  | Program level 4: Compliance Audits - Corrective Action Work Process | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when developing the resolution and implementation of the compliance audit recommendations. | 19 CCR 4.5 2762.8(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 214 | Program 4 Prevention Program | Compliance Audits | Followed corrective work action process for resolution and implementation of the compliance audit | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when developing the resolution and implementation of the compliance audit recommendations. |  |  | OBSERVATION: Owner/operator failed to: Follow the corrective action work process documented in subsections 2762.16 (d) and (e) when developing the resolution and implementation of the compliance audit recommendations. CORRECTIVE ACTION: Submit documentation to the UPA of compliance with the corrective action work process of the compliance audit recommendations. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010194 |  |  | Program level 4: Compliance Audits - Retention | Failure to retain the three (3) most recent compliance audit reports. | 19 CCR 4.5 2762.8(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 215 | Program 4 Prevention Program | Compliance Audits | Retained three most recent compliance audit reports | 51 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain the three (3) most recent compliance audit reports. |  |  | OBSERVATION: Owner/operator failed to retain the three (3) most recent compliance audit reports. CORRECTIVE ACTION: Obtain, retain and submit to the UPA copies of the three (3) most recent compliance audit reports | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010195 |  |  | Program level 4: Compliance Audits - Consultations | Failure to consult with operators with expertise and experience in each process audited and document the findings and recommendations from these consultations in the audit report, as part of the compliance audit. | 19 CCR 4.5 2762.8(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 216 | Program 4 Prevention Program | Compliance Audits | Consulted with operators and documented findings in the compliance audit report | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to consult with operators with expertise and experience in each process audited and document the findings and recommendations from these consultations in the audit report, as part of the compliance audit. |  |  | OBSERVATION: Owner/operator failed to consult with operators with expertise and experience in each process audited and document the findings and recommendations from these consultations in the audit report, as part of the compliance audit. CORRECTIVE ACTION: Submit documentation of proper consultation with the appropriate operators and of the documentation of findings and recommendations from these consultations. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010196 |  |  | Program level 4: Incident Investigation - Written Procedures | Failure to develop, implement, and maintain effective written procedures for promptly investigating and reporting any incident that results in or could reasonably have resulted in a major incident. | 19 CCR 4.5 2762.9(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 217 | Program 4 Prevention Program | Incident Investigation | Effective incident investigation procedures are written and implemented | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement, and maintain effective written procedures for promptly investigating and reporting any incident that results in or could reasonably have resulted in a major incident. |  |  | OBSERVATION: Owner/operator failed to develop, implement, and maintain effective written procedures for promptly investigating and reporting any incident that results in or could reasonably have resulted in a major incident. CORRECTIVE ACTION: Submit documentation of proper written procedures stemming from a major incident report | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010197 |  |  | Program level 4: Incident Investigation - Root Cause Analysis | Failure to ensure written procedures include an effective method for conducting a thorough root cause analysis. | 19 CCR 4.5 2762.9(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 218 | Program 4 Prevention Program | Incident Investigation | Effective method to conduct a thorough Root Cause Analysis procedure is written | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure written procedures include an effective method for conducting a thorough root cause analysis. |  |  | OBSERVATION: Owner/operator failed to ensure written procedures include an effective method for conducting a thorough root cause analysis. CORRECTIVE ACTION: Submit documentation of an effective method for conducting a thorough Root Cause Analysis. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010198 |  |  | Program level 4: Incident Investigation - Promptness | Failure to initiate the incident investigation as promptly as possible, but no later than 48 hours following an incident. | 19 CCR 4.5 2762.9(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 219 | Program 4 Prevention Program | Incident Investigation | Incident investigation initiated within 48 hours following an incident | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to initiate the incident investigation as promptly as possible, but no later than 48 hours following an incident. |  |  | OBSERVATION: Owner/operator failed to initiate the incident investigation as promptly as possible, but no later than 48 hours following an incident. CORRECTIVE ACTION: Immediately initiate an incident investigation/ Submit procedure to ensure incident investigations begin as promptly as possible, but no later than 48 hours following an incident. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010199 |  |  | Program level 4: Incident Investigation - Team Qualifications | Failure to ensure an incident investigation team is established and, at a minimum, consist of a person with expertise and experience in the process involved, a person with expertise in the owner or operator's root cause analysis method, and a person with expertise in overseeing the investigation and analysis. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure an employee and employee representative of that contractor, if applicable, is also included on the investigation team if the incident involved the work of a contractor. | 19 CCR 4.5 2762.9(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 220 | Program 4 Prevention Program | Incident Investigation | Investigation team consists of personnel with appropriate expertise | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure an incident investigation team is established and, at a minimum, consist of a person with expertise and experience in the process involved, a person with expertise in the owner or operator's root cause analysis method, and a person with expertise in overseeing the investigation and analysis. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure an employee and employee representative of that contractor, if applicable, is also included on the investigation team if the incident involved the work of a contractor. |  |  | OBSERVATION: Owner/operator failed to ensure an incident investigation team is established and, at a minimum, consist of a person with expertise and experience in the process involved, a person with expertise in the owner or operator's root cause analysis method, and a person with expertise in overseeing the investigation and analysis. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure an employee and employee representative of that contractor, if applicable, is also included on the investigation team if the incident involved the work of a contractor. CORRECTIVE ACTION: Submit documentation of proper incident investigation team qualifications. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010200 |  |  | Program level 4: Incident Investigation - RCA Method | Failure to ensure the incident investigation team implement the owner or operator's root cause analysis method to determine the underlying causes of the incident. Failure to ensure the analysis include identification of management system causes, including organizational and safety culture causes. | 19 CCR 4.5 2762.9(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 221 | Program 4 Prevention Program | Incident Investigation | Root Cause Analysis includes management system, organizational and safety culture causes | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the incident investigation team implement the owner or operator's root cause analysis method to determine the underlying causes of the incident. Failure to ensure the analysis include identification of management system causes, including organizational and safety culture causes. |  |  | OBSERVATION: Owner/operator failed to ensure the incident investigation team implement the owner or operator's root cause analysis method to determine the underlying causes of the incident. Failure to ensure the analysis include identification of management system causes, including organizational and safety culture causes. CORRECTIVE ACTION: Submit documentation of proper root cause analysis methods including management system, organizational and safety culture causes. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010201 |  |  | Program level 4: Incident Investigation - DMR | Failure to ensure the team review the related DMRs that were performed pursuant to section 2762.5(e) and incorporate the applicable findings from these DMRs into the incident investigation. | 19 CCR 4.5 2762.9(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 222 | Program 4 Prevention Program | Incident Investigation | Incident Investigation team reviewed related DMR and incorporated findings into its report | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the team review the related DMRs that were performed pursuant to section 2762.5(e) and incorporate the applicable findings from these DMRs into the incident investigation. |  |  | OBSERVATION: Owner/operator failed to ensure the team review the related DMRs that were performed pursuant to section 2762.5(e) and incorporate the applicable findings from these DMRs into the incident investigation. CORRECTIVE ACTION: Submit documentation of proper review of related DMRs and their incorporation into the incident investigation. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010202 |  |  | Program level 4: Incident Investigation - Recommendations | Failure to ensure the incident investigation team develop recommendations to address the findings of the investigation. Failure to ensure recommendations include interim actions that will reduce the risk of a recurrence or similar incident until final actions can be implemented. Failure to perform an HCA pursuant to section 2762.13, for recommendations that result from the investigation of a major incident. Failure to append the HCA report to the final investigation report. | 19 CCR 4.5 2762.9(g) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 223 | Program 4 Prevention Program | Incident Investigation | Incident Investigation team developed recommendations and interim actions to reduce risk | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the incident investigation team develop recommendations to address the findings of the investigation. Failure to ensure recommendations include interim actions that will reduce the risk of a recurrence or similar incident until final actions can be implemented. Failure to perform an HCA pursuant to section 2762.13, for recommendations that result from the investigation of a major incident. Failure to append the HCA report to the final investigation report. |  |  | OBSERVATION: Owner/operator failed to ensure the incident investigation team develop recommendations to address the findings of the investigation. Failure to ensure recommendations include interim actions that will reduce the risk of a recurrence or similar incident until final actions can be implemented. Failure to perform an HCA pursuant to section 2762.13, for recommendations that result from the investigation of a major incident. Failure to append the HCA report to the final investigation report. CORRECTIVE ACTION: Submit documentation of the incident team's recommendations addressing the findings of its investigation and interim actions to reduce risk. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010203 |  |  | Program level 4: Incident Investigation - Report | Failure to submit a written report for major incidents to the UPA within 90 calendar days of the incident. Failure to prepare a status report within 90 calendar days of the incident and every 30 calendar days thereafter until the investigation is complete for cases where the owner or operator has demonstrated that additional time is needed due to the complexity of the investigation. Failure to submit a final report within five (5) months of the incident. | 19 CCR 4.5 2762.9(h) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 224 | Program 4 Prevention Program | Incident Investigation | Investigation report/status updates for major incidents submitted to UPA as required | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to submit a written report for major incidents to the UPA within 90 calendar days of the incident. Failure to prepare a status report within 90 calendar days of the incident and every 30 calendar days thereafter until the investigation is complete for cases where the owner or operator has demonstrated that additional time is needed due to the complexity of the investigation. Failure to submit a final report within five (5) months of the incident. |  |  | OBSERVATION: Owner/operator failed to submit a written report for major incidents to the UPA within 90 calendar days of the incident. Failure to prepare a status report within 90 calendar days of the incident and every 30 calendar days thereafter until the investigation is complete for cases where the owner or operator has demonstrated that additional time is needed due to the complexity of the investigation. Failure to submit a final report within five (5) months of the incident. CORRECTIVE ACTION: Immediately submit a written report of a major incident or a status report to the UPA . | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010204 |  |  | Program level 4: Incident Investigation - Report Contents | Failure to ensure the investigation report includes: (1) Date and time of the incident; (2) Date and time the investigation began; (3) A detailed description of the incident; (4) The factors that caused or contributed to the incident, including direct causes, indirect causes and root causes, determined through the root cause analysis; (5) A list of any DMR(s), PHA(s), HCA(s), and SPA(s) that were reviewed as part of the investigation; (6) Interim recommendations to prevent a recurrence or similar incident; (7) Recommendations for permanent corrective actions. | 19 CCR 4.5 2762.9(i) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 225 | Program 4 Prevention Program | Incident Investigation | Investigation report is thorough and complete | 45 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the investigation report includes: (1) Date and time of the incident; (2) Date and time the investigation began; (3) A detailed description of the incident; (4) The factors that caused or contributed to the incident, including direct causes, indirect causes and root causes, determined through the root cause analysis; (5) A list of any DMR(s), PHA(s), HCA(s), and SPA(s) that were reviewed as part of the investigation; (6) Interim recommendations to prevent a recurrence or similar incident; (7) Recommendations for permanent corrective actions. |  |  | OBSERVATION: Owner/operator failed to ensure the investigation report includes: (1) Date and time of the incident; (2) Date and time the investigation began; (3) A detailed description of the incident; (4) The factors that caused or contributed to the incident, including direct causes, indirect causes and root causes, determined through the root cause analysis; (5) A list of any DMR(s), PHA(s), HCA(s), and SPA(s) that were reviewed as part of the investigation; (6) Interim recommendations to prevent a recurrence or similar incident; (7) Recommendations for permanent corrective actions. CORRECTIVE ACTION: Submit completed investigation report which includes all required contents. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010205 |  |  | Program level 4: Incident Investigation - Report Availability | Failure to ensure the report is provided to and, upon request, reviewed with employees whose job tasks are affected by the incident. Failure to ensure investigation reports are also made available to all operating, maintenance, and other personnel, including employees of contractors where applicable, whose work assignments are within the facility where the incident occurred or whose job tasks are relevant to the incident findings. Failure to ensure investigation reports are provided upon request to employee representatives, and where applicable, contractor employee representatives. | 19 CCR 4.5 2762.9(k) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 226 | Program 4 Prevention Program | Incident Investigation | Investigation report available to personnel whose job tasks are relevant to the incident findings | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the report is provided to and, upon request, reviewed with employees whose job tasks are affected by the incident. Failure to ensure investigation reports are also made available to all operating, maintenance, and other personnel, including employees of contractors where applicable, whose work assignments are within the facility where the incident occurred or whose job tasks are relevant to the incident findings. Failure to ensure investigation reports are provided upon request to employee representatives, and where applicable, contractor employee representatives. |  |  | OBSERVATION: Owner/operator failed to ensure the report is provided to and, upon request, reviewed with employees whose job tasks are affected by the incident. Failure to ensure investigation reports are also made available to all operating, maintenance, and other personnel, including employees of contractors where applicable, whose work assignments are within the facility where the incident occurred or whose job tasks are relevant to the incident findings. Failure to ensure investigation reports are provided upon request to employee representatives, and where applicable, contractor employee representatives. CORRECTIVE ACTION: Submit documentation that the incident investigation report has been made available to all appropriate personnel whose job tasks are relevant to the incident findings. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010206 |  |  | Program level 4: Incident Investigation - Corrective Action | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e), when resolving the investigation team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. Failure to ensure the corrective action plan include review, and revalidation as necessary, of the appropriate portions of all relevant PHAs and DMRs. | 19 CCR 4.5 2762.9(l) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 227 | Program 4 Prevention Program | Incident Investigation | Corrective action work process documented and relevant PHAs and DMRs reviewed | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e), when resolving the investigation team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. Failure to ensure the corrective action plan include review, and revalidation as necessary, of the appropriate portions of all relevant PHAs and DMRs. |  |  | OBSERVATION: Owner/operator failed to follow the corrective action work process documented in subsections 2762.16 (d) and (e), when resolving the investigation team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. Failure to ensure the corrective action plan include review, and revalidation as necessary, of the appropriate portions of all relevant PHAs and DMRs. CORRECTIVE ACTION: Submit documentation of compliance with the corrective action findings and recommendations and of review of the relevant PHAs and DMRs. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010207 |  |  | Program level 4: Incident Investigation - Retention | Failure to ensure incident investigation reports are retained for the life of the process unit. | 19 CCR 4.5 2762.9(m) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 228 | Program 4 Prevention Program | Incident Investigation | Incident investigation reports retained for the life of the unit | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure incident investigation reports are retained for the life of the process unit. |  |  | OBSERVATION: Owner/operator failed to ensure incident investigation reports are retained for the life of the process unit. CORRECTIVE ACTION: Obtain, retain and submit documentation of all incident reports for the life of the process unit. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010208 |  |  | Program level 4: Incident Investigation - Independent Analysis | Failure to assist the UPA in conducting an independent analysis, when the UPA chooses to perform an independent Process Safety Culture Assessment (PSCA), Incident Investigation, evaluation of the ARP management system or Human Factors Analysis after a major incident pursuant to section 2775.2.5. | 19 CCR 4.5 2762.9(n) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 229 | Program 4 Prevention Program | Incident Investigation | Assisted UPA to perform an independent analysis after a major incident | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to assist the UPA in conducting an independent analysis, when the UPA chooses to perform an independent Process Safety Culture Assessment (PSCA), Incident Investigation, evaluation of the ARP management system or Human Factors Analysis after a major incident pursuant to section 2775.2.5. |  |  | OBSERVATION: Owner/operator failed to assist the UPA in conducting an independent analysis, when the UPA chooses to perform an independent Process Safety Culture Assessment (PSCA), Incident Investigation, evaluation of the ARP management system or Human Factors Analysis after a major incident pursuant to section 2775.2.5. CORRECTIVE ACTION: Immediately assist the UPA in conducting an independent analysis of PSCA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010209 |  |  | Program level 4: Employee Participation - Plan | Failure to develop, implement and maintain a written plan to effectively provide for employee participation in Accidental Release Prevention elements, as required by Article 6.5. Failure to ensure the plan include provisions that provide for the following: (1) Effective participation by affected operating and maintenance employees and employee representatives, throughout all phases, in performing PHAs, DMRs, HCAs, MOCs, MOOCs, Process Safety Culture Assessments (PSCAs), Incident Investigations, SPAs, and PSSRs; (2) Effective participation by affected operating and maintenance employees and employee representatives, throughout all phases of in the development, training, implementation and maintenance of the Accidental Release Prevention elements required by Article 6.5. (3) Access by employees and employee representatives to all documents or information developed or collected by the owner or operator pursuant to Article 6.5, including information that might be subject to protection as a trade secret | 19 CCR 4.5 2762.10(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 230 | Program 4 Prevention Program | Employee Participation | Written employee participation plan developed, implemented & maintained | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement and maintain a written plan to effectively provide for employee participation in Accidental Release Prevention elements, as required by Article 6.5. Failure to ensure the plan include provisions that provide for the following: (1) Effective participation by affected operating and maintenance employees and employee representatives, throughout all phases, in performing PHAs, DMRs, HCAs, MOCs, MOOCs, Process Safety Culture Assessments (PSCAs), Incident Investigations, SPAs, and PSSRs; (2) Effective participation by affected operating and maintenance employees and employee representatives, throughout all phases of in the development, training, implementation and maintenance of the Accidental Release Prevention elements required by Article 6.5. (3) Access by employees and employee representatives to all documents or information developed or collected by the owner or operator pursuant to Article 6.5, including information that might be subject to protection as a trade secret |  |  | OBSERVATION: Owner/operator failed to: develop, implement and maintain a written plan to effectively provide for employee participation in Accidental Release Prevention elements, as required by Article 6.5, ensure the plan includes provisions that provide for effective participation by affected operating and maintenance employees and employee representatives and access by employees and employee representatives the following: (1) throughout all phases, in performing PHAs, DMRs, HCAs, MOCs, MOOCs, PSCAs, Incident Investigations, SPAs, and PSSRs; (2) throughout all phases of in the development, training, implementation and maintenance of the Accidental Release Prevention elements required by Article 6.5; (3) to all documents or information developed or collected by the owner or operator pursuant to Article 6.5, including information that might be subject to protection as a trade secret. CORRECTIVE ACTION: Submit documentation of compliance with employee participation. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010210 |  |  | Program level 4: Employee Participation - Employee Representative Selection | Failure to establish effective procedures in consultation with employees for the selection of employee representatives, where employees are not represented by an authorized collective bargaining agent. | 19 CCR 4.5 2762.10(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 231 | Program 4 Prevention Program | Employee Participation | Established procedures to select non union employee representatives | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to establish effective procedures in consultation with employees for the selection of employee representatives, where employees are not represented by an authorized collective bargaining agent. |  |  | OBSERVATION: Owner/operator failed to establish effective procedures in consultation with employees for the selection of employee representatives, where employees are not represented by an authorized collective bargaining agent. CORRECTIVE ACTION: Submit documentation of effective procedures to provide proper non union employee representative participation. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010211 |  |  | Program level 4: Hot Work Permit - Hot Work Operations | Failure to issue a hot work permit for hot work operations conducted on or near a covered process. | 19 CCR 4.5 2762.11(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 232 | Program 4 Prevention Program | Hot Work Permit | Hot work permits issued for operations on or near a covered process | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to issue a hot work permit for hot work operations conducted on or near a covered process. |  |  | OBSERVATION: Owner/operator Failed to issue a hot work permit for hot work operations conducted on or near a covered process. CORRECTIVE ACTION: Submit documentation to ensure hot work permits are properly issued. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010212 |  |  | Program level 4: Hot Work Permit - Fire Prevention and Protection | Failure to ensure the permit documents that the fire prevention and protection requirements in section 5189 of Title 8 of CCR have been implemented prior to beginning the hot work operations; failure to indicate the date(s) and time(s) authorized for hot work; and identify the equipment or process on which hot work is to be performed. Failure to ensure the permit is kept on file for one year. | 19 CCR 4.5 2762.11(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 233 | Program 4 Prevention Program | Hot Work Permit | Hot work permits issued fire prevention & protection requirements & retained on file for one year | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the permit documents that the fire prevention and protection requirements in section 5189 of Title 8 of CCR have been implemented prior to beginning the hot work operations; failure to indicate the date(s) and time(s) authorized for hot work; and identify the equipment or process on which hot work is to be performed. Failure to ensure the permit is kept on file for one year. |  |  | OBSERVATION: Owner/operator failed to ensure the permit documents that the fire prevention and protection requirements in section 5189 of Title 8 of CCR have been implemented prior to beginning the hot work operations; failure to indicate the date(s) and time(s) authorized for hot work; and identify the equipment or process on which hot work is to be performed. Failure to ensure the permit is kept on file for one year. CORRECTIVE ACTION: Submit documentation to ensure the hot work permit has proper fire prevention and protection requirements and are retained for one year. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010213 |  |  | Program level 4: Contractors - Owner/Operator Responsibilities | (1) Failure to obtain and evaluate information regarding the contract owner or operator's safety performance and programs, when selecting a contractor, and require that its contractors and any subcontractors use a skilled and trained workforce pursuant to Health and Safety Code Section 25536.7. (2) Failure to inform the contract owner or operator and ensure that the contract owner or operator has informed each of its employees of the work practices necessary to safely perform his or her jobs, including but not limited to: the potential hazards related to their jobs; applicable refinery safety rules; and in the applicable provisions of the stationary source's emergency action plan. (3) Failure to explain to the contract owner or operator the applicable provisions of Article 7. (4) Failure to develop and implement effective written procedures to ensure the safe entry, presence, and exit of the contract owner or operator and contract employees in process areas. (5) Failure to periodically evaluate the performance of the contract owner or operator in fulfilling their obligations as specified in subsection 2762.12 (c). (6) Failure to ensure and document that the requirements of section 2762.12 are performed and completed by the contractor owner or operator. | 19 CCR 4.5 2762.12(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 234 | Program 4 Prevention Program | Contractors | Contractor safety performance and programs reviewed | 51 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | (1) Failure to obtain and evaluate information regarding the contract owner or operator's safety performance and programs, when selecting a contractor, and require that its contractors and any subcontractors use a skilled and trained workforce pursuant to Health and Safety Code Section 25536.7. (2) Failure to inform the contract owner or operator and ensure that the contract owner or operator has informed each of its employees of the work practices necessary to safely perform his or her jobs, including but not limited to: the potential hazards related to their jobs; applicable refinery safety rules; and in the applicable provisions of the stationary source's emergency action plan. (3) Failure to explain to the contract owner or operator the applicable provisions of Article 7. (4) Failure to develop and implement effective written procedures to ensure the safe entry, presence, and exit of the contract owner or operator and contract employees in process areas. (5) Failure to periodically evaluate the performance of the contract owner or operator in fulfilling their obligations as specified in subsection 2762.12 (c). (6) Failure to ensure and document that the requirements of section 2762.12 are performed and completed by the contractor owner or operator. |  |  | OBSERVATION: Owner/operator failed to (1) obtain and evaluate information regarding the contract owner or operator's safety performance and programs and require use of a skilled and trained workforce pursuant to H&SC Sec 25536.7. (2) inform and ensure the contract owner or operator has informed each of its employees of the work practices necessary to safely perform their jobs. (3) explain to the contract owner or operator provisions of Article 7. (4) develop and implement effective written procedures to ensure the safe entry, presence, and exit of the contract owner or operator and contract employees in process areas. (5) periodically evaluate the contract owner or operator in fulfilling their obligations as specified in subsection 2762.12 (c). (6) ensure and document the contractor owner or operator complies with section 2762.12. CORRECTIVE ACTION: Submit documentation of the review of contractor's safety performance and programs. | OBSERVATION: Owner/operator failed to ensure the permit documents that the fire prevention and protection requirements in section 5189 of Title 8 of CCR have been implemented prior to beginning the hot work operations; failure to indicate the date(s) and time(s) authorized for hot work; and identify the equipment or process on which hot work is to be performed. Failure to ensure the permit is kept on file for one year. | [5 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010214 |  |  | Program level 4: Contractors - Contract Owner/Operator Responsibilities | Failure to ensure the contract owner/operator is performing the following responsibilities: (1) Ensure that each contract employee is trained in the work practices necessary to safely perform his or her jobs, including but not limited to: the potential hazards related to their jobs; applicable refinery safety rules; and in the applicable provisions of the stationary source's emergency action plan, and shall meet the requirements of Health and Safety Code Section 25536.7. (2) Documents that each contract employee has successfully completed the training required by section 2762.12 by maintaining a record identifying: (A) each employee who has received training; (B) the date(s) and subject(s) of training each employee has received; (C) and the means used to verify that the employee understood the training received. (3) Ensure that each contract employee follows the safety and health procedures of the stationary source. (4) Advise the owner or operator of any specific hazards presented by the contract owner or operator's work, or of any hazards found by the contract owner or operator while performing work for the stationary source. | 19 CCR 4.5 2762.12(b)(5); 2762.12(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 235 | Program 4 Prevention Program | Contractors | Complied with contract owner/operator responsibilities | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the contract owner/operator is performing the following responsibilities: (1) Ensure that each contract employee is trained in the work practices necessary to safely perform his or her jobs, including but not limited to: the potential hazards related to their jobs; applicable refinery safety rules; and in the applicable provisions of the stationary source's emergency action plan, and shall meet the requirements of Health and Safety Code Section 25536.7. (2) Documents that each contract employee has successfully completed the training required by section 2762.12 by maintaining a record identifying: (A) each employee who has received training; (B) the date(s) and subject(s) of training each employee has received; (C) and the means used to verify that the employee understood the training received. (3) Ensure that each contract employee follows the safety and health procedures of the stationary source. (4) Advise the owner or operator of any specific hazards presented by the contract owner or operator's work, or of any hazards found by the contract owner or operator while performing work for the stationary source. |  |  | OBSERVATION: Owner/operator failed to ensure that the contract owner/operator complies with the following: ensure each contract employee is trained in the work practices necessary to safely perform his or her jobs, including: the potential hazards related to their jobs; applicable refinery safety rules; and in the applicable provisions of the emergency action plan, and comply with H&SC 25536.7; document and maintain a training record for each contract employee identifying: each employee who has received training; the date(s) and subject(s) of training; and the means used to verify that the employee understood the training received; ensure each contract employee follows the safety and health procedures of the refinery; advise the owner/operator of any specific hazards presented or of any hazards found by the contract owner or operator's work while performing work. CORRECTIVE ACTION: Ensure that each contract owner/operator properly trains employees in the work practices to safely perform his or her job and submit compliance documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010215 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Schedule | Failure to conduct an HCA for all existing processes. Failure to ensure the HCA for existing processes is performed in accordance with the following schedule, and may be performed in conjunction with the PHA schedule: (1) No less than 50% of existing processes within three (3) years of the effective date of Article 6.5; (2) Remaining processes within five (5) years of the effective date of Article 6.5. | 19 CCR 4.5 2762.13(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 236 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Conducted an HCA for all existing processes in accordance with schedule | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to conduct an HCA for all existing processes. Failure to ensure the HCA for existing processes is performed in accordance with the following schedule, and may be performed in conjunction with the PHA schedule: (1) No less than 50% of existing processes within three (3) years of the effective date of Article 6.5; (2) Remaining processes within five (5) years of the effective date of Article 6.5. |  |  | OBSERVATION: Owner/operator failed to conduct an HCA for all existing processes. Owner/operator failed to ensure the HCA for existing processes is performed in accordance with the following schedule, and may be performed in conjunction with the PHA schedule: (1) No less than 50% of existing processes within three (3) years of the effective date of Article 6.5; (2) Remaining processes within five (5) years of the effective date of Article 6.5. CORRECTIVE ACTION: Conduct an HCA for all existing processes. Ensure the HCA for existing process is performed according to the required schedule and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010216 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Instances | Failure to also conduct an HCA in a timely manner in the following instances: (1) For all PHA recommendations for each scenario that identifies the potential for a major incident; (2) Whenever a major change is proposed at a facility, as part of a Management of Change review required by section 2762.6; (3) When a major incident occurs, on the recommendations of the incident investigation report required by section 2762.9; and (4) During the design and review of new processes, new process units, and new facilities, and their related process equipment. An HCA report prepared for this purpose shall be provided to the UPA. | 19 CCR 4.5 2762.13(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 237 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Conducted a timely HCA in specified instances | 47 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to also conduct an HCA in a timely manner in the following instances: (1) For all PHA recommendations for each scenario that identifies the potential for a major incident; (2) Whenever a major change is proposed at a facility, as part of a Management of Change review required by section 2762.6; (3) When a major incident occurs, on the recommendations of the incident investigation report required by section 2762.9; and (4) During the design and review of new processes, new process units, and new facilities, and their related process equipment. An HCA report prepared for this purpose shall be provided to the UPA. |  |  | OBSERVATION: Owner/operator failed to conduct an HCA in a timely manner in the following instances: (1) For all PHA recommendations for each scenario that identifies the potential for a major incident; (2) Whenever a major change is proposed at a facility, as part of a Management of Change review required by section 2762.6; (3) When a major incident occurs, on the recommendations of the incident investigation report required by section 2762.9; and (4) During the design and review of new processes, new process units, and new facilities, and their related process equipment. An HCA report prepared for this purpose shall be provided to the UPA. CORRECTIVE ACTION: Conduct an HCA in the above required instances and submit an HCA report to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010217 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Update | Failure to update all HCAs consistent with the requirements of section 2762.13 at least once every five years, in conjunction with the PHA schedule. | 19 CCR 4.5 2762.13(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 238 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Updated all HCAs | 17 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update all HCAs consistent with the requirements of section 2762.13 at least once every five years, in conjunction with the PHA schedule. |  |  | OBSERVATION: Owner/operator failed to update all HCAs consistent with the requirements of section 2762.13 at least once every five years, in conjunction with the PHA schedule. CORRECTIVE ACTION: Update all HCAs at least once every five years and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010218 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Team Qualifications | Failure to perform, update, and document an HCA by a team with expertise in engineering and process operations and the team shall include at least one operating employee who currently works on the process and has experience and knowledge specific to the process being evaluated. Failure to ensure the team also include one member knowledgeable in the HCA method being used. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure the team consult with individuals with expertise in damage mechanisms, process chemistry, and control systems, as necessary. | 19 CCR 4.5 2762.13(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 239 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Complied with HCA team qualifications and requirements | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform, update, and document an HCA by a team with expertise in engineering and process operations and the team shall include at least one operating employee who currently works on the process and has experience and knowledge specific to the process being evaluated. Failure to ensure the team also include one member knowledgeable in the HCA method being used. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure the team consult with individuals with expertise in damage mechanisms, process chemistry, and control systems, as necessary. |  |  | OBSERVATION: Owner/operator failed to perform, update, and document an HCA by a team with expertise in engineering and process operations and the team shall include at least one operating employee who currently works on the process and has experience and knowledge specific to the process being evaluated. Failure to ensure the team also include one member knowledgeable in the HCA method being used. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure the team consult with individuals with expertise in damage mechanisms, process chemistry, and control systems, as necessary. CORRECTIVE ACTION: Submit documentation to the UPA to demonstrate HCA was performed and updated by a qualified team. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010219 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Requirements | Failure to ensure the HCA team: (1) Include all risk-relevant data for each process or recommendation, including incident investigation reports pursuant to section 2762.9; (2) Identify, characterize and prioritize each process safety hazard. (3) Identify, analyze, and document all inherent safety measures and safeguards (or where appropriate, combinations of measures and safeguards) in an iterative manner to reduce each hazard to the greatest extent feasible. Identify, analyze, and document relevant, publicly available information on inherent safety measures and safeguards. This information shall include inherent safety measures and safeguards that have been: (A) achieved in practice by the petroleum refining industry and related industrial sectors; or, (B) required or recommended for the petroleum refining industry, and related industrial sectors, by a federal or state agency, or local California agency, in a regulation or report. | 19 CCR 4.5 2762.13(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 240 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Ensured HCA team complied with Section 2762.13(e) requirements | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the HCA team: (1) Include all risk-relevant data for each process or recommendation, including incident investigation reports pursuant to section 2762.9; (2) Identify, characterize and prioritize each process safety hazard. (3) Identify, analyze, and document all inherent safety measures and safeguards (or where appropriate, combinations of measures and safeguards) in an iterative manner to reduce each hazard to the greatest extent feasible. Identify, analyze, and document relevant, publicly available information on inherent safety measures and safeguards. This information shall include inherent safety measures and safeguards that have been: (A) achieved in practice by the petroleum refining industry and related industrial sectors; or, (B) required or recommended for the petroleum refining industry, and related industrial sectors, by a federal or state agency, or local California agency, in a regulation or report. |  |  | OBSERVATION: Owner/operator failed to ensure the HCA team: include all risk-relevant data for each process or recommendation, including incident investigation reports; identify, characterize and prioritize each process safety hazard; identify, analyze, and document all inherent safety measures and safeguards in an iterative manner to reduce each hazard to the greatest extent feasible; identify, analyze, and document relevant, publicly available information on inherent safety measures and safeguards; include inherent safety measures and safeguards that have been achieved in practice by the petroleum refining industry and related industrial sectors; or, required or recommended for the petroleum refining industry, and related industrial sectors, by a federal or state agency, or local California agency, in a regulation or report. CORRECTIVE ACTION: Ensure HCA team include above requirements above and submit documentation that demonstrates compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010220 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Recommendations | Failure to ensure the team develop written recommendations to eliminate hazards to the greatest extent feasible using first order inherent safety measures for each process safety hazard identified using the analysis required by subsection 2762.13(e). Failure to ensure the team develop written recommendations to reduce any remaining hazards to the greatest extent feasible using second order inherent safety measures. Failure to ensure the team also develop written recommendations to address any remaining risks in the following sequence and priority order, as necessary: (1) Effectively reduce remaining risks using passive safeguards; (2) Effectively reduce remaining risks using active safeguards; (3) Effectively reduce remaining risks using procedural safeguards. | 19 CCR 4.5 2762.13(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 241 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Ensured HCA team develop written recommendations | 49 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the team develop written recommendations to eliminate hazards to the greatest extent feasible using first order inherent safety measures for each process safety hazard identified using the analysis required by subsection 2762.13(e). Failure to ensure the team develop written recommendations to reduce any remaining hazards to the greatest extent feasible using second order inherent safety measures. Failure to ensure the team also develop written recommendations to address any remaining risks in the following sequence and priority order, as necessary: (1) Effectively reduce remaining risks using passive safeguards; (2) Effectively reduce remaining risks using active safeguards; (3) Effectively reduce remaining risks using procedural safeguards. |  |  | OBSERVATION: Owner/operator failed to ensure the team develop written recommendations to eliminate hazards to the greatest extent feasible using first order inherent safety measures for each process safety hazard identified using the analysis required by subsection 2762.13(e). Failure to ensure the team develop written recommendations to reduce any remaining hazards to the greatest extent feasible using second order inherent safety measures. Failure to ensure the team also develop written recommendations to address any remaining risks in the following sequence and priority order, as necessary: (1) Effectively reduce remaining risks using passive safeguards; (2) Effectively reduce remaining risks using active safeguards; (3) Effectively reduce remaining risks using procedural safeguards. CORRECTIVE ACTION: Ensure HCA team develops written recommendations and submit a copy of the recommendations to UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010221 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Report | Failure to ensure the HCA team complete an HCA report within 90 calendar days following development of the recommendations. Failure to ensure the report includes: (1) A description of the composition, experience, and expertise of the members of the team that performed the HCA; (2) A description of the methodology used by the team; (3) A description of each process safety hazard analyzed by the team, pursuant to subsection 2762.13 (e)(2); (4) A description of the inherent safety measure(s) and safeguards analyzed by the team, pursuant to subsection 2762.13 (e)(3); and (5) The rationale for the inherent safety measures and safeguards recommended by the team for each process safety hazard, pursuant to subsection 2762.13 (f). | 19 CCR 4.5 2762.13(g) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 242 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Ensured HCA team complete an HCA report | 40 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the HCA team complete an HCA report within 90 calendar days following development of the recommendations. Failure to ensure the report includes: (1) A description of the composition, experience, and expertise of the members of the team that performed the HCA; (2) A description of the methodology used by the team; (3) A description of each process safety hazard analyzed by the team, pursuant to subsection 2762.13 (e)(2); (4) A description of the inherent safety measure(s) and safeguards analyzed by the team, pursuant to subsection 2762.13 (e)(3); and (5) The rationale for the inherent safety measures and safeguards recommended by the team for each process safety hazard, pursuant to subsection 2762.13 (f). |  |  | OBSERVATION: Owner/operator failed to: ensure the HCA team complete an HCA report within 90 calendar days following development of the recommendations; ensure the report includes: (1) A description of the composition, experience, and expertise of the members of the team that performed the HCA; (2) A description of the methodology used by the team; (3) A description of each process safety hazard analyzed by the team, pursuant to subsection 2762.13 (e)(2); (4) A description of the inherent safety measure(s) and safeguards analyzed by the team, pursuant to subsection 2762.13 (e)(3); and (5) The rationale for the inherent safety measures and safeguards recommended by the team for each process safety hazard, pursuant to subsection 2762.13 (f). CORRECTIVE ACTION: Ensure the HCA team complete an HCA report within 90 calendar days following development of the recommendations and includes the above requirements. Submit a copy of the HCA report to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010222 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Corrective Action Work Process | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the HCA team's finding and recommendations determining corrective action for implementation, tracking to completion, and documentation of closeout. | 19 CCR 4.5 2762.13(h) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 243 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Followed corrective action work process when resolving HCA team's finding(s) | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the HCA team's finding and recommendations determining corrective action for implementation, tracking to completion, and documentation of closeout. |  |  | OBSERVATION: Owner/operator failed to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the HCA team's finding and recommendations determining corrective action for implementation, tracking to completion, and documentation of closeout. CORRECTIVE ACTION: Follow the corrective action work process for HCA team's resolution of recommendations and submit documentation to demonstrate compliance to the UPA . | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010223 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Retention | Failure to retain all HCA reports for the life of each process. | 19 CCR 4.5 2762.13(i) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 244 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Retained all HCA reports for the life of each process | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain all HCA reports for the life of each process. |  |  | OBSERVATION: Owner/operator failed to retain all HCA reports for the life of each process. CORRECTIVE ACTION: Retain all HCA reports and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010224 |  |  | Program level 4: Process Safety Culture Assessment - Program | Failure to develop, implement and maintain an effective Process Safety Culture Assessment (PSCA) program. | 19 CCR 4.5 2762.14(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 245 | Program 4 Prevention Program | Process Safety Culture Assessment | Developed, implemented, and maintained an effective PSCA program | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement and maintain an effective Process Safety Culture Assessment (PSCA) program. |  |  | OBSERVATION: Owner/operator failed to develop, implement and maintain an effective Process Safety Culture Assessment (PSCA) program. CORRECTIVE ACTION: Develop, implement, and maintain an effective PSCA program. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010225 |  |  | Program level 4: Process Safety Culture Assessment - Report and Action Plan | Failure to conduct an effective PSCA and produce a written report and action plan within eighteen (18) months following the effective date of Article 6.5 and at least once, every five (5) years thereafter. Failure to include an evaluation of the effectiveness of: (1) The owner or operator's hazard reporting program; (2) The owner or operator's response to reports of hazards; (3) The owner or operator's procedures to ensure that incentive programs do not discourage reporting of hazards; (4) The owner or operator's procedures to ensure that process safety is prioritized during upset or emergency conditions; and (5) Management commitment and leadership. | 19 CCR 4.5 2762.14(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 246 | Program 4 Prevention Program | Process Safety Culture Assessment | Conducted an effective PSCA and produced a written report and action plan | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to conduct an effective PSCA and produce a written report and action plan within eighteen (18) months following the effective date of Article 6.5 and at least once, every five (5) years thereafter. Failure to include an evaluation of the effectiveness of: (1) The owner or operator's hazard reporting program; (2) The owner or operator's response to reports of hazards; (3) The owner or operator's procedures to ensure that incentive programs do not discourage reporting of hazards; (4) The owner or operator's procedures to ensure that process safety is prioritized during upset or emergency conditions; and (5) Management commitment and leadership. |  |  | OBSERVATION: Owner/operator failed to: conduct an effective PSCA and produce a written report and action plan within eighteen (18) months following the effective date of Article 6.5 and at least once, every five (5) years thereafter; failed to include an evaluation of the effectiveness of the following elements of process safety leadership: 1) The owner or operator's hazard reporting program; (2) The owner or operator's response to reports of hazards; (3) The owner or operator's procedures to ensure that incentive programs do not discourage reporting of hazards; (4) The owner or operator's procedures to ensure that process safety is prioritized during upset or emergency conditions; and (5) Management commitment and leadership. CORRECTIVE ACTION: Conduct an effective PSCA and submit a written report and action plan to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010226 |  |  | Program level 4: Process Safety Culture Assessment - Team Qualifications | Failure to ensure the PSCA is conducted or overseen by a team that includes at least one person knowledgeable in refinery operations and at least one employee representative. Failure to provide for employee participation in the development and implementation of the PSCA, report, and recommendations, pursuant to section 2762.10. Failure to ensure the team consult with at least one employee or another individual with expertise in assessing process safety culture in the petroleum refining industry. | 19 CCR 4.5 2762.14(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 247 | Program 4 Prevention Program | Process Safety Culture Assessment | Ensured the PSCA team complied with qualifications and requirements | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PSCA is conducted or overseen by a team that includes at least one person knowledgeable in refinery operations and at least one employee representative. Failure to provide for employee participation in the development and implementation of the PSCA, report, and recommendations, pursuant to section 2762.10. Failure to ensure the team consult with at least one employee or another individual with expertise in assessing process safety culture in the petroleum refining industry. |  |  | OBSERVATION: Owner/operator failed to: ensure the PSCA is conducted or overseen by a team that includes at least one person knowledgeable in refinery operations and at least one employee representative; provide for employee participation in the development and implementation of the PSCA, report, and recommendations, pursuant to section 2762.10; ensure the team consult with at least one employee or another individual with expertise in assessing process safety culture in the petroleum refining industry. CORRECTIVE ACTION: Ensure the PSCA team meets the above requirements and provide documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010227 |  |  | Program level 4: Process Safety Culture Assessment - Report Schedule and Content | Failure to ensure the PSCA team develop a written report within 90 calendar days of completion of the assessment. Failure to ensure the report includes: (1) The method(s) used to assess the process safety culture; (2) The conclusions of the process safety culture assessment; (3) The rationale for the conclusions; and (4) The recommendations to address the findings from the PSCA. | 19 CCR 4.5 2762.14(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 248 | Program 4 Prevention Program | Process Safety Culture Assessment | Ensured the PSCA team develop a written report and included requirements | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PSCA team develop a written report within 90 calendar days of completion of the assessment. Failure to ensure the report includes: (1) The method(s) used to assess the process safety culture; (2) The conclusions of the process safety culture assessment; (3) The rationale for the conclusions; and (4) The recommendations to address the findings from the PSCA. |  |  | OBSERVATION: Owner/operator failed to: ensure the PSCA team develop a written report within 90 calendar days of completion of the assessment; ensure the report includes: (1) The method(s) used to assess the process safety culture; (2) The conclusions of the process safety culture assessment; (3) The rationale for the conclusions; and (4) The recommendations to address the findings from the PSCA. CORRECTIVE ACTION: Ensure the PSCA team develop a written report that meets the above requirements and submit a copy of the report to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010228 |  |  | Program level 4: Process Safety Culture Assessment - Corrective Actions | Failure to develop corrective actions based on the PSCA team recommendations and implement the corrective actions within twenty-four (24) months of the completion of the report. | 19 CCR 4.5 2762.14(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 249 | Program 4 Prevention Program | Process Safety Culture Assessment | Developed and implemented PSCA corrective actions | 51 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop corrective actions based on the PSCA team recommendations and implement the corrective actions within twenty-four (24) months of the completion of the report. |  |  | OBSERVATION: Owner/operator failed to develop corrective actions based on the PSCA team recommendations and implement the corrective actions within twenty-four (24) months of the completion of the report. CORRECTIVE ACTION: Develop and implement the corrective actions based on the PSCA team recommendations within (24) months of the completion of the report and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010229 |  |  | Program level 4: Process Safety Culture Assessment - Corrective Action Assessment | Failure to ensure the PSCA team conduct a written interim assessment of the implementation and effectiveness of each PSCA corrective action within three (3) years following the completion of the PSCA report. For a corrective action found to be ineffective, failed to implement changes necessary to ensure effectiveness in a timely manner not to exceed six months. | 19 CCR 4.5 2762.14(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 250 | Program 4 Prevention Program | Process Safety Culture Assessment | Ensured the PSCA team conducted a written corrective action assessment | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PSCA team conduct a written interim assessment of the implementation and effectiveness of each PSCA corrective action within three (3) years following the completion of the PSCA report. For a corrective action found to be ineffective, failed to implement changes necessary to ensure effectiveness in a timely manner not to exceed six months. |  |  | OBSERVATION: Owner/operator failed to ensure the PSCA team conduct a written interim assessment of the implementation and effectiveness of each PSCA corrective action within three (3) years following the completion of the PSCA report. For a corrective action found to be ineffective, failed to implement changes necessary to ensure effectiveness in a timely manner not to exceed six months. CORRECTIVE ACTION: Ensure the PSCA team conduct a written interim assessment of the implementation and effectiveness of each PSCA corrective action within three (3) years following the completion of the PSCA report. For a corrective action found to be ineffective, implement changes necessary to ensure effectiveness in a timely manner not to exceed six months, and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010230 |  |  | Program level 4: Process Safety Culture Assessment - Certification | Failure to ensure the stationary source manager or his or her designee serve as signatory to all process safety culture assessment reports and corrective action plans. | 19 CCR 4.5 2762.14(g) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 251 | Program 4 Prevention Program | Process Safety Culture Assessment | Ensured the refinery manager certifies all PSCA reports and corrective actions | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the stationary source manager or his or her designee serve as signatory to all process safety culture assessment reports and corrective action plans. |  |  | OBSERVATION: Owner/operator failed to ensure the stationary source manager or his or her designee serve as signatory to all process safety culture assessment reports and corrective action plans. CORRECTIVE ACTION: Ensure the stationary source manager or his or her designee serve as signatory to all process safety culture assessment reports and corrective action plans and provide signed copies of the documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010231 |  |  | Program level 4: Process Safety Culture Assessment - Employee Communication | Failure to ensure the PSCA report and action plan and the three year interim assessment are communicated and made available to employees, their representatives and participating contractors within 60 calendar days of the completion of the report. | 19 CCR 4.5 2762.14(h) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 252 | Program 4 Prevention Program | Process Safety Culture Assessment | Ensured the PSCA report, action plan and interim assessment are communicated and made available | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PSCA report and action plan and the three year interim assessment are communicated and made available to employees, their representatives and participating contractors within 60 calendar days of the completion of the report. |  |  | OBSERVATION: Owner/operator failed to ensure the PSCA report and action plan and the three year interim assessment are communicated and made available to employees, their representatives and participating contractors within 60 calendar days of the completion of the report. CORRECTIVE ACTION: Ensure the PSCA report and action plan and the three year interim assessment are communicated and made available to employees, their representatives and participating contractors within 60 calendar days of the completion of the report. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010232 |  |  | Program level 4: Human Factors Program - Plan | Failure to develop, implement and maintain an effective written Human Factors Program within eighteen (18) months of the effective date of Article 6.5. | 19 CCR 4.5 2762.15(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 253 | Program 4 Prevention Program | Human Factors Program | Developed, implemented, and maintained an effective written Human Factors Program | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement and maintain an effective written Human Factors Program within eighteen (18) months of the effective date of Article 6.5. |  |  | OBSERVATION: Owner/operator failed to develop, implement and maintain an effective written Human Factors Program within eighteen (18) months of the effective date of Article 6.5. CORRECTIVE ACTION: Develop, implement and maintain an effective written Human Factors Program and provide documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010233 |  |  | Program level 4: Human Factors Program - Analysis | Failure to include a written analysis of human factors where relevant in the design phase of a major change, incident investigations, PHAs, MOOCs, and HCAs. Failure to ensure the analysis includes a description of selected methodologies and criteria for their use. | 19 CCR 4.5 2762.15(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 254 | Program 4 Prevention Program | Human Factors Program | Included a written human factors analysis | 42 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to include a written analysis of human factors where relevant in the design phase of a major change, incident investigations, PHAs, MOOCs, and HCAs. Failure to ensure the analysis includes a description of selected methodologies and criteria for their use. |  |  | OBSERVATION: Owner/operator failed to include a written analysis of human factors where relevant in the design phase of a major change, incident investigations, PHAs, MOOCs, and HCAs; failed to ensure the analysis includes a description of selected methodologies and criteria for their use. CORRECTIVE ACTION: Include a written analysis of human factors where relevant in the design phase of a major change, incident investigations, PHAs, MOOCs, and HCAs; Ensure the analysis includes a description of selected methodologies and criteria for their use. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010234 |  |  | Program level 4: Human Factors Program - Evaluation Method and Criteria | Failure to ensure the human factors analysis use an effective method of evaluating the following: staffing levels; the complexity of tasks; the length of time needed to complete tasks; the level of training, experience, and competency of employees; the human-machine and human-system interface; the physical challenges of the work environment in which the task is performed; employee fatigue, including contractor employees and other effects of shiftwork and overtime; communication systems; and the understandability and clarity of operating and maintenance procedures. Failure to ensure the human factors analysis of process controls includes the following areas: (1) Error proof mechanisms; (2) Automatic Alerts; and (3) Automatic System Shutdowns. | 19 CCR 4.5 2762.15(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 255 | Program 4 Prevention Program | Human Factors Program | Ensured the human factors analysis use an effective evaluation method | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the human factors analysis use an effective method of evaluating the following: staffing levels; the complexity of tasks; the length of time needed to complete tasks; the level of training, experience, and competency of employees; the human-machine and human-system interface; the physical challenges of the work environment in which the task is performed; employee fatigue, including contractor employees and other effects of shiftwork and overtime; communication systems; and the understandability and clarity of operating and maintenance procedures. Failure to ensure the human factors analysis of process controls includes the following areas: (1) Error proof mechanisms; (2) Automatic Alerts; and (3) Automatic System Shutdowns. |  |  | OBSERVATION: Owner/operator failed to ensure the human factors analysis use an effective method of evaluating the following: staffing levels; the complexity of tasks; the length of time needed to complete tasks; the level of training, experience, and competency of employees; the human-machine and human-system interface; the physical challenges of the work environment in which the task is performed; employee fatigue, including contractor employees and other effects of shiftwork and overtime; communication systems; and the understandability and clarity of operating and maintenance procedures. Failure to ensure the human factors analysis of process controls includes the following areas: (1) Error proof mechanisms; (2) Automatic Alerts; and (3) Automatic System Shutdowns. CORRECTIVE ACTION: Ensure the human factors analysis complies with the above requirements and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010235 |  |  | Program level 4: Human Factors Program - New and Revised O & M Procedures | Failure to include an analysis of human factors in new and revised operating and maintenance procedures. | 19 CCR 4.5 2762.15(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 256 | Program 4 Prevention Program | Human Factors Program | Included a human factors analysis in new and revised operating and maintenance procedures | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to include an analysis of human factors in new and revised operating and maintenance procedures. |  |  | OBSERVATION: Owner/operator failed to include an analysis of human factors in new and revised operating and maintenance procedures. CORRECTIVE ACTION: Include a human factors analysis in new and revised operating and maintenance procedures and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010236 |  |  | Program level 4: Human Factors Program - Existing O & M Procedures Schedule | Failure to develop a schedule for revising existing operating and maintenance procedures based on a human factors analysis. Failure to complete no less than fifty (50) percent of assessments and revisions within three (3) years following the effective date of Article 6.5 and one hundred (100) percent within five (5) years. | 19 CCR 4.5 2762.15(e) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 257 | Program 4 Prevention Program | Human Factors Program | Developed a schedule for revising existing operating and maintenance procedures based on a HFA | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop a schedule for revising existing operating and maintenance procedures based on a human factors analysis. Failure to complete no less than fifty (50) percent of assessments and revisions within three (3) years following the effective date of Article 6.5 and one hundred (100) percent within five (5) years. |  |  | OBSERVATION: Owner/operator failed to develop a schedule for revising existing operating and maintenance procedures based on a human factors analysis; failed to complete no less than fifty (50) percent of assessments and revisions within three (3) years following the effective date of Article 6.5 and one hundred (100) percent within five (5) years. CORRECTIVE ACTION: Develop a schedule for revising existing operating and maintenance procedures based on a human factors analysis; complete no less than fifty (50) percent of assessments and revisions within three (3) years following the effective date of Article 6.5 and one hundred (100) percent within five (5) years. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010237 |  |  | Program level 4: Human Factors Program - Training | Failure to train all of their employees that have process and process equipment responsibilities on the Human Factors Program. | 19 CCR 4.5 2762.15(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 258 | Program 4 Prevention Program | Human Factors Program | Trained employees with process and process equipment responsibilities on the Human Factors Program | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to train all of their employees that have process and process equipment responsibilities on the Human Factors Program. |  |  | OBSERVATION: Owner/operator failed to train all of their employees that have process and process equipment responsibilities on the Human Factors Program. CORRECTIVE ACTION: Train all employees that have process and process equipment responsibilities on the Human Factors Program and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010238 |  |  | Program level 4: Human Factors Program - Employee Participation | Failure to provide for employee participation in the development and implementation of the Human Factors Program, pursuant to section 2762.10. | 19 CCR 4.5 2762.15(g) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 259 | Program 4 Prevention Program | Human Factors Program | Provided for employee participation in development and implementation of the Human Factors Program | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide for employee participation in the development and implementation of the Human Factors Program, pursuant to section 2762.10. |  |  | OBSERVATION: Owner/operator failed to provide for employee participation in the development and implementation of the Human Factors Program, pursuant to section 2762.10. CORRECTIVE ACTION: Provide for employee participation in the development and implementation of the Human Factors Program, pursuant to section 2762.10 and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010239 |  |  | Program level 4: Human Factors Program - Availability | Failure to make available and provide on request a copy of the written Human Factors Program to employees and their representatives, and to affected contractors, contractor employees, and contractor representatives. | 19 CCR 4.5 2762.15(h) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 260 | Program 4 Prevention Program | Human Factors Program | Provided a copy of the written Human factors Program to employees and contractors | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to make available and provide on request a copy of the written Human Factors Program to employees and their representatives, and to affected contractors, contractor employees, and contractor representatives. |  |  | OBSERVATION: Owner/operator failed to make available and provide on request a copy of the written Human Factors Program to employees and their representatives, and to affected contractors, contractor employees, and contractor representatives. CORRECTIVE ACTION: Make available and provide on request a copy of the written Human Factors Program to employees and their representatives, and to affected contractors, contractor employees, and contractor representatives. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010240 |  |  | Program level 4: Accidental Release Prevention Program Management System - Plan | Failure to develop and implement an effective written Accidental Release Prevention Program (ARP) Management System. Failure to review and update the ARP Management System every three (3) years. Failure to designate the stationary source manager as the person with authority and responsibility for compliance with section 2762.16, and maintain process safety goals that support continuous improvement. | 19 CCR 4.5 2762.16(a) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 261 | Program 4 Prevention Program | Management System | Developed and implemented an effective ARP Management System. | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement an effective written Accidental Release Prevention Program (ARP) Management System. Failure to review and update the ARP Management System every three (3) years. Failure to designate the stationary source manager as the person with authority and responsibility for compliance with section 2762.16, and maintain process safety goals that support continuous improvement. |  |  | OBSERVATION: Owner/operator failed to develop and implement an effective written Accidental Release Prevention Program (ARP) Management System. Failure to review and update the ARP Management System every three (3) years; failed to designate the stationary source manager as the person with authority and responsibility for compliance with section 2762.16, and maintain process safety goals that support continuous improvement. CORRECTIVE ACTION: Develop and implement an effective written Accidental Release Prevention Program (ARP) Management System. Review and update the ARP Management System every three (3) years. Designate the stationary source manager as the person with authority and responsibility for compliance with section 2762.16, and maintain process safety goals that support continuous improvement. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010241 |  |  | Program level 4: Accidental Release Prevention Program Management System - Policies and Procedures | Failure to develop and maintain written ARP policies and procedures, as part of the ARP Management System, as described below: (1) Job descriptions of roles and responsibilities under each section of Article 6.5; (2) An organizational chart of management positions with responsibilities for each section of Article 6.5; (3) Written procedures for ensuring the effective communication of safety, operations, and maintenance information among and across process and maintenance personnel, contractors, support personnel, supervisors and senior management; (4) Policies and procedures to ensure that the findings, recommendations and corrective action of all sections in Article 6.5 and the ARP Management System are communicated effectively to employees and employee representatives; and (5) Policies and procedures to effectively provide for employee participation in all applicable sections in Article 6.5 as specified in section 2762.10. | 19 CCR 4.5 2762.16(b) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 262 | Program 4 Prevention Program | Management System | Developed and maintained written ARP policies and procedures as part of the ARP Management System | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and maintain written ARP policies and procedures, as part of the ARP Management System, as described below: (1) Job descriptions of roles and responsibilities under each section of Article 6.5; (2) An organizational chart of management positions with responsibilities for each section of Article 6.5; (3) Written procedures for ensuring the effective communication of safety, operations, and maintenance information among and across process and maintenance personnel, contractors, support personnel, supervisors and senior management; (4) Policies and procedures to ensure that the findings, recommendations and corrective action of all sections in Article 6.5 and the ARP Management System are communicated effectively to employees and employee representatives; and (5) Policies and procedures to effectively provide for employee participation in all applicable sections in Article 6.5 as specified in section 2762.10. |  |  | OBSERVATION: Owner/operator failed to develop and maintain written ARP policies and procedures, as part of the ARP Management System, as follows: (1) Job descriptions of roles and responsibilities; (2) An organizational chart of management positions with responsibilities; (3) Written procedures for ensuring the effective communication of safety, operations, and maintenance information among and across process and maintenance personnel, contractors, support personnel, supervisors and senior management; (4) Policies and procedures to ensure that the findings, recommendations and corrective action of all sections in Article 6.5 and the ARP Management System are communicated effectively to employees and employee representatives; and (5) Policies and procedures to effectively provide for employee participation. CORRECTIVE ACTION: Develop and maintain written policies and procedures and submit documentation to demonstrate compliance with the above requirements to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010242 |  |  | Program level 4: Accidental Release Prevention Program Management System - Tracking Changes | Failure to track and document all changes to program elements under Article 6.5, as part of the ARP Management System. | 19 CCR 4.5 2762.16(c) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 263 | Program 4 Prevention Program | Management System | Tracked and documented all changes to program elements as part of the ARP Management System | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to track and document all changes to program elements under Article 6.5, as part of the ARP Management System. |  |  | OBSERVATION: Owner/operator failed to track and document all changes to program elements under Article 6.5, as part of the ARP Management System. CORRECTIVE ACTION: Track and document all changes to program elements and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010243 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Work Process | Failure to develop and document a corrective action work process to address findings and recommendations resulting from program elements. Failure to ensure the corrective action work plan for PSCAs is governed by section 2762.14. Failure to ensure the corrective action work process includes the requirements in subsection 2762.16 (e). | 19 CCR 4.5 2762.16(d) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 264 | Program 4 Prevention Program | Management System | Developed and documented a corrective action work process to address recommendations | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and document a corrective action work process to address findings and recommendations resulting from program elements. Failure to ensure the corrective action work plan for PSCAs is governed by section 2762.14. Failure to ensure the corrective action work process includes the requirements in subsection 2762.16 (e). |  |  | OBSERVATION: Owner/operator failed to develop and document a corrective action work process to address findings and recommendations resulting from program elements. Failure to ensure the corrective action work plan for PSCAs is governed by section 2762.14. Failure to ensure the corrective action work process includes the requirements in subsection 2762.16 (e). CORRECTIVE ACTION: Submit documentation to demonstrate compliance with the above requirements to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010244 |  |  | Program level 4: Accidental Release Prevention Program Management System - Recommendations Standards | Failure to comply with the following standards for findings and recommendations for the PHA, DMR, HCA, Incident Investigation, Compliance Audit and SPA: (1) All findings and recommendations must be provided by the team to the owner or operator at the earliest opportunity, but no later than 14 calendar days after recommendation and findings are complete. (2) The owner or operator may reject a team recommendation if the owner or operator can demonstrate in writing that one of the following applies: (A) The analysis upon which the recommendation is based contains material factual errors; (B) The recommendation is not relevant to process safety; or (C) The recommendation is infeasible; however, a determination of infeasibility shall not be based solely on cost. (3) The owner or operator may change a team recommendation if the owner or operator can demonstrate in writing that an alternative inherent safety measure would provide an equivalent or higher order of inherent safety, or, for a safeguard recommendation, an alternative safeguard would provide an equally or more effective level of protection. | 19 CCR 4.5 2762.16(e)(1), 2762.16(e)(2), 2762.16(e)(3) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 265 | Program 4 Prevention Program | Management System | Complied with standards for PHA, DMR, HCA, Incident Investigation, Audit, and SPA recommendations | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to comply with the following standards for findings and recommendations for the PHA, DMR, HCA, Incident Investigation, Compliance Audit and SPA: (1) All findings and recommendations must be provided by the team to the owner or operator at the earliest opportunity, but no later than 14 calendar days after recommendation and findings are complete. (2) The owner or operator may reject a team recommendation if the owner or operator can demonstrate in writing that one of the following applies: (A) The analysis upon which the recommendation is based contains material factual errors; (B) The recommendation is not relevant to process safety; or (C) The recommendation is infeasible; however, a determination of infeasibility shall not be based solely on cost. (3) The owner or operator may change a team recommendation if the owner or operator can demonstrate in writing that an alternative inherent safety measure would provide an equivalent or higher order of inherent safety, or, for a safeguard recommendation, an alternative safeguard would provide an equally or more effective level of protection. |  |  | OBSERVATION: Owner/operator (o/o) failed to comply with the following standards for recommendations for the PHA, DMR, HCA, Incident Investigation, Compliance Audit and SPA: All recommendations must be provided by the team to the o/o no later than 14 calendar days after completion; o/o may reject a team recommendation if the o/o can demonstrate in writing one of the following: analysis for the recommendation contains material factual errors; the recommendation is not relevant to process safety; or the recommendation is infeasible; however, infeasibility shall not be based solely on cost. The o/o may change a team recommendation if the o/o can demonstrate in writing that an alternative inherent safety measure would provide an equivalent or higher order of inherent safety, or, for a safeguard recommendation, an alternative safeguard would provide an equally or more effective level of protection. CORRECTIVE ACTION: Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010245 |  |  | Program level 4: Accidental Release Prevention Program Management System - Recommendation Change or Rejection | Failure to document where any of the conditions in subsection 2762.16 (e)(2) or (e)(3) is applied for the purpose of changing or rejecting a team recommendation. Failure to ensure that each recommendation that is changed or rejected by the owner or operator is communicated to onsite team members for comment and made available to offsite team members for comment. | 19 CCR 4.5 2762.16(e)(4) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 266 | Program 4 Prevention Program | Management System | Documented applied conditions for changing or rejecting a team recommendation | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document where any of the conditions in subsection 2762.16 (e)(2) or (e)(3) is applied for the purpose of changing or rejecting a team recommendation. Failure to ensure that each recommendation that is changed or rejected by the owner or operator is communicated to onsite team members for comment and made available to offsite team members for comment. |  |  | OBSERVATION: Owner/operator failed to document where any of the conditions in subsection 2762.16 (e)(2) or (e)(3) is applied for the purpose of changing or rejecting a team recommendation; failed to ensure that each recommendation that is changed or rejected by the owner or operator is communicated to onsite team members for comment and made available to offsite team members for comment. CORRECTIVE ACTION: Document where any of the conditions in subsection 2762.16 (e)(2) or (e)(3) is applied for changing or rejecting a team recommendation; ensure that each recommendation that is changed or rejected is communicated to onsite team members for comment and made available to offsite team members for comment. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010246 |  |  | Program level 4: Accidental Release Prevention Program Management System - Recommendation Comment Documentation | Failure to document any written comments from all team members on any rejected or changed findings and recommendations. | 19 CCR 4.5 2762.16(e)(5) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 267 | Program 4 Prevention Program | Management System | Documented written comments from all team members on rejected or changed recommendations | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document any written comments from all team members on any rejected or changed findings and recommendations. |  |  | OBSERVATION: Owner/operator failed to document any written comments from all team members on any rejected or changed findings and recommendations. CORRECTIVE ACTION: Document any written comments from all team members on any rejected or changed findings and recommendations and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010247 |  |  | Program level 4: Accidental Release Prevention Program Management System - Recommendation Documentation/ Communication | Failure to document a final decision for each recommendation and communicate it to onsite team members and make it available to offsite team members. | 19 CCR 4.5 2762.16(e)(6) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 268 | Program 4 Prevention Program | Management System | Documented decision for each recommendation and communicated it to team members | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document a final decision for each recommendation and communicate it to onsite team members and make it available to offsite team members. |  |  | OBSERVATION: Owner/operator failed to document a final decision for each recommendation and communicate it to onsite team members and make it available to offsite team members. CORRECTIVE ACTION: Document a final decision for each recommendation and communicate it to onsite team members and make it available to offsite team members. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010248 |  |  | Program level 4: Accidental Release Prevention Program Management System - Recommendation Target Dates | Failure to develop and document corrective actions to implement each accepted recommendation, including documentation of a completion date and assignment of responsibility for completion of each corrective action. Failure to ensure all target dates are consistent with the requirements of subsections 2762.16(e)(10) through (13) for completion of corrective actions. | 19 CCR 4.5 2762.16(e)(7) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 269 | Program 4 Prevention Program | Management System | Developed and documented corrective actions to implement each accepted recommendation | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and document corrective actions to implement each accepted recommendation, including documentation of a completion date and assignment of responsibility for completion of each corrective action. Failure to ensure all target dates are consistent with the requirements of subsections 2762.16(e)(10) through (13) for completion of corrective actions. |  |  | OBSERVATION: Owner/operator failed to: develop and document corrective actions to implement each accepted recommendation, including documentation of a completion date and assignment of responsibility for completion of each corrective action; ensure all target dates are consistent with the requirements of subsections 2762.16(e)(10) through (13) for completion of corrective actions. CORRECTIVE ACTION: Develop and document corrective actions to implement each accepted recommendation, including documentation of a completion date and assignment of responsibility for completion of each corrective action; ensure all target dates are consistent with the requirements of subsections 2762.16(e)(10) through (13) for completion of corrective actions. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010249 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Update | Failure to ensure that a corrective action requiring revalidation or update of any applicable PHA, HCA, DMR, or SPA is subject to the corrective action requirements in subsections 2762.16 (9) and (11) through (12). Failure to promptly append any revalidated or updated PHA, DMR, HCA, or SPA, to the applicable report. | 19 CCR 4.5 2762.16(e)(8) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 270 | Program 4 Prevention Program | Management System | Ensured a corrective action requiring revalidation is promptly appended to the applicable report | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that a corrective action requiring revalidation or update of any applicable PHA, HCA, DMR, or SPA is subject to the corrective action requirements in subsections 2762.16 (9) and (11) through (12). Failure to promptly append any revalidated or updated PHA, DMR, HCA, or SPA, to the applicable report. |  |  | OBSERVATION: Owner/operator failed to ensure that a corrective action requiring revalidation or update of any applicable PHA, HCA, DMR, or SPA is subject to the corrective action requirements in subsections 2762.16 (9) and (11) through (12). Failure to promptly append any revalidated or updated PHA, DMR, HCA, or SPA, to the applicable report. CORRECTIVE ACTION: Ensure that a corrective action requiring revalidation or update of any applicable PHA, HCA, DMR, or SPA is subject to the corrective action requirements in subsections 2762.16 (9) and (11) through (12). Promptly append any revalidated or updated PHA, DMR, HCA, or SPA, to the applicable report. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010250 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Completion Dates | Failure to promptly complete all corrective actions and comply with the completion dates required by subsection 2762.16 (e). Failure to conduct a MOC pursuant to section 2762.6 for any proposed change to a completion date. Failure to make all completion dates available, upon request, to all affected operation and maintenance employees and employee representatives. | 19 CCR 4.5 2762.16(e)(9) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 271 | Program 4 Prevention Program | Management System | Completed all corrective actions and completion dates. Conducted MOC for completion date change. | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to promptly complete all corrective actions and comply with the completion dates required by subsection 2762.16 (e). Failure to conduct a MOC pursuant to section 2762.6 for any proposed change to a completion date. Failure to make all completion dates available, upon request, to all affected operation and maintenance employees and employee representatives. |  |  | OBSERVATION: Owner/operator failed to: promptly complete all corrective actions and comply with the completion dates required by subsection 2762.16 (e); conduct a MOC pursuant to section 2762.6 for any proposed change to a completion date; make all completion dates available, upon request, to all affected operation and maintenance employees and employee representatives. CORRECTIVE ACTION: Promptly complete all corrective actions as required above and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010251 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Prioritization | Failure to prioritize and promptly complete corrective actions addressing process safety hazards, either through permanent corrections or interim safeguards sufficient to prevent the potential for a major incident, pending permanent corrections. | 19 CCR 4.5 2762.16(e)(10) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 272 | Program 4 Prevention Program | Management System | Prioritized and promptly completed corrective actions addressing process safety hazards | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prioritize and promptly complete corrective actions addressing process safety hazards, either through permanent corrections or interim safeguards sufficient to prevent the potential for a major incident, pending permanent corrections. |  |  | OBSERVATION: Owner/operator failed to prioritize and promptly complete corrective actions addressing process safety hazards, either through permanent corrections or interim safeguards sufficient to prevent the potential for a major incident, pending permanent corrections. CORRECTIVE ACTION: Prioritize and promptly complete corrective actions as required above and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010252 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Not Requiring Process Shutdown | Failure to ensure each corrective action except as specified under subsection 2762.16 (10) that does not require a process shutdown is completed within two and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. | 19 CCR 4.5 2762.16(e)(11) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 273 | Program 4 Prevention Program | Management System | Completed each corrective action not requiring process shutdown within two and half years | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure each corrective action except as specified under subsection 2762.16 (10) that does not require a process shutdown is completed within two and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. |  |  | OBSERVATION: Owner/operator failed to ensure each corrective action except as specified under subsection 2762.16 (10) that does not require a process shutdown is completed within two and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. CORRECTIVE ACTION: Ensure each corrective action except as specified under subsection 2762.16 (10) that does not require a process shutdown is completed within two and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010253 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action from Compliance Audit | Failure to ensure each corrective action from a compliance audit is completed within one and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. | 19 CCR 4.5 2762.16(e)(12) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 274 | Program 4 Prevention Program | Management System | Completed each compliance audit corrective action within one and half years | 76 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure each corrective action from a compliance audit is completed within one and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. |  |  | OBSERVATION: Owner/operator failed to ensure each corrective action from a compliance audit is completed within one and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. Failure to ensure each corrective action from an incident investigation is completed within one and half years after completion of the investigation unless the owner or operator demonstrates in writing that it is infeasible to do so. CORRECTIVE ACTION: Ensure each corrective action from a compliance audit and incident investigation is completed within one and half years unless the owner or operator demonstrates in writing that it is infeasible. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010254 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Requiring Process Shutdown | Failure to ensure each corrective action requiring a process shutdown is completed during the first regularly scheduled turnaround of the applicable process, subsequent to completion of the PHA, SPA, DMR, HCA, MOC, compliance audit or incident investigation, unless the owner or operator demonstrates in writing it is not feasible to do so. | 19 CCR 4.5 2762.16(e)(13) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 275 | Program 4 Prevention Program | Management System | Completed each corrective action requiring process shutdown during the first scheduled turnaround | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure each corrective action requiring a process shutdown is completed during the first regularly scheduled turnaround of the applicable process, subsequent to completion of the PHA, SPA, DMR, HCA, MOC, compliance audit or incident investigation, unless the owner or operator demonstrates in writing it is not feasible to do so. |  |  | OBSERVATION: Owner/operator failed to ensure each corrective action requiring a process shutdown is completed during the first regularly scheduled turnaround of the applicable process, subsequent to completion of the PHA, SPA, DMR, HCA, MOC, compliance audit or incident investigation, unless the owner or operator demonstrates in writing it is not feasible to do so. CORRECTIVE ACTION: Ensure each corrective action requiring a process shutdown is completed during the first regularly scheduled turnaround of the applicable process, subsequent to completion of the PHA, SPA, DMR, HCA, MOC, compliance audit or incident investigation, unless the owner or operator demonstrates in writing it is not feasible to do so. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010255 |  |  | Program level 4: Accidental Release Prevention Program Management System - Interim Safeguards | Failure to ensure that interim safeguards are sufficient to prevent the potential for a major incident, pending permanent corrections, where a corrective action cannot be implemented within the times described in 2762.16(e)(10) through (13). Failure to document all corrective actions delayed beyond the timelines established in subsection 2762.16 (e). The documentation shall include: (A) The rationale for deferring the corrective action(s); (B) The documentation required under the MOC process; (C) A timeline describing when the corrective action(s) will be implemented; and (D) An effective plan to make available the rationale and revised timeline to all affected employees and their representatives. | 19 CCR 4.5 2762.16(e)(14) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 276 | Program 4 Prevention Program | Management System | Ensured interim safeguards are sufficient to prevent a major incident | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that interim safeguards are sufficient to prevent the potential for a major incident, pending permanent corrections, where a corrective action cannot be implemented within the times described in 2762.16(e)(10) through (13). Failure to document all corrective actions delayed beyond the timelines established in subsection 2762.16 (e). The documentation shall include: (A) The rationale for deferring the corrective action(s); (B) The documentation required under the MOC process; (C) A timeline describing when the corrective action(s) will be implemented; and (D) An effective plan to make available the rationale and revised timeline to all affected employees and their representatives. |  |  | OBSERVATION: Owner/operator failed to: ensure that interim safeguards are sufficient to prevent the potential for a major incident, pending permanent corrections, where a corrective action cannot be implemented within the times described in 27622.16(e)(10) through (13); document all corrective actions delayed beyond the timelines established in subsection 2762.16(e); include the following documentation: (A) The rationale for deferring the corrective action(s); (B) The documentation required under the MOC process; (C) A timeline describing when the corrective action(s) will be implemented; and (D) An effective plan to make available the rationale and revised timeline to all affected employees and their representatives. CORRECTIVE ACTION: Ensure interim safeguards are sufficient to prevent the potential for a major incident, and delayed corrective actions meet the above requirements. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010256 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Annex | Failure to track each corrective action item to completion and append the documentation of completion to the applicable PHA, DMR, HCA, SPA, compliance audit, or incident investigation report. | 19 CCR 4.5 2762.16(e)(15) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 277 | Program 4 Prevention Program | Management System | Tracked each corrective action item to completion and appended the documentation | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to track each corrective action item to completion and append the documentation of completion to the applicable PHA, DMR, HCA, SPA, compliance audit, or incident investigation report. |  |  | OBSERVATION: Owner/operator failed to track each corrective action item to completion and append the documentation of completion to the applicable PHA, DMR, HCA, SPA, compliance audit, or incident investigation report. CORRECTIVE ACTION: Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010257 |  |  | Program level 4: Accidental Release Prevention Program Management System - Stop Work Procedures and Anonymous Hazard Reporting | Failure to develop and implement the following, within 90 calendar days of the effective date of Article 6.5, in consultation with employees and employees representatives: (1) Effective Stop Work procedures that ensure: (A) The authority of all employees, including employees of contractors, to refuse to perform a task where doing so could reasonably result in death or serious physical harm; (B) The authority of all employees, including employees of contractors, to recommend to the operator in charge of a unit that an operation or process be partially or completely shut-down, based on a process safety hazard; and, (C) The authority of the qualified operator in charge of a unit to partially or completely shut-down an operation or process, based on a process safety hazard. (2) Effective procedures to ensure the right of all employees, including employees of contractors, to anonymously report hazards. The owner or operator shall respond in writing within 30 calendar days to written hazard reports submitted by employees, employee representatives, contractors, employees of contractors and contractor employee representatives. The owner or operator shall prioritize and promptly respond to and correct hazards that present the potential for death or serious physical harm. | 19 CCR 4.5 2762.16(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 278 | Program 4 Prevention Program | Management System | Developed and implemented effective Stop Work procedures and to anonymously report hazards | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement the following, within 90 calendar days of the effective date of Article 6.5, in consultation with employees and employees representatives: (1) Effective Stop Work procedures that ensure: (A) The authority of all employees, including employees of contractors, to refuse to perform a task where doing so could reasonably result in death or serious physical harm; (B) The authority of all employees, including employees of contractors, to recommend to the operator in charge of a unit that an operation or process be partially or completely shut-down, based on a process safety hazard; and, (C) The authority of the qualified operator in charge of a unit to partially or completely shut-down an operation or process, based on a process safety hazard. (2) Effective procedures to ensure the right of all employees, including employees of contractors, to anonymously report hazards. The owner or operator shall respond in writing within 30 calendar days to written hazard reports submitted by employees, employee representatives, contractors, employees of contractors and contractor employee representatives. The owner or operator shall prioritize and promptly respond to and correct hazards that present the potential for death or serious physical harm. |  |  | OBSERVATION: Owner/operator failed to: develop and implement the following, within 90 calendar days of the effective date of Article 6.5, in consultation with employees/employees representatives: (1) Effective Stop Work procedures (2) Effective procedures to ensure the right of all employees/contractor employees, to anonymously report hazards. CORRECTIVE ACTION: Develop and implement effective Stop Work procedures and procedures to ensure the right of all employees/contractor employees to anonymously report hazards. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010258 |  |  | Program level 4: Accidental Release Prevention Program Management System - Reporting System | Failure to develop a system, within 90 calendar days of the effective date of section 2762.16, to document and enable employees to report information pursuant to subsections 2762.16 (f)(1) and (f)(2). | 19 CCR 4.5 2762.16(g) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 279 | Program 4 Prevention Program | Management System | Developed a system to document and enable employees to report information | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop a system, within 90 calendar days of the effective date of section 2762.16, to document and enable employees to report information pursuant to subsections 2762.16 (f)(1) and (f)(2). |  |  | OBSERVATION: Owner/operator failed to develop a system, within 90 calendar days of the effective date of section 2762.16, to document and enable employees to report information pursuant to subsections 2762.16 (f)(1) and (f)(2). CORRECTIVE ACTION: Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010259 |  |  | Program level 4: Accidental Release Prevention Program Management System-Process Safety Performance Indicators | Failure to report process safety performance indicators listed in subsection (A) through (E) below to CalEPA and the UPA every year on June 30 for the period from January 1 to December 31 of the prior year, starting one calendar year after the effective date of Article 6.5. (A) Past due inspections for piping and pressure vessels: i. Overdue inspection for piping and pressure vessels shall be reported. This information will not include relief devices, instrumentation, instrument air receivers, boilers, furnaces, atmospheric tanks, or rotating equipment. ii. Pressure vessels include but are not limited to: heat exchangers, columns, spheres, bullets as defined by CA Safety Order and U-stamped (or treated as such). The scope of the inspections for this reporting include external visual, condition monitoring location (CML) and nondestructive examination (NDE), and internal visual. Pressure vessel is defined by Title 8, Division 1, Chapter 4, Subchapter 1 Unfired Pressure vessel safety orders. iii. Process Piping and piping components excluding utility piping, the scope of the inspections shall include external visual, CML/NDE and internal visual as appropriate. iv. Past due is defined as overdue by the requirements listed in California Code of Regulations, Title 8, section 6857, API 510 and API 570. Deferral/extension when used shall follow the requirements contained within the above code and recommended practices. v. Inspections shall be defined by circuits rather than points. A circuit shall be defined by one of the following: isometrics, by process stream and piping class, or piece of equipment, such as a pressure vessel. When reporting past due inspections to Cal OES and the UPA, the owner or operator shall include the total number of circuits at the stationary source and the total number of annual planned circuit inspections for that year to provide context regarding the number of circuits/equipment defined by the inspection program at the facility. (B) Past due PHA corrective actions and seismic corrective actions shall be reported. If a stationary source receives an extension approved by the UPA, the new approved due date shall apply. (C) Past due Incident Investigation corrective actions shall be reported for major incidents. All major incidents that occur after the effective date of this Article are subject to this requirement. (D) Major incidents: The number of major incidents that have occurred since the effective date of this Article. (E) The number of temporary piping and equipment repairs that are installed on hydrocarbon and high energy utility systems that are past their date of replacement with a permanent repair and the total number of temporary piping and equipment repairs installed on hydrocarbon and high energy utility systems. The owner or operator shall document, but not report, the date the temporary piping repair was installed, and the date for the permanent repair is to be complete. (F) Past due item is an item that is not completed by the end of the month during the month that is due. Each month an item that is past due shall be counted overdue. If the item is continued from the prior month then it is also counted as a repeat item. The repeat row is a subset of the overdue items. The table below shall be used for each of the indicators listed above. | 19 CCR 4.5 2762.16(h)(1) | 2022-07-01 | 2024-09-30 | 2024-09-30 | Revised | 280 | Program 4 Prevention Program | Management System | Reported Process Safety Performance Indicators to CalEPA and the UPA annually on June 30. | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to report process safety performance indicators listed in subsection (A) through (E) below to CalEPA and the UPA every year on June 30 for the period from January 1 to December 31 of the prior year, starting one calendar year after the effective date of Article 6.5. (A) Past due inspections for piping and pressure vessels: i. Overdue inspection for piping and pressure vessels shall be reported. This information will not include relief devices, instrumentation, instrument air receivers, boilers, furnaces, atmospheric tanks, or rotating equipment. ii. Pressure vessels include but are not limited to: heat exchangers, columns, spheres, bullets as defined by CA Safety Order and U-stamped (or treated as such). The scope of the inspections for this reporting include external visual, condition monitoring location (CML) and nondestructive examination (NDE), and internal visual. Pressure vessel is defined by Title 8, Division 1, Chapter 4, Subchapter 1 Unfired Pressure vessel safety orders. iii. Process Piping and piping components excluding utility piping, the scope of the inspections shall include external visual, CML/NDE and internal visual as appropriate. iv. Past due is defined as overdue by the requirements listed in California Code of Regulations, Title 8, section 6857, API 510 and API 570. Deferral/extension when used shall follow the requirements contained within the above code and recommended practices. v. Inspections shall be defined by circuits rather than points. A circuit shall be defined by one of the following: isometrics, by process stream and piping class, or piece of equipment, such as a pressure vessel. When reporting past due inspections to Cal OES and the UPA, the owner or operator shall include the total number of circuits at the stationary source and the total number of annual planned circuit inspections for that year to provide context regarding the number of circuits/equipment defined by the inspection program at the facility. (B) Past due PHA corrective actions and seismic corrective actions shall be reported. If a stationary source receives an extension approved by the UPA, the new approved due date shall apply. (C) Past due Incident Investigation corrective actions shall be reported for major incidents. All major incidents that occur after the effective date of this Article are subject to this requirement. (D) Major incidents: The number of major incidents that have occurred since the effective date of this Article. (E) The number of temporary piping and equipment repairs that are installed on hydrocarbon and high energy utility systems that are past their date of replacement with a permanent repair and the total number of temporary piping and equipment repairs installed on hydrocarbon and high energy utility systems. The owner or operator shall document, but not report, the date the temporary piping repair was installed, and the date for the permanent repair is to be complete. (F) Past due item is an item that is not completed by the end of the month during the month that is due. Each month an item that is past due shall be counted overdue. If the item is continued from the prior month then it is also counted as a repeat item. The repeat row is a subset of the overdue items. The table below shall be used for each of the indicators listed above. |  |  | OBSERVATION: Owner/operator failed to: report process safety performance indicators listed in subsection (A) through (E) below to CalEPA and the UPA every year on June 30 for the period from January 1 to December 31 of the prior year, starting one calendar year after the effective date of Article 6.5; use the required table for each of the indicators listed. CORRECTIVE ACTION: Report process safety performance indicators as required above and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010260 |  |  | Program level 4: Accidental Release Prevention Program Management System -Individual Program 4 Process Safety Performance Indicators | Failure to develop and measure, no later than six months after the effective date of Article 6.5, a list of site-specific indicators, consisting of activities and other events in order to evaluate the performance of its process safety systems for the purpose of continuous improvement. Failure to prepare an annual written report by June 30 of each year containing a compilation of these site specific indicators for the previous calendar year. Failure to ensure the stationary source manager or designee certify annually that the report is current and accurate. | 19 CCR 4.5 2762.16(h)(2) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 281 | Program 4 Prevention Program | Management System | Developed and measured site-specific indicators to evaluate performance of process safety systems | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and measure, no later than six months after the effective date of Article 6.5, a list of site-specific indicators, consisting of activities and other events in order to evaluate the performance of its process safety systems for the purpose of continuous improvement. Failure to prepare an annual written report by June 30 of each year containing a compilation of these site specific indicators for the previous calendar year. Failure to ensure the stationary source manager or designee certify annually that the report is current and accurate. |  |  | OBSERVATION: Owner/operator failed to: develop and measure, no later than six months after the effective date of Article 6.5, a list of site-specific indicators, consisting of activities and other events in order to evaluate the performance of its process safety systems for the purpose of continuous improvement; prepare an annual written report by June 30 of each year containing a compilation of these site specific indicators for the previous calendar year; ensure the stationary source manager or designee certify annually that the report is current and accurate. CORRECTIVE ACTION: Develop and measure a list of site-specific indicators that meet above requirements; prepare an annual written report and ensure the refinery manager or designee annually certify report. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010261 |  |  | Program level 4: Access to Documents and Information | Failure to provide documents or information developed or collected pursuant to Article 6.5 to the UPA upon request. | 19 CCR 4.5 2762.17 | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 282 | Program 4 Prevention Program | Access to Documents and Information | Provided documents or information developed pursuant Article 6.5 to the UPA upon request. | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide documents or information developed or collected pursuant to Article 6.5 to the UPA upon request. |  |  | OBSERVATION: Owner/operator failed to provide documents or information developed or collected pursuant to Article 6.5 to the UPA upon request. CORRECTIVE ACTION: Submit and provide documentation or information developed or collected pursuant to Article 6.5 to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010 |  |  | CalARP Program - Administration/Documentation - General | Administration/Documentation - General | 19 CCR 4.5 Multiple Sections | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 284 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Training | 5020 |  |  | CalARP Program - Training - General | Training - General | 19 CCR 4.5 Multiple Sections | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 286 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Operations/Maintenance | 5030 |  |  | CalARP Program - Operations/Maintenance - General | Operations/Maintenance - General | 19 CCR 4.5 Multiple Sections | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 288 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Release/Leaks/Spills | 5040 |  |  | CalARP Program - Release/Leaks/Spills -General | Release/Leaks/Spills - General | 19 CCR 4.5 Multiple Sections | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 290 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 5050 |  |  | CalARP Program - Abandonment/Illegal Disposal/Unauthorized Treatment -General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 19 CCR 4.5 Multiple Sections | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 292 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010019 |  |  | Submission: Risk Management Plan New or Modified Stationary Source - Table 3 | Failure of a new or modified stationary source to submit a Risk Management Plan to the UPA prior to the date in which a regulated substance is first present in a process above the listed threshold quantity. | 19 CCR 4.5 2745.1(d) | 2019-09-01 | 2024-09-30 | 2024-09-30 | Deleted | 14 | RMP Components and Submission | RMP Submission | Submitted a RMP to the UPA prior to the date a RS is in a process above the threshold quantity | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure of a new or modified stationary source to submit a Risk Management Plan to the UPA prior to the date in which a regulated substance is first present in a process above the listed threshold quantity. |  |  | OBSERVATION: (Program 1 facility) The owner/operator failed to submit a Risk Management Plan to the CUPA prior to the date in which a regulated substance is first present in a process above the listed threshold quantity. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan to the CUPA that includes the information required by Sections 2745.3 through 2745.5 and 2745.8 through 2745.9. | OBSERVATION: (Program 2 or 3 facility) The owner/operator failed to submit a Risk Management Plan to the CUPA prior to the date in which a regulated substance is first present in a process above the listed threshold quantity. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan to the CUPA that includes the information required by Sections 2745.3 through 2745.9. | [5 empty] | Yes | Yes | Yes | Yes

## UST
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading (Optional) | Inspection Checklist Sub-Heading (Optional) | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop-Down | Default Degree of Violation | Required Item? | Points (Optional) | Comply By Days (Optional) | Violation Descriptive Text | TCR DESIGNATION | Violation Corrective Text (Optional) | Inspector Comment 1 (Optional) | Inspector Comment 2 (Optional) | Inspector Comment 3 (Optional) | Inspector Comment 4 (Optional) | Inspector Comment 5 (Optional) | UST FULL | UST DW | UST SW
UST Program | Operations/Maintenance | 2030075 | Release Detection (USEPATCR 9d) |  | Emergency Generator Tank Systems Line Leak Detector (LLD) (USEPATCR 9d) (USEPA Priority) | Failure of the functional line leak detector (LLD) for emergency generator tank systems to monitor with the capability of detecting a release of 3.0 gallons per hour leak at 10 pounds per square inch within an hour and restrict or shut off the flow of product through the piping or triggers a visual and audible alarm. | 23 CCR 16 2636(f), 2666(c), 2666(f) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 32 | UST System Observations | General Monitoring | E Gen System LLD detects 3 gph leak & restricts/shuts off flow or activates aud/vis alarm (TCR 9d) | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the functional line leak detector (LLD) for emergency generator tank systems to monitor with the capability of detecting a release of 3.0 gallons per hour leak at 10 pounds per square inch within an hour and restrict or shut off the flow of product through the piping or triggers a visual and audible alarm. | 9d |  | OBSERVATION: Owner/Operator did not install or failed to ensure that a functional LLD was installed on underground piping connected to emergency generator tank system which monitors at least hourly with the capability of detecting a release of 3.0 gph leak at 10 psi and restricts or shuts off the flow of product through the piping, or triggers a visual and audible alarm. CORRECTIVE ACTION: Repair or install LLD on underground piping connected to emergency generator tank system which meets the requirements listed above. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030020 |  |  | Emergency Generator Piping - Exemption | Failure to meet one or more exemption requirements for emergency generator tank system unburied fuel piping: 1) Conduct visual inspections each time the tank is operated but no less than monthly. 2) Maintain a log of inspection results for review by the UPA. | HSC 6.7 25281.5(b)(3) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 60 | On Site Records | Logs | Unburied fuel piping visually inspected at least monthly and log kept | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet one or more exemption requirements for emergency generator tank system unburied fuel piping: 1) Conduct visual inspections each time the tank is operated but no less than monthly. 2) Maintain a log of inspection results for review by the UPA. |  |  | OBSERVATION: Owner/Operator did not conduct visual inspections each time the tank is operated, but not less than monthly, and maintain a log of inspection results for review by the CUPA. CORRECTIVE ACTION: Conduct visual inspections each time the tank is operated, but not less than monthly, and maintain a log of inspection results for review by the CUPA. | OBSERVATION: A log of monthly checks of the unburied single walled piping was not found onsite. For an emergency generator tank system, the unburied piping is exempt from regulation if visual inspections are made each time the system is operated, but no less than monthly, and a log is maintained. CORRECTIVE ACTION: Immediately begin inspecting the system each time the system is operated, but no less than monthly, and maintain a log of the inspections, or submit a permit application to upgrade the UST system to meet Title 23 UST regulations. |  |  |  | Yes | No | No
UST Program | Operations/Maintenance | 2030059 |  |  | Emergency Generator Tank System In Below-Grade Structure Exemption | Failure to meet the conditions required to exempt an emergency generator tank system in a below-grade structure from UST regulations. | HSC 6.7 25281.6(a) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 73 | General Operating Requirements | Permit Condition/Approval | UST system below ground connected to a E Gen system in compliance with exclusion/exemption req's | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the conditions required to exempt an emergency generator tank system in a below-grade structure from UST regulations. |  |  | OBSERVATION: Owner/Operator did not maintain compliance with conditions of exemption from UST regulation for an emergency generator system in a below grade structure. CORRECTIVE ACTION: Maintain UST system below ground connected to a emergency generator system in accordance with exclusion/exemption status. Submit verification. |  |  |  |  | Yes | Yes | Yes
Note on N1: With the Checklist Item Order column in mind, this text represents text that will group one or more sub-headings and violations. If no Inspection Checklist Heading, the checklist items will not be grouped. Example: Leak Detection 100 Characters Max
Note on O1: With the Checklist Item Order field in mind and as a sub-item to Checklist Heading, this text represents text that will group one or more violations. If no Checklist Sub-Heading, the checklist items will fall under the Checklist Heading. Example: “Single Wall” 100 Characters Max
Note on P1: This is what appears on the checklist for the inspector. It should be descriptive and relatively short. May be the same as Name if sufficiently descriptive. Note: Decade recommends expressing the checklist item “in the positive.” For example, “Facility performs enhanced leak detection testing before the tank is placed in use” (positive) vs. “Failure to perform enhanced leak detection testing before the tank is placed in use” (negative). 100 Characters Max
Note on Q1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on R1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on S1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on T1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on U1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on V1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Example: Y or N
Note on W1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Example: Y or N
Note on X1: For this checklist item, display the option to set/override the Degree of Violation (e.g., Class 1, Class2, Minor) Example: Y or N
Note on Y1: Is this violation typically recorded as a Class 1, Class 2, or Minor Violation. Blank (no default) is also a valid option. Example: Y or N
Note on Z1: If marked Y, then the inspection cannot be completed without selecting IN, OUT, NA, or NO. Otherwise, mark this item N. Example: Y or N
Note on AA1: Indicate the number of points that should be added/deducted when this item is marked OUT of compliance. Example: 5
Note on AB1: Indicate the number of days following the first Notice of Violation on which the regulator expects compliance. Example: 30
Note on AC1: This static text may appear on a printed inspection report when inspections are conducted electronically. May use “Description” column from the Unified Program Violation Library.
Note on AD1: For Summary Reporting, this field shall specify if the cited violation relates to Release Detection. Example: Y or N
Note on AE1: This static text may appear on a printed inspection report when inspections are conducted electronically.
Note on AF1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AG1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AH1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AI1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AJ1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AK1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AL1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AM1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.

## APSA
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | AST Conditionally Exempt | AST Non_Qualified | AST Tier I | AST Tier II
APSA Program | Administration/Documentation | 4010001 |  |  | SPCC Plan prepared | Failure to prepare a Spill Prevention, Control, and Countermeasure (SPCC) Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3, 112.6 | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 1 | Requirement to Prepare and Implement |  | SPCC has been prepared | 22 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a Spill Prevention Control and Countermeasure (SPCC) Plan. |  |  | OBSERVATION: Failure to prepare SPCC. CORRECTIVE ACTION: Prepare SPCC. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030015 |  |  | Tanks inspected and/or integrity tested | Failure to test or inspect each aboveground container for integrity based on industry standards as discussed in the SPCC Plan: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(e), 112.8(c)(6) | 2020-10-01 | 2024-09-30 | 2024-09-30 | Revised | 64 | SPCC Requirements for Onshore Facilities | Inspections & Testing | Aboveground containers tested or inspected for integrity based on industry standards | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to test or inspect each aboveground container for integrity based on industry standards as discussed in the SPCC Plan: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. |  |  | OBSERVATION: Failure to test or inspect each aboveground container for integrity based on industry standards as discussed in the SPCC Plan: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. CORRECTIVE ACTION: Test or inspect each aboveground container for integrity based on industry standards on a regular schedule, after making material repairs, using non-destructive testing, inspecting each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. Maintain testing and inspection records. | [6 empty] | No | Yes | Yes | Yes

## HW
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | HazWaste SQG | HazWaste LQG
Hazardous Waste Generator | Administration/Documentation | 3010002 |  |  | Hazardous Waste Generator: Identification Number | Failure to obtain an Identification Number prior to treating, storing, disposing of, transporting or offering for transportation any hazardous waste. | 22 CCR 12 66262.12 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 1 | Recordkeeping/ Documentation | ID Number | Obtained an Identification Number (unless exempted HSC 25143.13) | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain an Identification Number prior to treating, storing, disposing of, transporting or offering for transportation any hazardous waste. |  |  | OBSERVATION: The generator has not obtained an Identification Number to manage hazardous waste. A hazardous waste generator shall not treat, store, dispose of, transport or offer for transportation, hazardous waste without obtaining an Identification Number. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you have obtained an Identification Number. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030040 |  |  | Large Quantity Generator: Contingency Plan | Failure to prepare and implement a written Contingency Plan to minimize hazards to human health or the environment from fires, explosions, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.51 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 2 | Recordkeeping/ Documentation | Contingency Plan | Contingency Plan prepared and implemented | 41 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare and implement a written Contingency Plan to minimize hazards to human health or the environment from fires, explosions, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water. |  |  | OBSERVATION: Facility failed to prepare an Contingency Plan. The owner or operator shall prepare an Emergency Response Plan designed to minimize hazards to human health or the environment from fires, explosions, or any unplanned release of hazardous waste to air, soil, or surface water. CORRECTIVE ACTION: Immediately prepare an Contingency Plan and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010024 |  |  | Large Quantity Generator: Contingency Plan Copies | Failure to maintain a copy of the contingency plan and all its revisions at the facility and to submit a copy to all local police departments, fire departments, hospitals, and State and local emergency response teams that may be called upon to provide emergency services. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.53 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 3 | Recordkeeping/ Documentation | Contingency Plan | Contingency Plan and all revisions maintained at the facility | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain a copy of the contingency plan and all its revisions at the facility and to submit a copy to all local police departments, fire departments, hospitals, and State and local emergency response teams that may be called upon to provide emergency services. |  |  | OBSERVATION: A copy of the Contingency Plan is not maintained at the facility. CORRECTIVE ACTION: Locate a copy of the Contingency Plan, maintain it at the facility, and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010023 |  |  | Large Quantity Generator: Contingency Plan Emergency Action Plan | Failure to include all of the following in the Contingency Plan: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. (If the owner or operator has already prepared a Spill Prevention, Control, and Countermeasures (SPCC) Plan or some other emergency or contingency plan, the owner or operator need only amend that plan to incorporate hazardous waste management provisions.) | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.52 | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 4 | Recordkeeping/ Documentation | Contingency Plan | Contingency plan contains all required content | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include all of the following in the Contingency Plan: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. (If the owner or operator has already prepared a Spill Prevention, Control, and Countermeasures (SPCC) Plan or some other emergency or contingency plan, the owner or operator need only amend that plan to incorporate hazardous waste management provisions.) |  |  | OBSERVATION: The Contingency Plan does not contain [LIST MISSING CONTENT]. CORRECTIVE ACTION: Revise the Contingency Plan to include all the content required by 22 CCR 15 66265.52 and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Training | 3020001 |  |  | Small Quantity Generator: Employee Training | Failure to ensure that all employees are thoroughly familiar with proper waste handling and emergency procedures, relevant to their responsibilities during normal facility operations and emergencies. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(5)(iii) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 5 | Recordkeeping/ Documentation | Training | Employees thoroughly familiar with all waste handling and emergency procedures | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that all employees are thoroughly familiar with proper waste handling and emergency procedures, relevant to their responsibilities during normal facility operations and emergencies. |  |  | OBSERVATION: Employees are not thoroughly familiar with proper waste handling and emergency procedures as demonstrated by the number and/or type of hazardous waste violations observed at the time of inspection. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that employees have been properly trained. | [6 empty] | Yes | No
Hazardous Waste Generator | Training | 3020002 |  |  | Large Quantity Generator: Employee Hazardous Waste Training | Failure to provide employees with hazardous waste training program of class room instructions or on-the-job training within 180 days after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. Training records on current personnel shall be kept until closure of the facility and for former employees the record shall be kept for at least three years from the date the employee last worked at the facility. The records shall include the following: the job title for each position at the facility related to hazardous waste management, and the name of the employee filling each job; a written job description for each position, duties of facility personnel assigned to each position, and a written description of the type and amount of both introductory and continuing training that will be given to each person filling a position. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.16 | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 6 | Recordkeeping/ Documentation | Training | Facility personnel are trained annually and maintain required documentation until closure | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide employees with hazardous waste training program of class room instructions or on-the-job training within 180 days after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. Training records on current personnel shall be kept until closure of the facility and for former employees the record shall be kept for at least three years from the date the employee last worked at the facility. The records shall include the following: the job title for each position at the facility related to hazardous waste management, and the name of the employee filling each job; a written job description for each position, duties of facility personnel assigned to each position, and a written description of the type and amount of both introductory and continuing training that will be given to each person filling a position. |  |  | OBSERVATION: As demonstrated by the number and type of hazardous waste violations observed at the time of inspection, personnel are not adequately trained to perform their duties in a way that ensures the facility's compliance with hazardous waste laws and regulations, and/or employee training records have not been kept or do not contain all required information, or employees were not trained within 180 days after their hire date or assignment to a new facility or position, and annually thereafter. CORRECTIVE ACTION: Conduct training with applicable personnel and document it according to the requirements of 22 CCR 15 66265.16(d). Submit a copy of the documentation to the CUPA. | OBSERVATION: Documented training of personnel was not available at the time of inspection. CORRECTIVE ACTION: Locate training documentation or conduct training with applicable personnel and document it. Submit a copy of the training documentation to the CUPA. | [5 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030006 |  |  | Hazardous Waste Generator: Land Disposal Restriction | Failure to determine if the waste has to be treated before it can be land disposed and retain the documentation at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. | 22 CCR 12 66262.34(a)(4); 22 CCR 18 66268.7(a) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 18 | Recordkeeping/ Documentation | Waste Determination | Determined land disposal restrictions for hazardous waste | 57 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to determine if the waste has to be treated before it can be land disposed and retain the documentation at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. |  |  | OBSERVATION: Land Disposal Restriction (LDR) documentation for [HAZARDOUS WASTE] was not available at the time of inspection. CORRECTIVE ACTION: Submit LDR documentation for [HAZARDOUS WASTE] to this department. Retain the documentation at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050002 |  |  | Hazardous Waste Generator: Improper Disposal of Hazardous Waste | Failure to dispose of hazardous waste at a facility which has a permit from DTSC or disposing of hazardous waste at any point which is not authorized. | HSC 6.5 25189.5(a) | 2021-08-02 | 2024-09-30 | 2024-09-30 | Revised | 26 | Hazardous Waste Management | Disposal | Disposed of hazardous waste at an authorized location | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to dispose of hazardous waste at a facility which has a permit from DTSC or disposing of hazardous waste at any point which is not authorized. |  |  | OBSERVATION: Owner/Operator failed to dispose of hazardous waste at a facility which has a permit from DTSC or disposed of hazardous waste at a point which is not authorized pursuant to HSC chapter 6.5. CORRECTIVE ACTION: Immediately discontinue disposing of hazardous waste at any facility not permitted by DTSC or to any point which is not authorized pursuant to HSC chapter 6.5. Submit a statement to the CUPA indicating improperly disposed of hazardous waste has been properly managed, and that all hazardous wastes will only be disposed at facilities permitted by DTSC in the future. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030009 |  |  | Generator of < 100 kg/mth: Accumulation Time Exceeded (180/270, or 90 Days for Acutely/Extremely) | Failure to send hazardous waste offsite for treatment, storage, or disposal within 180 days (or 270 days if waste is transported over 200 miles) of when the accumulation period begins*, for a generator who generates less than 100 kilogram per month if all of the following conditions are met: (1) The quantity of hazardous waste accumulated onsite never exceeds 6,000 kilograms. (2) The generator complies with the requirements of 40 Code of Federal Regulations section 262.34(d), (e) and (f). (3) The generator does not hold acutely hazardous waste or extremely hazardous waste in an amount greater than one kilogram for more than 90 days. *The accumulation period begins when the generator has accumulated 100 kilograms of hazardous waste or one kilogram of extremely hazardous waste or acutely hazardous waste. | 22 CCR 12 66262.34(d); HSC 6.5 25123.3(c), 25123.3(h)(1) | 2020-10-01 | 2024-09-30 | 2024-09-30 | Revised | 28 | Hazardous Waste Management | Accumulation Time Limits | <100 kg/mth generator disposed of waste within 180 days of accumulation start date (90 days for AHW) | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to send hazardous waste offsite for treatment, storage, or disposal within 180 days (or 270 days if waste is transported over 200 miles) of when the accumulation period begins*, for a generator who generates less than 100 kilogram per month if all of the following conditions are met: (1) The quantity of hazardous waste accumulated onsite never exceeds 6,000 kilograms. (2) The generator complies with the requirements of 40 Code of Federal Regulations section 262.34(d), (e) and (f). (3) The generator does not hold acutely hazardous waste or extremely hazardous waste in an amount greater than one kilogram for more than 90 days. *The accumulation period begins when the generator has accumulated 100 kilograms of hazardous waste or one kilogram of extremely hazardous waste or acutely hazardous waste. |  |  | OBSERVATION: Owner/Operator who is a generator of <100 kg/mth failed to send hazardous waste offsite for treatment, storage, or disposal within 180/270 days of accumulating 100 kilograms, or within 90 days of accumulating 1 kg of extremely/acutely hazardous waste. CORRECTIVE ACTION: Dispose of hazardous waste and submit a copy of the manifest/receipt to the CUPA. Ensure that hazardous waste is not stored for more than 180/270 days after the accumulation period begins, and that acute/extremely hazardous waste is not stored for more than 90 days after accumulating 1 kilogram. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030010 |  |  | Small Quantity Generator: Time Exceeded for Hazardous Waste Conditional Accumulation (180 Days) | Failure to send hazardous waste offsite for treatment, storage, or disposal within 180 days (or 270 days if waste is transported over 200 miles) for a generator who generates less than 1000 kilograms per month if all of the following conditions are met: (1) The quantity of hazardous waste accumulated onsite never exceeds 6,000 kilograms. (2) The generator complies with the requirements of 40 Code of Federal Regulations section 262.34(d), (e) and (f). (3) The generator does not hold acutely hazardous waste or extremely hazardous waste in an amount greater than one kilogram for more than 90 days. | 22 CCR 12 66262.34(d); HSC 6.5 25123.3(h)(1) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 29 | Hazardous Waste Management | Accumulation Time Limits | Disposed of hazardous waste within 180 days of accumulation start date | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to send hazardous waste offsite for treatment, storage, or disposal within 180 days (or 270 days if waste is transported over 200 miles) for a generator who generates less than 1000 kilograms per month if all of the following conditions are met: (1) The quantity of hazardous waste accumulated onsite never exceeds 6,000 kilograms. (2) The generator complies with the requirements of 40 Code of Federal Regulations section 262.34(d), (e) and (f). (3) The generator does not hold acutely hazardous waste or extremely hazardous waste in an amount greater than one kilogram for more than 90 days. |  |  | OBSERVATION: Owner/Operator is a small quantity generator and failed to send hazardous waste offsite for treatment, storage, or disposal within 180 days (or 270 days if waste is transported over 200 miles), or has failed to comply with the conditions of CCR 66262.34(d) and has stored hazardous waste over 90 days. CORRECTIVE ACTION: Dispose of hazardous waste that has been stored over the applicable time limit and provide documentation that the violation has been corrected. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030012 |  |  | Large Quantity Generator: Hazardous Waste Accumulation Time Exceeded | Failure to send hazardous waste offsite for treatment, storage, or disposal within 90 days for a generator who generates 1000 kilograms or more per month. | 22 CCR 12 66262.34(a), (c); HSC 6.5 25123.3(b)(1) | 2021-08-02 | 2024-09-30 | 2024-09-30 | Revised | 30 | Hazardous Waste Management | Accumulation Time Limits | Disposed of hazardous waste within 90 days of accumulation start date | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to send hazardous waste offsite for treatment, storage, or disposal within 90 days for a generator who generates 1000 kilograms or more per month. |  |  | OBSERVATION: Owner/Operator failed to send hazardous waste offsite for treatment, storage, or disposal within 90 days of accumulation start date. CORRECTIVE ACTION: Dispose of hazardous waste and submit a copy of the manifest/receipt to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030057 |  |  | Hazardous Waste Generator: Satellite Accumulation | Failure to meet the following conditions of satellite accumulation regulations: • Accumulate up to 55 gallons of hazardous waste or one quart of acute hazardous waste at or near the initial point of accumulation which was under the control of the operator. • Total time hazardous waste can be accumulated onsite in any generator accumulation area is either one year from the initial date of accumulation, or 90/180/270 days (depending on size of generator and distance transported) from the date on which the quantity limitation of 55 gallons of hazardous waste or one quart of acutely hazardous waste is reached, whichever comes first. • The generator complies with section 66265.171, 66265.172, and 66265.173(a). • The container must be clearly marked with the initial date that hazardous waste is first placed in the container and labelled with the words “Hazardous Waste” including specified information • Container must be labelled with the date the satellite accumulation limit is reached and moved within three days after reaching the 55 gallon (or one quart) limit to a central accumulation area • 55 gallons (or one quart of acute hazardous waste) of waste per process may be accumulated | 22 CCR 12 66262.34(e) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 31 | Hazardous Waste Management | Accumulation Time Limits | Met all requirements for hazardous waste satellite accumulation | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to meet the following conditions of satellite accumulation regulations: • Accumulate up to 55 gallons of hazardous waste or one quart of acute hazardous waste at or near the initial point of accumulation which was under the control of the operator. • Total time hazardous waste can be accumulated onsite in any generator accumulation area is either one year from the initial date of accumulation, or 90/180/270 days (depending on size of generator and distance transported) from the date on which the quantity limitation of 55 gallons of hazardous waste or one quart of acutely hazardous waste is reached, whichever comes first. • The generator complies with section 66265.171, 66265.172, and 66265.173(a). • The container must be clearly marked with the initial date that hazardous waste is first placed in the container and labelled with the words “Hazardous Waste” including specified information • Container must be labelled with the date the satellite accumulation limit is reached and moved within three days after reaching the 55 gallon (or one quart) limit to a central accumulation area • 55 gallons (or one quart of acute hazardous waste) of waste per process may be accumulated |  |  | OBSERVATION: Failure of the Owner/Operator to comply with one or more satellite accumulation requirements. {Describe as needed} CORRECTIVE ACTION: Ensure that all hazardous wastes being accumulated pursuant to satellite accumulation meet all applicable requirements and submit documentation of compliance to the CUPA. {Describe specific corrections as needed} | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030007 |  |  | Hazardous Waste Generator: Hazardous Waste Labeling Standards | Failure to properly label hazardous waste accumulation containers and portable tanks with the following requirements: "Hazardous Waste", name and address of the generator, physical and chemical characteristics of the Hazardous Waste, and starting accumulation date. | 22 CCR 12 66262.34(f) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 32 | Hazardous Waste Management | Container Management | Labeled all containers or portable tanks containing hazardous waste | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly label hazardous waste accumulation containers and portable tanks with the following requirements: "Hazardous Waste", name and address of the generator, physical and chemical characteristics of the Hazardous Waste, and starting accumulation date. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed without a hazardous waste label. CORRECTIVE ACTION: Submit a photo to the CUPA demonstrating that the container listed above has been properly labeled. | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed without the following information on the label: [LIST MISSING INFORMATION]. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that the container listed above has been properly labeled. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030013 |  |  | Small Quantity Generator: Container in Poor Condition or Damaged | Failure to accumulate hazardous waste in a container that is in good condition. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(1), 262.34(d)(2), 265.171 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 33 | Hazardous Waste Management | Container Management | Accumulated hazardous waste in containers that are in good condition | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to accumulate hazardous waste in a container that is in good condition. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [LIST HAZARDOUS WASTE] located in the [LOCATION] was observed [DESCRIBE CONDITION]. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is in good condition or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030015 |  |  | Small Quantity Generator: Hazardous Waste Container Incompatible with Material Stored | Failure to accumulate or store hazardous waste in container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(2), 265.172 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 34 | Hazardous Waste Management | Container Management | Hazardous waste accumulated in lined and/or compatible containers | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to accumulate or store hazardous waste in container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed in an [UNLINED / INCOMPATIBLE] container. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is compatible with the hazardous waste or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030017 |  |  | Small Quantity Generator: Open Hazardous Waste Containers | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(2), 265.173 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 35 | Hazardous Waste Management | Container Management | Containers of hazardous waste closed except when adding or removing waste | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed open. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that the container listed above has been properly closed. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030019 |  |  | Small Quantity Generator: Weekly Hazardous Waste Storage Area Inspection | Failure to inspect hazardous waste storage areas at least weekly and look for leaking and deteriorating containers. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(2), 265.174 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 36 | Hazardous Waste Management | Container Management | Inspects all hazardous waste storage areas at least weekly | 58 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to inspect hazardous waste storage areas at least weekly and look for leaking and deteriorating containers. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed [LEAKING / DETERIORATING]. CORRECTIVE ACTION: Submit a copy of the inspection log to the CUPA demonstrating that the hazardous waste storage area is being inspected weekly. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030022 |  |  | Small Quantity Generator: Incompatible Waste Storage | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(2), 265.17(b), 265.177 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 37 | Hazardous Waste Management | Container Management | Incompatible waste in containers managed properly to prevent a reaction | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [LIST HAZARDOUS WASTES] located in the [LOCATION] are not compatible and were observed stored in a manner that could result a reaction. CORRECTIVE ACTION: Transfer or separate the containers of incompatible wastes noted above to other compatible containers or by separating containers to prevent a reaction and submit photos to the CUPA demonstrating compliance. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030014 |  |  | Large Quantity Generator: Container in Poor Condition or Damaged | Failure to accumulate hazardous waste in a container that is in good condition. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.171 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 38 | Hazardous Waste Management | Container Management | Accumulated hazardous waste in containers that are in good condition | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to accumulate hazardous waste in a container that is in good condition. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed [DESCRIBE CONDITION]. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is in good condition or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030016 |  |  | Large Quantity Generator: Hazardous Waste Container Incompatible with Material Stored | Failure to accumulate or store hazardous waste in container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.172 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 39 | Hazardous Waste Management | Container Management | Hazardous waste accumulated in lined and/or compatible containers | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to accumulate or store hazardous waste in container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed in an [UNLINED / INCOMPATIBLE] container. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is compatible with the hazardous waste or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030018 |  |  | Large Quantity Generator: Open Hazardous Waste Container | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.173 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 40 | Hazardous Waste Management | Container Management | Containers of hazardous waste closed except when adding or removing waste | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed open. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that the container listed above has been properly closed. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030020 |  |  | Large Quantity Generator: Weekly Hazardous Waste Storage Areas Inspection | Failure to inspect weekly, areas where hazardous waste containers are stored or transferred. The owner or operator shall look for leaking containers and for deterioration of containers and the containment system caused by corrosion or other factors. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.174 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 41 | Hazardous Waste Management | Container Management | Inspects all hazardous waste containers at least weekly | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to inspect weekly, areas where hazardous waste containers are stored or transferred. The owner or operator shall look for leaking containers and for deterioration of containers and the containment system caused by corrosion or other factors. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed [LEAKING / DETERIORATING]. CORRECTIVE ACTION: Submit a copy of the inspection log to the CUPA demonstrating that the hazardous waste storage area is being inspected weekly. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030021 |  |  | Large Quantity Generator: Reactive and Ignitable Waste 15 meters (50 feet) from Property Line | Failure to locate reactive and ignitable waste at least 15 meters (50 feet) from the facility's property line. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.176 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 42 | Hazardous Waste Management | Container Management | Reactive and ignitable waste containers located at least 50 ft from property line | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to locate reactive and ignitable waste at least 15 meters (50 feet) from the facility's property line. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [HAZARDOUS WASTES] located in the [LOCATION] were observed closer than 50 feet from the property line. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that all containers holding ignitable or reactive waste are stored at least 50 feet from the property line. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030023 |  |  | Large Quantity Generator: Incompatible Waste Storage | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.17(b), 66265.177 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 43 | Hazardous Waste Management | Container Management | Incompatible waste in containers managed properly to prevent a reaction | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [LIST HAZARDOUS WASTES] located in the [LOCATION] are not compatible and were observed stored in a manner that could result a reaction. CORRECTIVE ACTION: Transfer or separate the containers of incompatible wastes noted above to other compatible containers or by separating containers to prevent a reaction and submit photos to the CUPA demonstrating compliance. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030061 |  |  | Large Quantity Generator: Air Emissions for Waste in Containers | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.178 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 44 | Hazardous Waste Management | Container Management | Complied with air emission requirements for HW in containers | 60 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with air emission requirements for HW in containers as specified in articles 27, 28, and 28.5 of chapter 15. |  |  | OBSERVATION: The facility Owner/Operator failed to meet air emission requirements for hazardous waste containers as observed by [ENTER SPECIFIC OBSERVATIONS]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the air emission requirements specified in articles 27, 28, and 28.5 of chapter 15 have been met. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030056 |  |  | Hazardous Waste Generator: Hazardous Waste Tank Label | Failure to label stationary hazardous waste tanks as "hazardous waste" and mark with an accumulation start date. | 22 CCR 12 66262.34(f) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 46 | Hazardous Waste Management | Tank Management | Stationary tanks marked as "Hazardous Waste" and marked with accumulation start date | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to label stationary hazardous waste tanks as "hazardous waste" and mark with an accumulation start date. |  |  | OBSERVATION: The [HAZARDOUS WASTE] tank was observed without a label. CORRECTIVE ACTION: Submit a photo to the CUPA demonstrating that the [HAZARDOUS WASTE] tank has been properly labeled. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030025 |  |  | Small Quantity Generator: Hazardous Waste Tank Spill Control/Overfill | Failure to equip a continuously fed hazardous waste tank with a means to stop the inflow (e.g., waste feed cutoff system or by-pass system to a stand-by tank). | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(3), 265.201(b)(4) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 47 | Hazardous Waste Management | Tank Management | Continuously fed hazardous waste tanks are equipped with an overfill protection device | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to equip a continuously fed hazardous waste tank with a means to stop the inflow (e.g., waste feed cutoff system or by-pass system to a stand-by tank). |  |  | OBSERVATION: An overfill protection device on the continuously fed [HAZARDOUS WASTE] tank has not been provided. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the [HAZARDOUS WASTE] tank has been equipped with an overfill prevention device. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030027 |  |  | Small Quantity Generator: Daily Tank, Monitoring, and Discharge Inspection | Failure to inspect hazardous waste tanks at least once each operating day for the following, when present: (1) Discharge control equipment (e.g., waste feed cutoff systems, by-pass systems, and drainage systems) to ensure that it is in good working order; (2) Data gathered from monitoring equipment (e.g., pressure and temperature gauges) to ensure that the tank is being operated according to its design; (3) The level of waste in the tank. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(3), 265.201(c)(1), 265.201(c)(2), 265.201(c)(3) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 48 | Hazardous Waste Management | Tank Management | Daily inspections of the hazardous waste tank systems conducted | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to inspect hazardous waste tanks at least once each operating day for the following, when present: (1) Discharge control equipment (e.g., waste feed cutoff systems, by-pass systems, and drainage systems) to ensure that it is in good working order; (2) Data gathered from monitoring equipment (e.g., pressure and temperature gauges) to ensure that the tank is being operated according to its design; (3) The level of waste in the tank. |  |  | OBSERVATION: Daily hazardous waste tank inspections for the [HAZARDOUS WASTE] tank have not been conducted. CORRECTIVE ACTION: Conduct daily inspections of the hazardous waste tank according to the requirements identified above and submit a copy of the documentation to the CUPA. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030028 |  |  | Small Quantity Generator: Weekly Hazardous Waste Tank Construction and System Fixture Inspection | Failure to inspect hazardous waste tanks for the following, when present: 1) The construction materials of the tank at least weekly to detect corrosion or leaking of fixtures or seams. 2) The construction materials of, and the area immediately surrounding, discharge confinement structures (e.g., dikes) at least weekly to detect erosion or obvious signs of leakage (e.g., wet spots or dead vegetation). | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(3), 265.201(c)(4), 265.201(c)(5) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 49 | Hazardous Waste Management | Tank Management | Weekly inspections of the hazardous waste tank system conducted | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to inspect hazardous waste tanks for the following, when present: 1) The construction materials of the tank at least weekly to detect corrosion or leaking of fixtures or seams. 2) The construction materials of, and the area immediately surrounding, discharge confinement structures (e.g., dikes) at least weekly to detect erosion or obvious signs of leakage (e.g., wet spots or dead vegetation). |  |  | OBSERVATION: OBSERVATION: Weekly hazardous waste tank inspections for the [HAZARDOUS WASTE] tank have not been conducted. CORRECTIVE ACTION: Conduct weekly inspections of the hazardous waste tank according to the requirements identified above and submit a copy of the documentation to the CUPA. | [6 empty] | Yes | No
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050007 |  |  | Small Quantity Generator: Hazardous Waste Facility Closure | Failure to remove all hazardous waste from tanks, discharge control equipment, and discharge confinement structures upon closure of the facility. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(3), 265.201(f) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 50 | Hazardous Waste Management | Tank Management | Removed hazardous waste from tanks, equipment, and discharge confinement structures upon closure | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to remove all hazardous waste from tanks, discharge control equipment, and discharge confinement structures upon closure of the facility. |  |  | OBSERVATION: The [HAZARDOUS WASTE] has not been removed from the hazardous waste tank, discharge control equipment, and discharge confinement structures upon closure. CORRECTIVE ACTION: Submit manifests/receipts demonstrating [HAZARDOUS WASTE] has been removed from the tank, discharge control equipment, and discharge confinement structures. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030024 |  |  | Small Quantity Generator: Tank 2ft Freeboard | Failure to operate uncovered tanks to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system, or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(3), 265.201(b)(3) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 51 | Hazardous Waste Management | Tank Management | Uncovered hazardous waste tanks have 2 feet of freeboard unless equipped with adequate containment | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to operate uncovered tanks to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system, or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. |  |  | OBSERVATION: The uncovered [HAZARDOUS WASTE] tank does not contain 2 feet of freeboard and is not equipped with a containment structure, drainage control system, or diversion structure. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank is covered or meets the requirements identified above. | [6 empty] | Yes | No
Hazardous Waste Generator | Administration/Documentation | 3010025 |  |  | Large Quantity Generator: New Hazardous Waste Tank System P.E. Certification | Failure to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service. The written assessment shall state that, the new hazardous waste tank system has sufficient structural integrity, is acceptable for the transferring, storing and treating of hazardous waste, and that the tanks and containment system including the foundation, structural support, seams, connections, and pressure controls (if applicable) are suitably designed to meet the regulation. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.192(a) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 52 | Hazardous Waste Management | Tank Management | Obtained a written hazardous waste tank system assessment prior to placing into use | 83 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service. The written assessment shall state that, the new hazardous waste tank system has sufficient structural integrity, is acceptable for the transferring, storing and treating of hazardous waste, and that the tanks and containment system including the foundation, structural support, seams, connections, and pressure controls (if applicable) are suitably designed to meet the regulation. |  |  | OBSERVATION: A written hazardous waste tank assessment has not been obtained for the [HAZARDOUS WASTE] tank system prior to placing system into service. CORRECTIVE ACTION: Obtain a written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192 and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010032 |  |  | Large Quantity Generator: Reassessment for Hazardous Waste Tank System P.E. Certification | Failure of generator to obtain assessment or reassessment every five (5) years or the remaining service life of the tank system, as stated in the engineer's assessment, whichever is less. This assessment applies to onground or aboveground tank systems containing only non-RCRA hazardous wastes generated onsite, or for a small quantity generator onground or aboveground tank systems containing RCRA hazardous wastes generated onsite. | 22 CCR 15 66265.192(h) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 53 | Hazardous Waste Management | Tank Management | Written hazardous waste tank system assessment/reassessment by P.E. completed | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of generator to obtain assessment or reassessment every five (5) years or the remaining service life of the tank system, as stated in the engineer's assessment, whichever is less. This assessment applies to onground or aboveground tank systems containing only non-RCRA hazardous wastes generated onsite, or for a small quantity generator onground or aboveground tank systems containing RCRA hazardous wastes generated onsite. |  |  | OBSERVATION: A hazardous waste tank reassessment has not been conducted for the [HAZARDOUS WASTE] tank system within 5 years of the previous tank system assessment or within the remaining service life of the tank system as stated in the engineer's report, whichever is less. CORRECTIVE ACTION: Obtain a written hazardous waste tank system reassessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192 and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010026 |  |  | Large Quantity Generator: New Tank Assessment Standards | Failure to include all required information in the tank system assessment. | 22 CCR 15 66265.192(k) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 54 | Hazardous Waste Management | Tank Management | Written hazardous waste tank system assessment meets all requirements | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to include all required information in the tank system assessment. |  |  | OBSERVATION: The written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system did not include the following: [LIST] CORRECTIVE ACTION: Revise the written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192(k) and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030026 |  |  | Large Quantity Generator: Hazardous Waste Tank Standards | Failure to comply with general tank operating requirements: (a) Hazardous wastes or treatment reagents shall not be placed in a tank system if they could cause the tank, its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail; (b) The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: (1) spill prevention controls (e.g., check valves, dry discount couplings); (2) overfill prevention controls (e.g., level sensing devices, high level alarms, automatic feed cutoff, or bypass to a standby tank); and (3) maintenance of sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., standby tank with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank). | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.194 | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 55 | Hazardous Waste Management | Tank Management | Tanks are compatible with hazardous waste and have spill/overflow prevention provided | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to comply with general tank operating requirements: (a) Hazardous wastes or treatment reagents shall not be placed in a tank system if they could cause the tank , its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail; (b) The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: (1) spill prevention controls (e.g., check valves, dry discount couplings); (2) overfill prevention controls (e.g., level sensing devices, high level alarms, automatic feed cutoff, or bypass to a standby tank); and (3) maintenance of sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. (Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., standby tank with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank). |  |  | OBSERVATION: Owner/Operator failed to comply with general tank operating requirements by either, placing wastes or treatment reagents into tank system that caused or could cause the tank, its ancillary equipment, or secondary containment to rupture, leak, corrode, or otherwise fail, and/or by failing to use appropriate controls/practices to prevent spills and overflows from tank system, such as check valves, dry discount couplings, level sensing devices, high level alarms, automatic feed cutoff or bypass to standby tank. For uncovered hazardous waste tanks owner/operator failed to maintain 2 ft of freeboard on tanks not equipped with secondary containment. CORRECTIVE ACTION: Correct the violations noted and/or equip waste tank as needed to comply with spill and overfill prevention requirements. Submit photos/documentation to the CUPA demonstrating that the tank or secondary containment system meets all requirements identified above. | OBSERVATION: The [HAZARDOUS WASTE] tank system is not compatible with [HAZARDOUS WASTE] observed accumulating in the tank system. Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] has been removed from the tanks system and has been placed in compatible containers/tanks. | [5 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030041 |  |  | Large Quantity Generator: Secondary Containment | Failure to meet required secondary containment requirements for hazardous waste tank systems or components. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.193 | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 56 | Hazardous Waste Management | Tank Management | Secondary containment provided and meets requirements for all hazardous waste tank systems | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to meet required secondary containment requirements for hazardous waste tank systems or components. |  |  | OBSERVATION: Secondary containment is not provided for the [HAZARDOUS WASTE] tank system. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating that secondary containment has been provided for the [HAZARDOUS WASTE] tank system and is in accordance with the requirements of 22 CCR 15 66265.193. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030029 |  |  | Large Quantity Generator: Hazardous Waste Tank Inspections | Failure to conduct and document inspections of hazardous waste tank systems each operating day and retain records of those inspections at the facility. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.195(a), 66265.195(c) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 57 | Hazardous Waste Management | Tank Management | Conducts/documents daily inspections of hazardous waste tank system | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to conduct and document inspections of hazardous waste tank systems each operating day and retain records of those inspections at the facility. |  |  | OBSERVATION: Daily inspections of the [HAZARDOUS WASTE] tank system have not been conducted and documented. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank system is being properly inspected and documented. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030042 |  |  | Large Quantity Generator: Hazardous Waste Tank Cathodic Inspection | Failure to inspect cathodic protection systems, if present, according to the following schedule to ensure that they are functioning properly: (1) the proper operation of the cathodic protection system shall be confirmed within six months after initial installation, and annually thereafter; and (2) all sources of impressed current shall be inspected and/or tested, as appropriate, at least bimonthly (i.e., every other month). (c) The owner or operator shall document in the operating record of the facility an inspection of the above items. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.195(b), 66265.195(c) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 58 | Hazardous Waste Management | Tank Management | Inspect/document the HW tank system cathodic protection system annually/impressed current bimonthly | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to inspect cathodic protection systems, if present, according to the following schedule to ensure that they are functioning properly: (1) the proper operation of the cathodic protection system shall be confirmed within six months after initial installation, and annually thereafter; and (2) all sources of impressed current shall be inspected and/or tested, as appropriate, at least bimonthly (i.e., every other month). (c) The owner or operator shall document in the operating record of the facility an inspection of the above items. |  |  | OBSERVATION: Annual cathodic protection and bimonthly impressed current inspections of the [HAZARDOUS WASTE] tank system have not been conducted and documented. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank system has been inspected for cathodic protection and all sources of impressed current. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010027 |  |  | Large Quantity Generator: Hazardous Waste Tank Equipment Replacement | Failure to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). | 22 CCR 15 66265.192(m) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 59 | Hazardous Waste Management | Tank Management | Obtained approval before replacement of identical/equivalent tank system parts not in 66265.192(l) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). |  |  | OBSERVATION: Owner/Operator failed to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). CORRECTIVE ACTION: Provide CUPA with documentation on the tank system parts or components that have been replaced. CUPA will then determine if a new written hazardous waste tank system assessment for the tank system is required. | [6 empty] | No | Yes
Hazardous Waste Generator | Release/Leaks/Spills | 3040001 |  |  | Large Quantity Generator: Hazardous Waste Tank Release | Failure to immediately remove from service a tank system or secondary containment system from which there has been a leak, spill, is unfit for use and comply with applicable requirements. | 22 CCR 15 66265.196 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 60 | Hazardous Waste Management | Tank Management | Leaking/unfit HW tank or secondary containment removed from service | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to immediately remove from service a tank system or secondary containment system from which there has been a leak, spill, is unfit for use and comply with applicable requirements. |  |  | OBSERVATION: Owner/Operator failed to immediately remove from service a hazardous waste tank system or secondary containment system from which there has been a leak, spill, or is unfit for use, and comply with applicable requirements. CORRECTIVE ACTION: Immediately remove the [HAZARDOUS WASTE] tanks system from service. Submit documentation to the CUPA demonstrating that all requirements in 22 CCR 15 66265.196 have been met. | [6 empty] | No | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050006 |  |  | Large Quantity Generator: Tank Closure Requirements and Documentation | Failure of owner or operator to properly close a hazardous waste tank system ensuring the minimization of further maintenance and that the required requirements have been met. | 22 CCR 15 66265.111, 66265.114, 66265.197 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 61 | Hazardous Waste Management | Tank Management | All hazardous waste tank system closure requirements have been met. | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of owner or operator to properly close a hazardous waste tank system ensuring the minimization of further maintenance and that the required requirements have been met. |  |  | OBSERVATION: Owner/Operator failed to properly close hazardous waste tank system. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the hazardous waste tank system has been closed in accordance with the requirements of 22 CCR 15 66265.197, and facility has complied with the requirements of 22 CCR 15 66265.111. and 66265.114. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030062 |  |  | Large Quantity Generator: Air Emissions for Wastes in Tanks | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.202 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 62 | Hazardous Waste Management | Tank Management | Complied with air emissions requirements for HW in tanks | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with air emission requirements for HW in tanks as specified in articles 27, 28, and 28.5 of chapter 15. |  |  | OBSERVATION: The facility Owner/Operator failed to meet the air emission requirements for hazardous waste tanks as observed by [ENTER SPECIFIC OBSERVATIONS]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the air emission requirements specified in articles 27, 28, and 28.5 of chapter 15 have been met. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010022 |  |  | Small Quantity Generator: Emergency Plan | Failure to post the following information next to the telephone: (A) The name and telephone number of the emergency coordinator; (B) Location of fire extinguishers and spill control material, and, if present, fire alarm; and (C) The telephone number of the fire department, unless the facility has a direct alarm. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(5)(ii) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 76 | General Facility Operations | Site Safety | Posted emergency information next to the telephone | 50 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to post the following information next to the telephone: (A) The name and telephone number of the emergency coordinator; (B) Location of fire extinguishers and spill control material, and, if present, fire alarm; and (C) The telephone number of the fire department, unless the facility has a direct alarm. |  |  | OBSERVATION: Emergency information is not posted next to the telephone. CORRECTIVE ACTION: Complete and post all required emergency information next to the telephone. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030039 |  |  | Small Quantity Generator: Emergency Coordinator | Failure to have at least one employee either on the premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(5)(i) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 77 | General Facility Operations | Site Safety | Emergency coordinator on the premises or on call | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have at least one employee either on the premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. |  |  | OBSERVATION: An emergency coordinator was not on the premises or available on call. CORRECTIVE ACTION: Submit documentation to this office demonstrating that at least one employee is either on the premises or on call with the responsibility for coordinating all emergency response measures. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030032 |  |  | Small Quantity Generator: Facility Emergency Equipment | Failure of the facility to maintain the following emergency equipment or equivalents: 1) An internal communications or alarm system; 2) A device, such as a telephone (immediately available at the scene of Operations/ Maintenance ) or a hand-held two-way radio, capable of summoning emergency assistance from local police departments, fire departments, or State or local emergency response teams; 3) Portable fire extinguishers, fire control equipment, spill control equipment, and decontamination equipment; and 4) Water at adequate volume and pressure to supply water hose streams, or foam producing equipment, or automatic sprinklers, or water spray systems. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(4), 265.32 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 78 | General Facility Operations | Site Safety | Facility equipped with all required emergency equipment | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the facility to maintain the following emergency equipment or equivalents: 1) An internal communications or alarm system; 2) A device, such as a telephone (immediately available at the scene of Operations/ Maintenance ) or a hand-held two-way radio, capable of summoning emergency assistance from local police departments, fire departments, or State or local emergency response teams; 3) Portable fire extinguishers, fire control equipment, spill control equipment, and decontamination equipment; and 4) Water at adequate volume and pressure to supply water hose streams, or foam producing equipment, or automatic sprinklers, or water spray systems. |  |  | OBSERVATION: The facility has not been equip with [LIST EQUIPMENT]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the facility has been equip with [LIST EQUIPMENT]. to the CUPA within [# days]. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030034 |  |  | Small Quantity Generator: Emergency Equipment Maintenance | Failure to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(4), 265.33 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 79 | General Facility Operations | Site Safety | Tests and maintains all required safety equipment at the facility | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. |  |  | OBSERVATION: [LIST EQUIPMENT] has not been tested and maintained to assure its proper operation in time of emergency. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating [LIST EQUIPMENT] has been properly tested or maintained. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030036 |  |  | Small Quantity Generator: Aisle Space | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless aisle space is not needed for any of these purposes. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(4), 265.35 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 80 | General Facility Operations | Site Safety | Maintains adequate aisle space | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless aisle space is not needed for any of these purposes. |  |  | OBSERVATION: The hazardous waste storage area located in the [LOCATION] did not have adequate aisle space allowing for unobstructed movement. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that adequate aisle space has been provided. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030030 |  |  | Small Quantity Generator: Facility Maintained to Prevent Fire/Explosion/Release | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(4), 265.31 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 81 | General Facility Operations | Site Safety | Maintains and operates the facility to minimize the possibility of fire/explosion/release | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. |  |  | OBSERVATION: [HAZARDOUS WASTE] was observed [DESCRIBE SPILL] in the [LOCATION]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the spill has been properly removed and managed. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030063 |  |  | Large Quantity Generator: Emergency Coordinator | Failure to have at least one employee either on the facility premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.55 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 82 | General Facility Operations | Site Safety | Emergency coordinator on the premises or on call | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have at least one employee either on the facility premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. |  |  | OBSERVATION: An emergency coordinator was not on the premises or available on call. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that at least one employee is either on the premises or on call with the responsibility for coordinating all emergency response measures. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030033 |  |  | Large Quantity Generator: Facility Emergency Equipment | Failure of the facility to maintain the following emergency equipment or equivalents: 1) An internal communications or alarm system; 2) A device, such as a telephone (immediately available at the scene of Operations/ Maintenance ) or a hand-held two-way radio, capable of summoning emergency assistance from local police departments, fire departments, or State or local emergency response teams; 3) Portable fire extinguishers, fire control equipment, spill control equipment, and decontamination equipment; and 4) Water at adequate volume and pressure to supply water hose streams, or foam producing equipment, or automatic sprinklers, or water spray systems. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.32 | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 83 | General Facility Operations | Site Safety | Facility equipped with all required emergency equipment | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the facility to maintain the following emergency equipment or equivalents: 1) An internal communications or alarm system; 2) A device, such as a telephone (immediately available at the scene of Operations/ Maintenance ) or a hand-held two-way radio, capable of summoning emergency assistance from local police departments, fire departments, or State or local emergency response teams; 3) Portable fire extinguishers, fire control equipment, spill control equipment, and decontamination equipment; and 4) Water at adequate volume and pressure to supply water hose streams, or foam producing equipment, or automatic sprinklers, or water spray systems. |  |  | OBSERVATION: The facility has not been equip with [LIST EQUIPMENT]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the facility has been equip with [LIST EQUIPMENT]. to the CUPA within [# days]. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030035 |  |  | Large Quantity Generator: Emergency Equipment Maintenance | Failure to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.33 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 84 | General Facility Operations | Site Safety | Tests and maintains all required safety equipment at the facility | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. |  |  | OBSERVATION: [LIST EQUIPMENT] has not been tested and maintained to assure its proper operation in time of emergency. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating [LIST EQUIPMENT] has been properly tested or maintained. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030037 |  |  | Large Quantity Generator: Aisle Space | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless it can be demonstrated to the Department that aisle space is not needed for any of these purposes. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.35 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 85 | General Facility Operations | Site Safety | Maintains adequate aisle space | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless it can be demonstrated to the Department that aisle space is not needed for any of these purposes. |  |  | OBSERVATION: The hazardous waste storage area located in the [LOCATION] did not have adequate aisle space allowing for unobstructed movement. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that adequate aisle space has been provided. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030031 |  |  | Large Quantity Generator: Facility Maintained To Prevent Fire/Explosion/Release | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.31 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 86 | General Facility Operations | Site Safety | Maintains and operates the facility to minimize the possibility of fire/explosion/release | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. |  |  | OBSERVATION: [HAZARDOUS WASTE] was observed [DESCRIBE SPILL] in the [LOCATION]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the spill has been properly removed and managed. | [6 empty] | No | Yes
Hazardous Waste Generator | Release/Leaks/Spills | 3040004 |  |  | Universal Waste Handler: Release | Failure of the universal waste handler of PV modules electronic devices, CRTs, and CRT glass to prevent the release of the universal waste to the environment under reasonable conditions by the following methods: 1) Immediately clean spills and leaks of universal wastes; and 2) Place all universal waste spills and leaks in containers that are structurally sound and compatible with the universal waste. | 22 CCR 23 66273.33.5, 66273.33.6 | 2021-08-02 | 2024-09-30 | 2024-09-30 | Revised | 99 | Universal Waste | UW Management | UWH properly cleaned up and contained spills of PV modules, electronic devices, CRTs and CRT glass | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the universal waste handler of PV modules electronic devices, CRTs, and CRT glass to prevent the release of the universal waste to the environment under reasonable conditions by the following methods: 1) Immediately clean spills and leaks of universal wastes; and 2) Place all universal waste spills and leaks in containers that are structurally sound and compatible with the universal waste. |  |  | OBSERVATION: Failure of Universal Waste Handler of PV modules, electronic devices, CRTs and/or CRT glass to prevent the release of universal waste to the environment by failing to immediately clean spills and leaks of universal wastes and/or by placing spilled/leaked waste in containers that are not structurally sound and compatible with the waste. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the spilled PV modules, electronic devices, CRTs and/or CRT glass have been properly removed/cleaned up and managed. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010 |  |  | HW-Administration/Documentation - General | Administration/Documentation - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 101 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes | Yes
Hazardous Waste Generator | Training | 3020 |  |  | HW-Training - General | Training - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 103 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030 |  |  | HW-Operations/Maintenance - General | Operations/Maintenance - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 105 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes | Yes
Hazardous Waste Generator | Release/Leaks/Spills | 3040 |  |  | HW-Release/Leaks/Spills - General | Release/Leaks/Spills - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 107 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050 |  |  | HW-Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 109 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes | Yes

## HHW
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | PHHWCF | THHWCF
Household Hazardous Waste Program | Administration/Documentation | 3310 |  |  | HHW-Administration/Documentation - General | Administration/Documentation - General | 22 CCR Multiple Chapters Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 51 | General Facility Requirements |  | Administration/Documentation - General | 38 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Administration/Documentation - General | [9 empty] | yes | yes
Household Hazardous Waste Program | Training | 3320 |  |  | HHW-Training - General | Training - General | 22 CCR Multiple Chapters Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 53 | General Facility Requirements |  | Training - General | 18 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Training - General | [9 empty] | yes | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330 |  |  | HHW-Operations/Maintenance - General | Operations/Maintenance - General | 22 CCR Multiple Chapters Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 55 | General Facility Requirements |  | Operations/Maintenance - General | 32 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Operations/Maintenance - General | [9 empty] | yes | yes
Household Hazardous Waste Program | Release/Leaks/Spills | 3340 |  |  | HHW-Release/Leaks/Spills - General | Release/Leaks/Spills - General | 22 CCR Multiple Chapters Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 57 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes | Yes
Household Hazardous Waste Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 3350 |  |  | HHW-Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 22 CCR Multiple Chapters Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 59 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | yes | yes

## TP
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | TP full list | TP CA | TP CECL | TP CEL | TP CESQT | TP CESW | TP PBR
Tiered Permitting | Administration/Documentation | 3210 |  |  | Tiered Permitting - Administration/Documentation - General | Administration/Documentation - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 65 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Training | 3220 |  |  | Tiered Permitting - Training - General | Training - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 67 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Operations/Maintenance | 3230 |  |  | Tiered Permitting - Operations/Maintenance - General | Operations/Maintenance - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 69 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Release/Leaks/Spills | 3240 |  |  | Tiered Permitting - Release/Leaks/Spills - General | Release/Leaks/Spills - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 71 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Abandonment/Illegal Disposal/Unauthorized Treatment | 3250 |  |  | Tiered Permitting - Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 73 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## RCRA
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | RCRA LQG
RCRA Large Quantity Generator | Administration/Documentation | 3110001 |  | 262.A | RCRA: EPA ID Number | Failure to obtain an Identification Number prior to treating, storing, disposing of, transporting or offering for transportation any hazardous waste. | 22 CCR 12 66262.12 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 1 | Recordkeeping/ Documentation | ID Number | Obtained an Identification Number (unless exempted HSC 25143.13) | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain an Identification Number prior to treating, storing, disposing of, transporting or offering for transportation any hazardous waste. |  |  | OBSERVATION: The generator has not obtained an Identification Number to manage hazardous waste. A hazardous waste generator shall not treat, store, dispose of, transport or offer for transportation, hazardous waste without obtaining an Identification Number. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you have obtained an Identification Number. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130018 |  | 262.C | RCRA: Contingency Plan | Failure to prepare and implement a written Contingency Plan to minimize hazards to human health or the environment from fires, explosions, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.51 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 2 | Recordkeeping/ Documentation | Contingency Plan | Contingency Plan prepared and implemented | 41 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare and implement a written Contingency Plan to minimize hazards to human health or the environment from fires, explosions, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water. |  |  | OBSERVATION: Facility failed to prepare an Contingency Plan. The owner or operator shall prepare an Emergency Response Plan designed to minimize hazards to human health or the environment from fires, explosions, or any unplanned release of hazardous waste to air, soil, or surface water. CORRECTIVE ACTION: Immediately prepare an Contingency Plan and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110012 |  | 262.D | RCRA: Contingency Plan Copies | Failure to maintain a copy of the contingency plan and all its revisions at the facility and to submit a copy to all local police departments, fire departments, hospitals, and State and local emergency response teams that may be called upon to provide emergency services. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.53 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 3 | Recordkeeping/ Documentation | Contingency Plan | Contingency Plan and all revisions maintained at the facility | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain a copy of the contingency plan and all its revisions at the facility and to submit a copy to all local police departments, fire departments, hospitals, and State and local emergency response teams that may be called upon to provide emergency services. |  |  | OBSERVATION: A copy of the Contingency Plan is not maintained at the facility. CORRECTIVE ACTION: Locate a copy of the Contingency Plan, maintain it at the facility, and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110011 |  | 262.C | RCRA: Contingency Plan Emergency Action Plan | Failure to include all of the following in the Contingency Plan: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. (If the owner or operator has already prepared a Spill Prevention, Control, and Countermeasures (SPCC) Plan or some other emergency or contingency plan, the owner or operator need only amend that plan to incorporate hazardous waste management provisions.) | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.52 | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 4 | Recordkeeping/ Documentation | Contingency Plan | Contingency plan contains all required content | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include all of the following in the Contingency Plan: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. (If the owner or operator has already prepared a Spill Prevention, Control, and Countermeasures (SPCC) Plan or some other emergency or contingency plan, the owner or operator need only amend that plan to incorporate hazardous waste management provisions.) |  |  | OBSERVATION: The Contingency Plan does not contain one or more of the following: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. CORRECTIVE ACTION: Revise the Contingency Plan to include all the content required by 22 CCR 15 66265.52 and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Training | 3120001 |  | 262.A | RCRA: Employee Hazardous Waste Training | Failure to provide employees with hazardous waste training program of class room instructions or on-the-job training within the first six months after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. Training records on current personnel shall be kept until closure of the facility and for former employees the record shall be kept for at least three years from the date the employee last worked at the facility. The records shall include the following: the job title for each position at the facility related to hazardous waste management, and the name of the employee filling each job; a written job description for each position, duties of facility personnel assigned to each position, and a written description of the type and amount of both introductory and continuing training that will be given to each person filling a position. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.16 | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 5 | Recordkeeping/ Documentation | Training | Trained facility personnel annually and maintained required documentation until closure | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide employees with hazardous waste training program of class room instructions or on-the-job training within the first six months after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. Training records on current personnel shall be kept until closure of the facility and for former employees the record shall be kept for at least three years from the date the employee last worked at the facility. The records shall include the following: the job title for each position at the facility related to hazardous waste management, and the name of the employee filling each job; a written job description for each position, duties of facility personnel assigned to each position, and a written description of the type and amount of both introductory and continuing training that will be given to each person filling a position. |  |  | OBSERVATION: As demonstrated by the hazardous waste violations observed at the time of inspection, personnel are not adequately trained to perform their duties in a way that ensures the facility's compliance with the requirements of this chapter, and/or proper training documentation has not been maintained. CORRECTIVE ACTION: Conduct training with applicable personnel and document it according to the requirements of 22 CCR 15 66265.16(d). Submit a copy of the documentation to the CUPA. | OBSERVATION: Documented training of personnel was not available at the time of inspection. CORRECTIVE ACTION: Locate training documentation or conduct training with applicable personnel and document it. Submit a copy of the training documentation to the CUPA. | [5 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130002 |  | 262.C | RCRA: Land Disposal Restriction | Failure to determine whether waste is restricted from land disposal. | 22 CCR 12 66262.34(a)(4); 22 CCR 18 66268.7(a) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 16 | Recordkeeping/ Documentation | Waste Determination | Determined land disposal restrictions for hazardous waste | 57 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to determine whether waste is restricted from land disposal. |  |  | OBSERVATION: Land Disposal Restriction (LDR) documentation for [HAZARDOUS WASTE] was not available at the time of inspection. CORRECTIVE ACTION: Submit LDR documentation for [HAZARDOUS WASTE] to the CUPA. Retain the documentation at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. | [6 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150003 |  |  | Improper Disposal of Hazardous Waste | Failure to dispose of hazardous waste at a facility which has a permit from DTSC or disposing of hazardous waste at any point which is not authorized. | HSC 6.5 25189.5(a), 25201(a) | 2021-08-02 | 2024-09-30 | 2024-09-30 | Revised | 25 | Hazardous Waste Management | Disposal | Disposed of hazardous waste at an authorized location | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to dispose of hazardous waste at a facility which has a permit from DTSC or disposing of hazardous waste at any point which is not authorized. |  |  | OBSERVATION: Owner/Operator failed to dispose of hazardous waste at a facility which has a permit from DTSC or disposed of hazardous waste at a point which is not authorized pursuant to HSC chapter 6.5. CORRECTIVE ACTION: Immediately discontinue disposing of hazardous waste at any facility not permitted by DTSC or to any point which is not authorized pursuant to HSC chapter 6.5. Submit a statement to the CUPA indicating improperly disposed of hazardous waste has been properly managed, and that all hazardous wastes will only be disposed at facilities permitted by DTSC in the future. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130004 |  | 262.C | RCRA: Hazardous Waste Accumulation Time Exceeded | Failure to send hazardous waste offsite for treatment, storage, or disposal within 90 days for a generator who generates 1000 kilograms or more of RCRA hazardous waste or one kilogram of acute hazardous waste per month. | 22 CCR 12 66262.34(a) (c); HSC 6.5 25123.3(b)(1) | 2021-08-02 | 2024-09-30 | 2024-09-30 | Revised | 27 | Hazardous Waste Management | Accumulation Time Limits | Disposed of hazardous waste within 90 days of accumulation start date | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to send hazardous waste offsite for treatment, storage, or disposal within 90 days for a generator who generates 1000 kilograms or more of RCRA hazardous waste or one kilogram of acute hazardous waste per month. |  |  | OBSERVATION: Owner/Operator failed to send hazardous waste offsite for treatment, storage, or disposal within 90 days of accumulation start date. CORRECTIVE ACTION: Dispose of hazardous waste and submit a copy of the manifest/receipt to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130023 |  | 262.C | RCRA: Hazardous Waste Generator: Satellite Accumulation | Failure to meet the following conditions of satellite accumulation regulations: • Accumulate up to 55 gallons of hazardous waste or one quart of acute hazardous waste at or near the initial point of accumulation which was under the control of the operator. • Total time hazardous waste can be accumulated onsite in any generator accumulation area is either one year from the initial date of accumulation, or 90 days from the date on which the quantity limitation of 55 gallons of hazardous waste or one quart of acutely hazardous waste is reached, whichever comes first. • The generator complies with sections 66265.171, 66264.172, and 66265.173(a). • The container must be clearly marked with the initial date that hazardous waste is first placed in the container and labelled with the words “Hazardous Waste” including specified information. • Container must be labelled with the date the satellite accumulation limit is reached and moved within three days after reaching the 55 gallon (or one quart) limit to a central accumulation area. • 55 gallons (or one quart of acute hazardous waste) of waste per process may be accumulated. | 22 CCR 12 66262.34(e) | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 28 | Hazardous Waste Management | Accumulation Time Limits | Met all requirements for hazardous waste satellite accumulation | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1I | Yes |  | 30 | Failure to meet the following conditions of satellite accumulation regulations: • Accumulate up to 55 gallons of hazardous waste or one quart of acute hazardous waste at or near the initial point of accumulation which was under the control of the operator. • Total time hazardous waste can be accumulated onsite in any generator accumulation area is either one year from the initial date of accumulation, or 90 days from the date on which the quantity limitation of 55 gallons of hazardous waste or one quart of acutely hazardous waste is reached, whichever comes first. • The generator complies with sections 66265.171, 66264.172, and 66265.173(a). • The container must be clearly marked with the initial date that hazardous waste is first placed in the container and labelled with the words “Hazardous Waste” including specified information. • Container must be labelled with the date the satellite accumulation limit is reached and moved within three days after reaching the 55 gallon (or one quart) limit to a central accumulation area. • 55 gallons (or one quart of acute hazardous waste) of waste per process may be accumulated. |  |  | OBSERVATION: Failure of the Owner/Operator to comply with one or more satellite accumulation requirements [Describe as needed]. CORRECTIVE ACTION: Ensure that all hazardous wastes being accumulated pursuant to satellite accumulation meet all applicable requirements and submit documentation of compliance to the CUPA. {Describe specific corrections as needed} | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130003 |  | 262.C | RCRA: Hazardous Waste Labeling Standards | Failure to properly label hazardous waste accumulation containers with the following requirements: "Hazardous Waste", name and address of the generator, physical and chemical characteristics of the Hazardous Waste, and starting accumulation date. | 22 CCR 12 66262.34(f) | 2011-07-01 | 2024-09-30 | 2024-09-30 | Revised | 29 | Hazardous Waste Management | Container Management | Labeled all containers or portable tanks containing hazardous waste | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly label hazardous waste accumulation containers with the following requirements: "Hazardous Waste", name and address of the generator, physical and chemical characteristics of the Hazardous Waste, and starting accumulation date. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed without a hazardous waste label. CORRECTIVE ACTION: Submit a photo to the CUPA demonstrating that the container listed above has been properly labeled. | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed without the following information on the label: [LIST MISSING INFORMATION]. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that the container listed above has been properly labeled. | [5 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130005 |  | 262.C | RCRA: Container in Poor Condition or Damaged | Failure to accumulate hazardous waste in a container that is in good condition. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.171 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 30 | Hazardous Waste Management | Container Management | Accumulated hazardous waste in containers that are in good condition | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to accumulate hazardous waste in a container that is in good condition. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed [DESCRIBE CONDITION]. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is in good condition or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130006 |  | 262.C | RCRA: Hazardous Waste Container Incompatible with Material Stored | Failure to accumulate or store hazardous waste in a container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored, so that the ability of the container to contain the waste is not impaired. | 22 CCR 12 66262.34(a); 22 CCR 15 66265.172 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 31 | Hazardous Waste Management | Container Management | Hazardous waste accumulated in lined and/or compatible containers | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to accumulate or store hazardous waste in a container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored, so that the ability of the container to contain the waste is not impaired. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed in an [UNLINED / INCOMPATIBLE] container. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is compatible with the hazardous waste or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130007 |  | 262.C | RCRA: Open Hazardous Waste Container | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.173 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 32 | Hazardous Waste Management | Container Management | Containers of hazardous waste closed except when adding or removing waste | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed open. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that the container listed above has been properly closed. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130008 |  | 262.C | RCRA: Weekly Hazardous Waste Storage Areas Inspection | Failure to inspect weekly areas where hazardous waste containers are stored. The owner or operator must look for leaking containers and for deterioration of containers caused by corrosion or other factors. | 22 CCR 12 66262.34(a); 22 CCR 15 66265.174 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 33 | Hazardous Waste Management | Container Management | Inspects all hazardous waste containers at least weekly | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to inspect weekly areas where hazardous waste containers are stored. The owner or operator must look for leaking containers and for deterioration of containers caused by corrosion or other factors. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed [LEAKING / DETERIORATING]. CORRECTIVE ACTION: Submit a copy of the inspection log to the CUPA demonstrating that the hazardous waste storage area is being inspected weekly. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130009 |  | 262.C | RCRA: Reactive and Ignitable Waste 50 ft from Property Line | Failure to keep reactive and ignitable waste at least 15 meters (50 feet) from the facility's property line. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.176 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 34 | Hazardous Waste Management | Container Management | Reactive and ignitable waste containers located at least 50 ft from property line | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to keep reactive and ignitable waste at least 15 meters (50 feet) from the facility's property line. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [HAZARDOUS WASTES] located in the [LOCATION] were observed closer than 50 feet from the property line. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that all containers holding ignitable or reactive waste are stored at least 50 feet from the property line. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130010 |  | 262.C | RCRA: Incompatible Waste Storage | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.17(b), 66265.177 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 35 | Hazardous Waste Management | Container Management | Incompatible waste in containers managed properly to prevent a reaction | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [LIST HAZARDOUS WASTES] located in the [LOCATION] are not compatible and were observed stored in a manner that could result a reaction. CORRECTIVE ACTION: Transfer or separate the containers of incompatible wastes noted above to other compatible containers or by separating containers to prevent a reaction and submit photos to the CUPA demonstrating compliance. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130025 |  | 262.C | RCRA: Air Emissions for Waste in Containers | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.178 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 36 | Hazardous Waste Management | Container Management | Complied with air emission requirements for HW in containers | 60 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. |  |  | OBSERVATION: The facility Owner/Operator failed to meet air emission requirements for hazardous waste containers as observed by [ENTER SPECIFIC OBSERVATIONS]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the air emission requirements specified in articles 27, 28, and 28.5 of chapter 15 have been met. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130022 |  | 262.C | RCRA: Hazardous Waste Generator: Hazardous Waste Tank Label | Failure to label stationary hazardous waste tanks as "hazardous waste" and mark with an accumulation start date. | 22 CCR 12 66262.34(f) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 38 | Hazardous Waste Management | Tank Management | Stationary tanks marked as "Hazardous Waste" and marked with accumulation start date | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to label stationary hazardous waste tanks as "hazardous waste" and mark with an accumulation start date. |  |  | OBSERVATION: The [HAZARDOUS WASTE] tank was observed without a label. CORRECTIVE ACTION: Submit a photo to the CUPA demonstrating that the [HAZARDOUS WASTE] tank has been properly labeled. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110013 |  | 262.C | RCRA: New Hazardous Waste Tank System P.E. Certification | Failure to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service. The written assessment shall state that, the new hazardous waste tank system has sufficient structural integrity, is acceptable for the transferring, storing and treating of hazardous waste, and that the tanks and containment system including the foundation, structural support, seams, connections, and pressure controls (if applicable) are suitably designed to meet the regulation. | 22 CCR 15 66265.192(a) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 39 | Hazardous Waste Management | Tank Management | Written hazardous waste tank system assessment by P.E. completed | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service. The written assessment shall state that, the new hazardous waste tank system has sufficient structural integrity, is acceptable for the transferring, storing and treating of hazardous waste, and that the tanks and containment system including the foundation, structural support, seams, connections, and pressure controls (if applicable) are suitably designed to meet the regulation. |  |  | OBSERVATION: A written hazardous waste tank assessment has not been obtained for the [HAZARDOUS WASTE] tank system. CORRECTIVE ACTION: Obtain a written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192 and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110014 |  | 262.C | RCRA: New Tank Assessment Standards | Failure to include all required information in the new tank system assessment. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.192(k) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 40 | Hazardous Waste Management | Tank Management | Written hazardous waste tank system assessment meets all requirements | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to include all required information in the new tank system assessment. |  |  | OBSERVATION: The written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system did not include the following: [LIST] CORRECTIVE ACTION: Revise the written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192(k) and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110023 |  |  | Reassessment for Hazardous Waste Tank System P.E. Certification | Failure of generator to obtain assessment or reassessment every five (5) years or the remaining service life of the tank system, as stated in the engineer's assessment, whichever is less. This assessment applies to onground or aboveground tank systems containing only non-RCRA hazardous wastes generated onsite, or for a small quantity generator onground or aboveground tank systems containing RCRA hazardous wastes generated onsite. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.192(h) | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 41 | Hazardous Waste Management | Tank Management | Written hazardous waste tank system assessment/reassessment by P.E. completed | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of generator to obtain assessment or reassessment every five (5) years or the remaining service life of the tank system, as stated in the engineer's assessment, whichever is less. This assessment applies to onground or aboveground tank systems containing only non-RCRA hazardous wastes generated onsite, or for a small quantity generator onground or aboveground tank systems containing RCRA hazardous wastes generated onsite. |  |  | OBSERVATION: A hazardous waste tank reassessment has not been conducted for the [HAZARDOUS WASTE] tank system within 5 years of the previous tank system assessment or within the remaining service life of the tank system as stated in the engineer's report, whichever is less. CORRECTIVE ACTION: Obtain a written hazardous waste tank system reassessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192 and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130011 |  | 262.C | RCRA: Hazardous Waste Tank Standards | Failure to comply with general tank operating requirements: (a) Hazardous wastes or treatment reagents shall not be placed in a tank system if they could cause the tank , its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail. (b) The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: (1) spill prevention controls (e.g., check valves, dry discount couplings); (2) overfill prevention controls (e.g., level sensing devises, high level alarms, automatic feed cutoff, or bypass to a standby tank); and (3) maintenance of sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.194 | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 42 | Hazardous Waste Management | Tank Management | Tanks are compatible with hazardous waste and have spill/overflow prevention provided | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to comply with general tank operating requirements: (a) Hazardous wastes or treatment reagents shall not be placed in a tank system if they could cause the tank , its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail. (b) The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: (1) spill prevention controls (e.g., check valves, dry discount couplings); (2) overfill prevention controls (e.g., level sensing devises, high level alarms, automatic feed cutoff, or bypass to a standby tank); and (3) maintenance of sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. |  |  | OBSERVATION: Appropriate controls and practices are not in place to prevent spills and overflows from the [HAZARDOUS WASTE] tank or secondary containment system. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank or secondary containment system meets all requirements identified above. | OBSERVATION: The [HAZARDOUS WASTE] tank system is not compatible with [HAZARDOUS WASTE] observed accumulating in the tank system. Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] has been removed from the tanks system and has been placed in compatible containers/tanks. | [5 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130019 |  | 262.C | RCRA: Secondary Containment | Failure to meet required secondary containment requirements for hazardous waste tank systems or components. | 22 CCR 15 66265.193 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 43 | Hazardous Waste Management | Tank Management | Secondary containment provided and meets requirements for all hazardous waste tank systems | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to meet required secondary containment requirements for hazardous waste tank systems or components. |  |  | OBSERVATION: Secondary containment is not provided for the [HAZARDOUS WASTE] tank system. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating that secondary containment has been provided for the [HAZARDOUS WASTE] tank system and is in accordance with the requirements of 22 CCR 15 66265.193. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130012 |  | 262.C | RCRA: Hazardous Waste Tank Inspections | Failure to conduct and document inspections of hazardous waste tank systems each operating day and retain records of those inspections at the facility. | 22 CCR 12 66262.34 (a)(1); 22 CCR 15 66265.195(a), 66265.195(c) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 44 | Hazardous Waste Management | Tank Management | Conducts/documents daily inspections of hazardous waste tank system | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to conduct and document inspections of hazardous waste tank systems each operating day and retain records of those inspections at the facility. |  |  | OBSERVATION: Daily inspections of the [HAZARDOUS WASTE] tank system have not been conducted and documented. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank system is being properly inspected and documented. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130020 |  | 262.C | RCRA: Hazardous Waste Tank Cathodic Inspection | Failure of the owner or operator to inspect and document the cathodic protection systems to ensure the proper operation within six months after initial installation, and annually thereafter; and all sources of impressed current at least bimonthly (i.e., every other month). | 22 CCR 12 66262.34(a); 22 CCR 15 66265.195(b), 66265.195(c) | 2022-07-01 | 2024-09-30 | 2024-09-30 | Revised | 45 | Hazardous Waste Management | Tank Management | Inspect/document the HW tank system cathodic protection system annually/impressed current bimonthly | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the owner or operator to inspect and document the cathodic protection systems to ensure the proper operation within six months after initial installation, and annually thereafter; and all sources of impressed current at least bimonthly (i.e., every other month). |  |  | OBSERVATION: Annual cathodic protection and bimonthly impressed current inspections of the [HAZARDOUS WASTE] tank system have not been conducted and documented. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank system has been inspected for cathodic protection and all sources of impressed current. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110015 |  | 262.C | RCRA: Hazardous Waste Tank Equipment Replacement | Failure to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). The notification to the CUPA of replacement shall include the following: (1) Name, address, and EPA identification number of the facility; (2) Date of planned replacement; (3) Description part or component to be replaced; (4) Description of the tank system and type of waste(s) handled; (5) Description of how the part or component is identical or functionally equivalent to the part or component to be replaced. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.192(m) | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 46 | Hazardous Waste Management | Tank Management | Obtained approval before replacement of identical/equivalent tank system parts not in 66265.192(l) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). The notification to the CUPA of replacement shall include the following: (1) Name, address, and EPA identification number of the facility; (2) Date of planned replacement; (3) Description part or component to be replaced; (4) Description of the tank system and type of waste(s) handled; (5) Description of how the part or component is identical or functionally equivalent to the part or component to be replaced. |  |  | OBSERVATION: Replacement of [TANK SYSTEM PARTS] for the [HAZARDOUS WASTE] tank system were made on [DATE]. The written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system has not been updated and the generator did not contact the CUPA to determine if the tank system parts/components were identical or functionally equivalent. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the [TANK SYSTEM PARTS] are identical or functionally equivalent or revise the written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192(k) and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Release/Leaks/Spills | 3140001 |  | 262.C | RCRA: Hazardous Waste Tank Release | Failure to immediately remove from service a tank system or secondary containment system from which there has been a leak, spill, is unfit for use and comply with applicable requirements. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.196 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 47 | Hazardous Waste Management | Tank Management | Leaking/unfit HW tank or secondary containment removed from service | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to immediately remove from service a tank system or secondary containment system from which there has been a leak, spill, is unfit for use and comply with applicable requirements. |  |  | OBSERVATION: The [HAZARDOUS WASTE] tank system was observed leaking to [LOCATION] and is unfit for use. CORRECTIVE ACTION: Immediately remove the [HAZARDOUS WASTE] tanks system from service. Submit documentation to the CUPA demonstrating that all requirements in 22 CCR 15 66265.196 have been met. | [6 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150002 |  | 262.A | RCRA: Tank Closure Requirements and Documentation | Failure of owner or operator to properly close a hazardous waste tank system ensuring the minimization of further maintenance and that the required requirements have been met. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.111, 66265.114, 66265.197 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 48 | Hazardous Waste Management | Tank Management | Met all hazardous waste tank system closure requirements | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of owner or operator to properly close a hazardous waste tank system ensuring the minimization of further maintenance and that the required requirements have been met. |  |  | OBSERVATION: The [HAZARDOUS WASTE] tank system has not been properly closed. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the [HAZARDOUS WASTE] tank system has been closed in accordance with the requirements of 22 CCR 15 66265.197. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130026 |  | 262.C | RCRA: Air Emissions for wastes in Tanks | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.202 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 49 | Hazardous Waste Management | Tank Management | Complied with air emissions requirements for HW in tanks | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. |  |  | OBSERVATION: The facility Owner/Operator failed to meet the air emission requirements for hazardous waste tanks as observed by [ENTER SPECIFIC OBSERVATIONS]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the air emission requirements specified in articles 27, 28, and 28.5 of chapter 15 have been met. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130027 |  | 262.C | RCRA: Drip Pad requirements | Failure to comply with Drip Pad requirements, including but not limited to design and operating requirements, annual assessment, contingency plan, inspections, and closure requirements. | 22 CCR 12 66262.34 (a)(1)(B); 22 CCR 15 66265.440 - 66265.445 | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 50 | Hazardous Waste Management | Drip Pad | In compliance with drip pad requirements | 41 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to comply with Drip Pad requirements, including but not limited to design and operating requirements, annual assessment, contingency plan, inspections, and closure requirements. |  |  | OBSERVATION: Owner/Operator failed to comply with drip pad requirements including but not limited to design and operating requirements, annual assessment, contingency plan, inspections and closure requirements (Article 17.5 of Chapter 15). CORRECTIVE ACTION: Ensure compliance with all drip pad requirements including, but not limited to, design and operating requirements, annual assessment, contingency plan, inspections and closure requirements (Article 17.5 of Chapter 15) . | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130037 |  | 262.C | Emergency Coordinator | Failure to have at least one employee either on the facility premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.55 | 2018-10-01 | 2024-09-30 | 2024-09-30 | Revised | 64 | General Facility Operations | Site Safety | Emergency coordinator on the premises or on call | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have at least one employee either on the facility premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. |  |  | OBSERVATION: An emergency coordinator was not on the premises or available on call. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that at least one employee is either on the premises or on call with the responsibility for coordinating all emergency response measures. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130014 |  | 262.C | RCRA: Facility Emergency Equipment | Failure to equip the facility with required emergency equipment, unless none of the hazards posed by waste handled at the facility could require the particular kind of required equipment. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.32 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 65 | General Facility Operations | Site Safety | Facility equipped with all required emergency equipment | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to equip the facility with required emergency equipment, unless none of the hazards posed by waste handled at the facility could require the particular kind of required equipment. |  |  | OBSERVATION: The facility has not been equip with [LIST EQUIPMENT]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the facility has been equip with [LIST EQUIPMENT]. to the CUPA within [# days]. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130015 |  | 262.C | RCRA: Emergency Equipment Maintenance | Failure of the facility to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.33 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 66 | General Facility Operations | Site Safety | Tests and maintains all required safety equipment at the facility | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the facility to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. |  |  | OBSERVATION: [LIST EQUIPMENT] has not been tested and maintained to assure its proper operation in time of emergency. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating [LIST EQUIPMENT] has been properly tested or maintained. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130016 |  | 262.C | RCRA: Aisle Space | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless aisle space is not needed for any of these purposes. | 22 CCR 15 66265.35 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 67 | General Facility Operations | Site Safety | Maintains adequate aisle space | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless aisle space is not needed for any of these purposes. |  |  | OBSERVATION: The hazardous waste storage area located in the [LOCATION] did not have adequate aisle space allowing for unobstructed movement. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that adequate aisle space has been provided. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130013 |  | 262.C | RCRA: Facility Maintained to Prevent Fire/Explosion/Release | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.31 | 2016-06-01 | 2024-09-30 | 2024-09-30 | Revised | 68 | General Facility Operations | Site Safety | Maintains and operates the facility to minimize the possibility of fire/explosion/release | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. |  |  | OBSERVATION: [HAZARDOUS WASTE] was observed [DESCRIBE SPILL] in the [LOCATION]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the spill has been properly removed and managed. | [6 empty] | Yes
RCRA Large Quantity Generator | Release/Leaks/Spills | 3140003 |  |  | Universal Waste Handler: Release | Failure of the universal waste handler of PV modules, electronic devices, CRTs, and CRT glass to prevent the release of the universal waste to the environment under reasonable conditions by the following methods: 1) Immediately clean spills and leaks of universal wastes; and 2) Place all universal waste spills and leaks in containers that are structurally sound and compatible with the universal waste. | 22 CCR 23 66273.33.5, 66273.33.6 | 2021-08-02 | 2024-09-30 | 2024-09-30 | Revised | 80 | Universal Waste | UW Management | UWH properly cleaned up and contained spills of PV modules, electronic devices, CRTs and CRT glass | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the universal waste handler of PV modules, electronic devices, CRTs, and CRT glass to prevent the release of the universal waste to the environment under reasonable conditions by the following methods: 1) Immediately clean spills and leaks of universal wastes; and 2) Place all universal waste spills and leaks in containers that are structurally sound and compatible with the universal waste. |  |  | OBSERVATION: Failure of Universal Waste Handler of PV modules, electronic devices, CRTs and/or CRT glass to prevent the release of universal waste to the environment by failing to immediately clean spills and leaks of universal wastes and/or by placing spilled/leaked waste in containers that are not structurally sound and compatible with the waste. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the spilled PV modules, electronic devices, CRTs and/or CRT glass have been properly removed/cleaned up and managed. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110 |  | 262.A | RCRA-Administration/Documentation - General | Administration/Documentation - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 82 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes
RCRA Large Quantity Generator | Training | 3120 |  | 262.A | RCRA-Training - General | Training - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 84 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130 |  | 262.A | RCRA-Operations/Maintenance - General | Operations/Maintenance - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 86 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes
RCRA Large Quantity Generator | Release/Leaks/Spills | 3140 |  | 262.A | RCRA-Release/Leaks/Spills - General | Release/Leaks/Spills - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 88 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150 |  | 262.A | RCRA-Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2024-09-30 | 2024-09-30 | Revised | 90 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes

## Spreadsheet Notes
Please note the following regarding these spreadsheets:
These spreadsheets may be used by UPAs/PAs to create/update electronic inspection checklists for all Unified Programs.
These spreadsheets are updated each year after the CERS Violation Library has been updated.
The revised versions of these spreadsheets are made available generally 2-3 months before the CERS Violation Library changes go live in CERS.
The version of these spreadsheets that shows edits displays added text as underlined and deleted text with strikethrough, both of which are in red. Minor spelling corrections or formatting changes may not be displayed, but if any changes did occur the Violation Type Number cell and the cells that were updated are highlighted yellow and the Comment column says Revised. This is true even if the only thing that changed was the Checklist Item Order value. The same is true for the Clean version of the spreadsheets but only the final version of text is shown. Actual revisions are not detailed on the Clean version, so there is no underlined text or strikethrough and all text is black, but revised cells are highlighted in yellow. Note that the Comments column cells are not highlighted. New violations in the Edited version show the text in all cells in red and underlined. New violations in the Clean version also show all text in red, but not underlined. All cells of New violations in the Edited and Clean versions are not highlighted in yellow.
The column titled Comments says Existing for any violation that was not revised during this update period, Revised for any violation that had any cell updated, and New for new violations. Note that a violation is identified as Revised if any revision is made. However, a new Begin Date is only assigned if changes occurred to the CERS info (see below) and the change was deemed to be significant by CalEPA. When there are Revised violations that have a new Begin Date assigned, in CERS they assign a new End Date to the previous (expiring) version of the violation, which is one day before the Begin Date of the Revised versions. To maintain the previous versions of revised violations in your system, so they will continue to be displayed on reports as they should for the date they were cited, you will likely need to assign an End Date of 9/30/2024 to the previous versions of Revised violations since the new Begin Date of the Revised versions will be 10/1/2024. The expiring versions of violations are not displayed in these spreadsheets. A separate spreadsheet is available showing all expiring versions of violations with the End Date as 9/30/2024. This sheet will also include any Deleted violations. (That is this set of spreadsheets)
The word Deleted is entered in the Comments column for deleted violations, for which there is no revised version, and the Checklist Item Order value is blank, and as a result, deleted violations, if any, show up at the end of the sheets that shows edits and on the "NEW REVISED AND DELETED ONLY" sheets. Deleted violations are highlighted in gray. These deleted violations have no new revised version are not included on the clean versions.
The Begin Dates will match the Begin Dates in CERS. If a violation only had CUPA column info updated this does not result in a new Begin Date. Only CERS info changes deemed significant result in a new Begin Date.
CERS Info refers the information provided in columns A-K. This information matches violation information in CERS.
CUPA Info refers to the information provided in all columns to the right of column K. This information is not in CERS.
Each row is a separate violation and the spreadsheets are sorted by Checklist Item Order, which represents the intended order on the checklists that the violations will be displayed.
Inspection Checklist Item Text is the text that will show on the inspection checklist for that violation. This field was originally set up to only allow for 100 characters, which is the reason for abbreviations and limited detail at times.
The character limit in CERS for violation comments is 1000 characters. There are some prewritten Inspector Comments (Observation and Corrective Action) that are over 1000 characters. Depending on your system this may result in only the first 1000 characters being transferred to CERS or it may result in a failure to transfer any of the information, if an inspector utilizes a default inspection comment that is >1000 characters.
When the spreadsheets were first developed the Default Degree of Violation (Class) was set for all violations. You may want to make this field blank in your inspection system so inspectors must set the class versus relying on a default class which may not always be correct given the specific circumstances.
The far right columns of each spreadsheet will have one or more columns for the type(s) of facilities for that program. i.e. HMBP will only have one, but UST will have three (DW, SW, Full). Violations will be set as Yes in these columns if they apply to that facility type and No if not. So those violations with a Yes in the UST DW column will show up on an inspection checklist for DW UST sites, and those with a No will not. Those with a Yes in the SW column will show on a checklist for SW sites. There is a Yes for every violation in the Full column so all violations will show on a checklist for Full, which, for UST, would be for a facility that includes both SW and DW components. This same method is used on all program sheets with multiple facility types. All programs except HMBP and RCRA LQG have multiple facility types. There is only a Full column for UST and TP spreadsheets.