## APSA
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | AST Conditionally Exempt | AST Non_Qualified | AST Tier I | AST Tier II
APSA Program | Administration/Documentation | 4010001 |  |  | SPCC Plan prepared | Failure to prepare a Spill Prevention, Control, and Countermeasures (SPCC) Plan before operations begin. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3, 112.6 | 2024-10-01 | 2099-12-31 | 2024-10-01 | Existing | 1 | Requirement to Prepare and Implement |  | SPCC has been prepared | 22 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a Spill Prevention, Control, and Countermeasures (SPCC) Plan before operations begin. |  |  | OBSERVATION: Failure to prepare SPCC Plan before operations begin. CORRECTIVE ACTION: Prepare SPCC Plan. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010057 |  |  | SPCC Plan complete | Failure to prepare an SPCC Plan that meets all applicable requirements. | 40 CFR 1 112.3, 112.6; HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(2) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 2 | Requirement to Prepare and Implement |  | SPCC plan has been prepared that meets all applicable requirements | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an SPCC Plan that meets all applicable requirements. |  |  | OBSERVATION: Failure to prepare an SPCC Plan that meets all applicable requirements. CORRECTIVE ACTION: Complete or revise SPCC plan that meets all applicable requirements. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030038 |  |  | Implementation of SPCC Plan | Failure to implement the SPCC Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 3 | Requirement to Prepare and Implement |  | SPCC has been implemented | 25 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to implement a Spill Prevention Control and Countermeasure (SPCC) Plan. |  |  | OBSERVATION: Failure to implement SPCC. CORRECTIVE ACTION: Implement SPCC. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010008 |  |  | SPCC Plan available onsite | Failure to maintain a complete copy of the SPCC Plan at the facility if the facility is normally attended at least four hours per day, or at the nearest field office if the facility is not so attended. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3(e)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 4 | Requirement to Prepare and Implement |  | SPCC onsite If facility staffed 4 hrs/day, or at the nearest field office if not so attended | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to maintain SPCC plan onsite if facility is manned at least four (4) hours per day, or at the nearest field office if the facility is not so attended. |  |  | OBSERVATION: Failure to maintain SPCC plan onsite if facility is manned at least four (4) hours per day, or at the nearest field office if the facility is not so attended. CORRECTIVE ACTION: Maintain SPCC plan onsite If facility staffed 4 hrs/day, or at the nearest field office if the facility is not so attended. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010059 |  |  | SPCC Plan and required records available | Failure to have the SPCC Plan and all applicable required records and documentation available for review upon request by the UPA during normal working hours. | 19 CCR 11 1601, 1613(a) | 2025-07-01 | 2099-12-31 | 2025-07-01 | New | 5 | Requirement to Prepare and Implement |  | SPCC Plan and all required records/documentation available for review during normal working hours | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to have the SPCC Plan and all applicable required records and documentation available for review upon request by the UPA during normal working hours. |  |  | OBSERVATION: Owner/Operator failed to have the SPCC Plan and all applicable required records and documentation available for review when requested by the UPA during normal working hours. CORRECTIVE ACTION: Provide copies of [SPECIFY RECORDS BEING REQUESTED] to the UPA and ensure that the SPCC Plan and all required records and documentation is available for review during normal working hours. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010003 |  |  | Professional engineer certification | Failure to have a licensed professional engineer properly review and certify the SPCC Plan. | 40 CFR 1 112.3(d); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(3) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 6 | Requirement to Prepare and Implement |  | Professional engineer has properly reviewed and certified the SPCC Plan | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have a licensed professional engineer properly review and certify the SPCC Plan. |  |  | OBSERVATION: PE failed to properly review and/or certify the SPCC Plan for one or more of the requirements. CORRECTIVE ACTION: Submit SPCC that has been properly reviewed and certified by a PE. | [6 empty] | No | Yes | No | No
APSA Program | Administration/Documentation | 4010045 |  |  | Professional engineer attestations | Failure of the owner or operator to ensure a professional engineer makes all required attestations in the SPCC Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3(d)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 7 | Requirement to Prepare and Implement |  | A professional engineer made all required attestations in the SPCC Plan | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator to ensure a professional engineer makes all required attestations in the SPCC Plan. |  |  | OBSERVATION: Failure of to ensure a professional engineer makes all required attestations in the SPCC Plan as listed in 40 CFR 112.3(d)(1): [specify missing attestations]. CORRECTIVE ACTION: Amend the SPCC plan to ensure that the professional engineer's certification contains all the required attestations. | [6 empty] | No | Yes | No | No
APSA Program | Administration/Documentation | 4010047 |  |  | Qualified Facility - Certification of SPCC Plan | Failure to have management or a professional engineer certify the SPCC Plan and comply with certification requirements at a qualified facility. | 40 CFR 1 112.6(a)(1), 112.6(b); HSC 6.67 25270.4.5 (a); 19 CCR 11 1601, 1611(a)(3) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 8 | Requirement to Prepare and Implement |  | Qualified Facility's SPCC plan has been self or PE certified. | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to have management or a professional engineer certify the SPCC Plan and comply with certification requirements at a qualified facility. |  |  | OBSERATION: SPCC Plan has not been properly certified by management or professional engineer. CORRECTIVE ACTION: Facility must certify or have professional engineer certify the SPCC Plan. | [6 empty] | No | No | Yes | Yes
APSA Program | Administration/Documentation | 4010035 |  |  | Appropriate SPCC Plan | Failure to prepare an appropriate SPCC Plan within 6 months when the facility no longer meets the Tier I or Tier II qualified facility criteria. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(2), 112.6(b)(2) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 9 | Requirement to Prepare and Implement |  | Facility prepared appropriate SPCC when no longer meeting Tier I/II requirements | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an appropriate SPCC Plan within 6 months when the facility no longer meets the Tier I or Tier II qualified facility criteria. |  |  | OBSERVATION: Failure to prepare appropriate SPCC plan when no longer meeting the conditions of a Tier I or Tier II Qualified Facility: CORRECTIVE ACTION: Maintain compliance with Tier I or II qualified facility requirements or prepare and implement a SPCC plan for a Tier II or Non-Qualified Facility as is applicable. | [6 empty] | No | No | Yes | Yes
APSA Program | Administration/Documentation | 4010010 |  |  | SPCC Plan amended | Failure to amend the SPCC Plan within 6 months: 1. When the facility has had a change in design, construction, operation, or maintenance which affects the facility’s discharge potential. AND/OR 2. To include more effective proven technology at the time of the 5-year SPCC Plan review and evaluation. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.5(a), 112.5(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 10 | SPCC Amendments |  | Facility has amended SPCC as necessary | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to amend the SPCC Plan within 6 months: 1. When the facility has had a change in design, construction, operation, or maintenance which affects the facility’s discharge potential. AND/OR 2. To include more effective proven technology at the time of the 5-year SPCC Plan review and evaluation. |  |  | OBSERVATION: 1. Failure to amend SPCC plan within 6 months of when the facility has had a change in: design, construction, operation, or maintenance which affects the facility’s discharge potential. 2. Failure to amend SPCC plan within 6 months to include more effective proven technology at the time of the 5-year SPCC Plan review and evaluation. CORRECTIVE ACTION: Amend SPCC as required. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030039 |  |  | Implementation of SPCC Plan amendments | Failure to implement SPCC Plan amendments within 6 months. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.5(a), 112.5(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 11 | SPCC Amendments |  | SPCC has been implemented within 6 months of amendment | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to implement a Spill Prevention Control and Countermeasure (SPCC) Plan within 6 months of amendment . |  |  | OBSERVATION: Failure to implement SPCC within 6 months of amendment. CORRECTIVE ACTION: Implement amended SPCC. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010039 |  |  | Certification of technical amendments | Failure to have technical amendment(s) certified by a licensed professional engineer. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.5(c) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 12 | SPCC Amendments |  | Technical amendment(s) were certified by a licensed professional engineer | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have technical amendment(s) certified by a licensed professional engineer. |  |  | OBSERVATION: Failure to have Technical Amendment(s) that materially affect the potential for a discharge [list here] certified by a professional engineer. CORRECTIVE ACTION: All Technical Amendments listed above must be reviewed, modified as necessary and certified by a professional engineer. | [6 empty] | No | Yes | No | No
APSA Program | Administration/Documentation | 4010048 |  |  | Tier I - Certification of technical amendments | Failure of a Tier I qualified facility to certify the SPCC Plan according to 40 CFR 112.6(a)(1) if a technical change has been made to the facility design, construction, operation, or maintenance. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 13 | SPCC Amendments |  | Tier I Qualified Facility has certified tech amendments. | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a Tier I qualified facility to certify the SPCC Plan according to 40 CFR 112.6(a)(1) if a technical change has been made to the facility design, construction, operation, or maintenance. |  |  | OBSERVATION: Owner/Operator failed to certify technical amendments to the SPCC Plan when there has been a change in facility design, construction, operation or maintenance that may affect its potential for a discharge. CORRECTIVE ACTION: Certify technical amendments to the SPCC when there has been a change in facility design, construction, operation or maintenance that may affect its potential for a discharge. | [6 empty] | No | No | Yes | No
APSA Program | Administration/Documentation | 4010052 |  |  | Tier II – Certification of technical amendments | Failure to have technical amendment(s) certified by the owner or operator or a professional engineer for a Tier II qualified facility when required. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(b)(2); 112.6(b)(2)(i) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 14 | SPCC Amendments |  | Tech amendments certified when a change in facility design/operations occurs, & by PE when required | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to have technical amendment(s) certified by the owner or operator or a professional engineer for a Tier II qualified facility when required. |  |  | OBSERVATION: Technical amendments to the SPCC Plan have not been certified by owner/operator or professional engineer, when required, when there has been a change in facility design, construction, operation or maintenance that may affect its potential for a discharge. CORRECTIVE ACTION: Have technical amendments properly certified in SPCC Plan. | [6 empty] | No | No | No | Yes
APSA Program | Administration/Documentation | 4010009 |  |  | Five-year SPCC Plan review and documentation of the review | Failure to complete a review and evaluation of the SPCC Plan at least once every five years, document the completion of the review, and sign a statement as to whether the SPCC Plan will be amended. | 40 CFR 1 112.5 (b); HSC 6.67 25270.4.5 (a); 19 CCR 11 1601, 1611(a)(4) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 15 | Five Year Review |  | 5 year review performed on SPCC and documented | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to complete a review and evaluation of the SPCC Plan at least once every five years, document the completion of the review, and sign a statement as to whether the SPCC Plan will be amended. |  |  | OBSERVATION: Failure to perform and/or document the five-year review of the SPCC plan. CORRECTIVE ACTION: Complete and document the 5 year review of SPCC Plan and submit verification of proper completion. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010012 |  |  | SPCC Plan basic requirements | Failure to prepare an SPCC Plan which fulfills all basic requirements that include: 1. The SPCC Plan must be prepared in accordance with good engineering practices. 2. Have full approval of management at a level of authority to commit the necessary resources to fully implement the SPCC Plan. 3. Prepare the SPCC Plan in writing. 4. Follow the sequence of the SPCC rule or include a cross-reference. 5. If the SPCC Plan calls for additional procedures, methods, or equipment not yet fully operational, discuss the items in separate paragraphs. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 16 | General SPCC Requirements |  | SPCC in writing, follows code seq/cross ref, good eng practice, mgt approval, items not in place | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an SPCC Plan which fulfills all basic requirements that include: 1. The SPCC Plan must be prepared in accordance with good engineering practices. 2. Have full approval of management at a level of authority to commit the necessary resources to fully implement the SPCC Plan. 3. Prepare the SPCC Plan in writing. 4. Follow the sequence of the SPCC rule or include a cross-reference. 5. If the SPCC Plan calls for additional procedures, methods, or equipment not yet fully operational, discuss the items in separate paragraphs. |  |  | OBSERVATION: Failure to prepare SPCC Plan that meets the following requirements: 1. Follows the sequence of SPCC rule and/or includes cross-reference. 2. Prepared in accordance with good engineering practices. 3. Has the full approval of management at a level of authority to commit the necessary resources to fully implement the SPCC plan. 4. Plan is in writing. 5. Plan addresses additional procedures/methods/equipment not yet fully operational. CORRECTIVE ACTION: Prepare a SPCC plan that: 1. Follows a sequence of rule and/or includes a cross-reference. 2. Is prepared in accordance with good engineering practices. 3. Has full approval of management at a level of authority to commit the necessary resources to fully implement the SPCC plan. 4. Is in writing. 5. Addresses additional procedures/methods/equipment not yet fully operational. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010013 |  |  | SPCC Plan discussion of conformance with requirements | Failure to include in the SPCC Plan an adequate discussion of the facility's conformance with the requirements of 40 CFR Part 112, other effective discharge prevention and containment procedures listed in Part 112, or any applicable more stringent State rules, regulations, and guidelines. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(j) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 17 | General SPCC Requirements |  | SPCC Plan discusses conformance with all SPCC rule requirements, & state rules/regs/guidelines. | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to discuss in the SPCC Plan conformance with SPCC requirements and other effective discharge prevention and containment procedures, or any applicable more stringent State rules, regulations, and guidelines. |  |  | OBSERVATION: Failure of SPCC Plan to adequately discuss conformance with all SPCC rule requirements, other effective discharge prevention and containment procedures, or any applicable more stringent State rules, regulations, and guidelines. CORRECTIVE ACTION: Revise SPCC Plan to include an adequate discussion of conformance with all SPCC rule requirements, other effective discharge prevention and containment procedures, or any applicable more stringent State rules, regulations, and guidelines. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010014 |  |  | Equivalent environmental protection | Failure to state reasons for nonconformance and describe equivalent methods in detail if claiming equivalent environmental protection for SPCC requirements other than secondary containment. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(2) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 18 | General SPCC Requirements | Environmental Equivalence | Environmental Equivalence, if claimed, is addressed in SPCC, other than for secondary containment. | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to state reasons for nonconformance in SPCC Plan and describe in detail alternate methods used to achieve environmentally equivalent protection when claiming environmental equivalence for SPCC requirements other than secondary containment. |  |  | OBSERVATION: Failure to state reasons for nonconformance in SPCC Plan and describe in detail alternate methods used to achieve environmentally equivalent protection when claiming environmental equivalence for SPCC requirements other than secondary containment. CORRECTIVE: ACTION: In SPCC Plan discuss reasons for nonconformance and describe alternate methods used to achieve environmentally equivalent protection. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010050 |  |  | Tier II - Certification of alternative measures by professional engineer | Failure to have a professional engineer review and certify in writing one or more of the following alternative measures for a Tier II qualified facility: 1. Alternative method which achieves equivalent environmental protection pursuant to 40 CFR 112.7(a)(2). 2. Impracticability determination and measures in lieu of secondary containment pursuant to 40 CFR 112.7(d). 3. Measures pursuant to 40 CFR 112.9(c)(6) for produced water containers and any associated piping and appurtenances downstream from the container. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(b)(3); 112.6(b)(4)(iii) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 19 | General SPCC Requirements | Tier II Alternative Measures | PE certified enviro equivalence, impracticability, and produced water containers/piping, if needed | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have a professional engineer review and certify in writing one or more of the following alternative measures for a Tier II qualified facility: 1. Alternative method which achieves equivalent environmental protection pursuant to 40 CFR 112.7(a)(2). 2. Impracticability determination and measures in lieu of secondary containment pursuant to 40 CFR 112.7(d). 3. Measures pursuant to 40 CFR 112.9(c)(6) for produced water containers and any associated piping and appurtenances downstream from the container. |  |  | OBSERVATION: PE did not review and certify one or more of the following: 1. Alternative environmental equivalence methods 2. Impracticability for secondary containment 3. Produced water containers and associated piping as described in 112.9(c)(6). CORRECTIVE ACTION: Obtain a PE review and certification for one or more of the following: 1. Alternative environmental equivalence methods 2. Impracticability for secondary containment 3. Produced water containers and associated piping as described in 112.9(c)(6). | [6 empty] | No | No | No | Yes
APSA Program | Administration/Documentation | 4010051 |  |  | Tier II – Professional engineer attestations | Failure of the owner or operator to ensure a professional engineer makes all required attestations in the SPCC Plan when a professional engineer certification is necessary due to an alternative measure claim at a Tier II qualified facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(b)(4)(i) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 20 | General SPCC Requirements | Tier II Alternative Measures | PE required attestations in the SPCC Plan for alternative measure claim at a Tier II facility | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator to ensure a professional engineer makes all required attestations in the SPCC Plan when a professional engineer certification is necessary due to an alternative measure claim at a Tier II qualified facility. |  |  | OBSERVATION: PE did not attest to one or more of the following: 1. PE did not attest that they are familiar with the requirements of 112.6(b). 2. SPCC does not include that the PE or agent has visited the facility. 3. SPCC does not include that the PE attests that the alternate environmental equivalence or the determination of impracticability and alternative measures in accordance with § 112.7(d) is consistent with good engineering practice. CORRECTIVE ACTION: Obtain PE certification for one or more of the following: 1. Obtain PE certification that they are familiar with the requirements of 112.6(b). 2. Obtain PE or agent certification that they have visited the facility. 3.Have PE attest that the alternate environmental equivalence or the determination of impracticability and alternative measures in accordance with § 112.7(d) is consistent with good engineering practice | [6 empty] | No | No | No | Yes
APSA Program | Administration/Documentation | 4010016 |  |  | Facility Description | Failure to adequately and accurately describe in the SPCC Plan the physical layout of the facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 21 | General SPCC Requirements | Facility Description/Storage/Diagram | Physical layout of the facility is adequately and accurately described in SPCC | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately and accurately describe in the SPCC Plan the physical layout of the facility. |  |  | OBSERVATION: Failure to adequately and accurately describe the physical layout of the facility, or no description of the physical layout of the facility included in the SPCC plan. CORRECTIVE ACTION: Update SPCC plan to adequately and accurately describe the physical layout of facility. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010041 |  |  | Oil type and storage capacity of storage containers | Failure to address in the SPCC Plan the type of oil and storage capacity for each fixed container. For mobile or portable containers, either provide the type of oil and storage capacity, or an estimate of the potential number of mobile or portable containers, the types of oil, and anticipated storage capacities. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3)(i) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 22 | General SPCC Requirements | Facility Description/Storage/Diagram | SPCC Plan addresses the type of oil and storage capacity for all fixed and portable containers | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to address in the SPCC Plan the type of oil and storage capacity for each fixed container. For mobile or portable containers, either provide the type of oil and storage capacity, or an estimate of the potential number of mobile or portable containers, the types of oil, and anticipated storage capacities. |  |  | OBSERVATION: Failure to address in the SPCC Plan the type of oil and storage capacity for each fixed container, or, for portable and/or mobile containers, either provide the type of oil and storage capacity, or an estimate of the potential number of portable or mobile containers, the types of oil, and anticipated storage capacities. CORRECTIVE ACTION: Amend the SPCC Plan to properly address the type and storage capacity of all fixed and portable and/or mobile containers as required. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010015 |  |  | Facility Diagram | Failure to include in the SPCC Plan an adequate facility diagram, or no facility diagram included. The facility diagram is not required on a Tier I qualified facility SPCC Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 23 | General SPCC Requirements | Facility Description/Storage/Diagram | SPCC contains an adequate facility diagram | 42 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to have an adequate facility diagram, or no facility diagram included within the SPCC plan. |  |  | OBSERVATION: Failure to have an adequate facility diagram, or no facility diagram included within the SPCC plan. CORRECTIVE ACTION: Include an adequate facility diagram in the SPCC | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010030 |  |  | Discharge prevention measures | Failure to address in the SPCC Plan discharge prevention measures, including procedures for routine handling of products such as loading/unloading and facility transfers. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3)(ii) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 24 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC adequately addresses discharge prevention measures for routine handling, loading/unloading | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to address in the SPCC Plan discharge prevention measures, including procedures for routine handling of products such as loading/unloading and facility transfers. |  |  | OBSERVATION: Failure to address discharge prevention measures, including procedures for routine handling of products such as loading/unloading and facility transfers within the SPCC plan. CORRECTIVE ACTION: Revise SPCC plan to adequately discuss discharge prevention measures, including procedures for routine handling of products such as loading/unloading and facility transfers. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010042 |  |  | Countermeasures for discharge discovery, response, and cleanup | Failure to address in the SPCC Plan countermeasures for discharge discovery, response, and cleanup (both facility’s and contractor’s resources). | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3)(iv) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 25 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC Plan addressed countermeasures for discharge discovery, response and cleanup | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to address in the SPCC Plan countermeasures for discharge discovery, response, and cleanup (both facility’s and contractor’s resources). |  |  | OBSERVATION: Failure to address in the SPCC Plan countermeasures for discharge discovery, response, and cleanup. CORRECTIVE ACTION: Amend the SPCC Plan to fully address the countermeasures the facility will conduct to discover, respond and cleanup any discharge. This should include both the facility's and contractor's prescribed actions and resources. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010043 |  |  | Disposal methods | Failure to address in the SPCC Plan disposal methods for recovered materials. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3)(v) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 26 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC Plan addresses disposal methods for recovered materials | 60 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to address in the SPCC Plan disposal methods for recovered materials. |  |  | OBSERVATION: Failure to address in the SPCC Plan disposal methods for recovered materials. CORRECTIVE ACTION: Amend the SPCC Plan to address the disposal methods for recovered materials. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010017 |  |  | Discharge reporting procedures | Failure to include in the SPCC Plan: 1. A contact list and phone numbers for the facility response coordinator, National Response Center, cleanup contractors with an agreement for response, and all Federal, State, and local agencies who must be contacted in case of a discharge. 2. Information and procedures that would enable a person reporting an oil discharge to relate all information as described in 40 CFR 112.7(a)(4), unless facility submitted a Facility Response Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3)(vi); 112.7(a)(4) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 27 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC contains procedures for reporting a discharge | 50 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include in the SPCC Plan: 1. A contact list and phone numbers for the facility response coordinator, National Response Center, cleanup contractors with an agreement for response, and all Federal, State, and local agencies who must be contacted in case of a discharge 2. Information and procedures that would enable a person reporting an oil discharge to relate all information as described in 40 CFR 112.7(a)(4), unless facility submitted a Facility Response Plan. |  |  | OBSERVATION: Failure to adequately discuss procedures for reporting a discharge, or no information and procedures for reporting a discharge are included within the SPCC plan. CORRECTIVE ACTION: Include procedures for reporting a discharge in the SPCC. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010018 |  |  | Discharge response procedures | Failure to organize the SPCC Plan so that portions describing procedures to be used when a discharge occurs will be readily usable in an emergency and include appropriate supporting material as appendices, unless facility submitted a Facility Response Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(5) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 28 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC organized so discharge procedures are readily usable if the facility has no response plan | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to organize the SPCC Plan so that portions describing procedures to be used when a discharge occurs will be readily usable in an emergency and include appropriate supporting material as appendices, unless facility submitted a Facility Response Plan. |  |  | OBSERVATION: Failure to organize the SPCC Plan so that portions describing procedures to be used when a discharge occurs will be readily usable in an emergency, unless facility submitted a Facility Response Plan. CORRECTIVE ACTION: Update SPCC Plan so that portions describing procedures to be used when a discharge occurs will be readily usable in an emergency. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010019 |  |  | Discharge predictions | Failure to include in the SPCC Plan a prediction of the direction, rate of flow, and total quantity of oil that could be discharged for each type of major equipment failure where experience indicates a reasonable potential for equipment failure. The rate of flow is not required on a Tier I qualified facility SPCC Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 29 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC predicts direction, rate of flow, total quantity of oil that could be released from a discharge | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include in the SPCC Plan a prediction of the direction, rate of flow, and total quantity of oil that could be discharged for each type of major equipment failure where experience indicates a reasonable potential for equipment failure. The rate of flow is not required on a Tier I qualified facility SPCC Plan. |  |  | OBSERVATION: Failure to predict the direction, rate of flow, and total quantity of oil that could be discharged for each type of major equipment failure in the SPCC plan. CORRECTIVE ACTION: Update SPCC plan to include prediction of the direction, rate of flow, and total quantity of oil that could be discharged for each type of major equipment failure. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010054 |  |  | Tier I - Failure analysis-direction and amount of flow | Failure to include in the SPCC Plan a prediction of direction and total quantity of oil potentially discharged from the facility as a result of each type of major equipment failure. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(3)(i) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 30 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC contains a prediction of direction and total quantity of oil potentially discharged | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include in the SPCC Plan a prediction of direction and total quantity of oil potentially discharged from the facility as a result of each type of major equipment failure. |  |  | OBSERVATION: Failure to include in the SPCC Plan a prediction of direction and total quantity of oil potentially discharged from the facility as a result of each type of major equipment failure. CORRECTIVE ACTION: Update SPCC plan to include a prediction of direction and total quantity of oil potentially discharged from the facility as a result of each type of major equipment failure. | [6 empty] | No | No | Yes | No
APSA Program | Administration/Documentation | 4010020 |  |  | General Containment Description | Failure to discuss in the SPCC Plan the appropriate general containment, diversionary structures, or equipment to prevent a discharge, including typical failure mode and most likely quantity of discharge for the following: 1. Bulk storage containers, 2. Mobile/portable containers, 3. Oil-filled equipment, 4. Piping and related appurtenances, 5. Mobile refuelers or non-transportation-related tank cars, and 6. Transfer areas, equipment and activities. This does not apply to facilities with oil filled operational equipment implementing 112.7(k). | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(c) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 31 | General SPCC Requirements | Containment | SPCC addresses the appropriate general containment/diversionary structures/equipment | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to discuss in the SPCC Plan the appropriate general containment, diversionary structures, or equipment to prevent a discharge, including typical failure mode and most likely quantity of discharge for the following: 1. Bulk storage containers, 2. Mobile/portable containers, 3. Oil-filled equipment, 4. Piping and related appurtenances, 5. Mobile refuelers or non-transportation-related tank cars, and 6. Transfer areas, equipment and activities. This does not apply to facilities with oil filled operational equipment implementing 112.7(k). |  |  | OBSERVATION: Failure to discuss the appropriate general containment, diversionary structures, or equipment to prevent a discharge, including typical failure mode and most likely quantity of discharge within the SPCC plan. CORRECTIVE ACTION: Update SPCC plan to address the general containment, diversionary structures, and equipment in use at facility to prevent a discharge, including typical failure mode and most likely quantity of potential discharge. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030037 |  |  | General containment | Failure to provide appropriate secondary containment and/or diversionary structures or equipment for the following: 1. Bulk storage containers, 2. Mobile or portable containers, 3. Oil-filled equipment, 4. Piping and related appurtenances, 5. Mobile refuelers or non-transportation-related tank cars, and 6. Transfer areas, equipment and activities and ensure that the entire containment system, including walls and floor, are capable of containing oil and constructed so that any discharge will not escape the containment system before cleanup occurs. | 40 CFR 1 112.7(c); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(5) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 32 | General SPCC Requirements | Containment | Appropriate (general) containment/diversionary structures/equipment have been provided | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide appropriate secondary containment and/or diversionary structures or equipment for the following: 1. Bulk storage containers, 2. Mobile or portable containers, 3. Oil-filled equipment, 4. Piping and related appurtenances, 5. Mobile refuelers or non-transportation-related tank cars, and 6. Transfer areas, equipment and activities and ensure that the entire containment system, including walls and floor, are capable of containing oil and constructed so that any discharge will not escape the containment system before cleanup occurs. |  |  | OBSERVATION: Failure to provide the appropriate general containment/diversionary structures/equipment for the following: bulk storage containers, mobile or portable containers, oil-filled equipment, piping and related appurtenances, mobile refuelers or non-transportation-related tank cars, and transfer areas. CORRECTIVE ACTION: Provide appropriate general containment measures and/or diversionary structures/equipment capable of containing oil and constructed so that any discharge will not escape the containment system before cleanup occurs. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010004 |  |  | Impracticability claims of appropriate containment explained and certified | Failure to clearly explain why appropriate containment/diversionary structures are not practicable and/or SPCC Plan claiming impracticability is not certified by a licensed professional engineer. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(d) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 33 | General SPCC Requirements | Impracticability | Impracticability of containment/diversionary items, if claimed, is PE demonstrated and certified | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to clearly explain why appropriate containment/diversionary structures are not practicable and/or SPCC Plan claiming impracticability is not certified by a licensed professional engineer. Note: impracticability determinations must be certified by a PE for Tier II plans. |  |  | OBSERVATION: Failure to clearly explain why appropriate containment/diversionary structures are not practicable and/or SPCC Plan claiming impracticability is not certified by a licensed professional engineer. CORRECTIVE ACTION: SPCC Plan must clearly explain why appropriate containment/diversionary structures are not practicable and PE shall certify all claims of impracticability. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030033 |  |  | Secondary Containment Impracticability – Testing | Failure to perform required periodic integrity and leak testing when claiming secondary containment impracticability. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(d) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 34 | General SPCC Requirements | Impracticability | Periodic integrity/leak testing performed with impracticability claim | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform required periodic integrity and leak testing when claiming secondary containment impracticability. |  |  | OBSERVATION: Failure to perform periodic integrity and leak testing when claiming secondary containment impracticability. CORRECTIVE ACTION: Perform periodic integrity and leak testing of items in areas where making secondary containment impracticability claim. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010005 |  |  | Oil spill contingency plan prepared when claiming impracticability | Failure to prepare an oil spill contingency plan when claiming impracticability of appropriate containment/diversionary structures. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(d)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 35 | General SPCC Requirements | Impracticability | If claiming impracticability of containment/diversionary items a contingency plan has been included | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an oil spill contingency plan when claiming impracticability of appropriate containment/diversionary structures. Note: impracticability determinations must be certified by a PE for Tier II plans. |  |  | OBSERVATION: Failure to prepare an oil spill contingency plan when claiming impracticability of appropriate containment/diversionary structures. CORRECTIVE ACTION: If claiming impracticability of containment/diversionary items, include a contingency plan. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010006 |  |  | Written commitment of manpower, equipment, materials when claiming impracticability | Failure to provide a written commitment of manpower, equipment, and materials required to expeditiously control and remove any discharge that may be harmful when claiming impracticability of appropriate containment/diversionary structures. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(d)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 36 | General SPCC Requirements | Impracticability | If claiming impracticability written commitment of manpower, equipment, and materials provided | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide a written commitment of manpower, equipment, and materials required to expeditiously control and remove any discharge that may be harmful when claiming impracticability of appropriate containment/diversionary structures. |  |  | OBSERVATION: Failure to provide a written commitment of manpower, equipment, and materials required to expeditiously control and remove any discharge that may be harmful when claiming impracticability of appropriate containment/diversionary structures. CORRECTIVE ACTION: If claiming impracticability of containment/diversionary structures provide a written commitment of manpower, equipment, and materials. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010023 |  |  | Employee Training and Spill Prevention Briefings Description | Failure to include in the SPCC plan an adequate description of employee training. Training shall address, at a minimum: 1. Operation and maintenance of equipment to prevent discharges; 2. Discharge procedure protocols; 3. Applicable pollution control laws, rules, and regulations; 4. General facility operations; 5. Content of the facility SPCC plan; and 6. Annual discharge prevention briefings for oil-handling personnel to assure adequate understanding of the SPCC plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(f)(1), 112.7(f)(3) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 37 | General SPCC Requirements | Training | Employee training and spill prevention briefings discussed in SPCC plan | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include in the SPCC plan an adequate description of employee training. Training shall address, at a minimum: 1. Operation and maintenance of equipment to prevent discharges; 2. Discharge procedure protocols; 3. Applicable pollution control laws, rules, and regulations; 4. General facility operations; 5. Content of the facility SPCC plan; and 6. Annual discharge prevention briefings for oil-handling personnel to assure adequate understanding of the SPCC plan. |  |  | OBSERVATION: Failure to include in SPCC plan a discussion, or adequate description of all required employee training including annual spill prevention briefings provided to oil-handling personnel. CORRECTIVE ACTION: Revise SPCC plan to adequately describe employee training, addressing all training requirements including spill prevention briefings provided to oil-handling personnel at least once per year. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Training | 4020001 |  |  | Employee training requirements | Failure to provide the following training to all oil-handling personnel and maintain training records for at least three years: 1. Operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. 5. Contents of the SPCC Plan. | 40 CFR 1 112.7(f)(1); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(7) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 38 | General SPCC Requirements | Training | Training provided to all oil-handling personnel and records maintained for 3 years | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide the following training to all oil-handling personnel and maintain training records for at least three years: 1. Operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. 5. Contents of the SPCC Plan. |  |  | OBSERVATION: Failure to provide training to all oil-handling personnel and maintain trainding records for at least three years regarding one or more of the following: 1. The operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. AND 5. The contents of the SPCC Plan. CORRECTIVE ACTION: Provide required training, submit doucmentation of training to the UPA, and maintain training records for three years. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010022 |  |  | Designated Person | Failure to designate person who reports to management as accountable for discharge prevention at facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(f)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 39 | General SPCC Requirements | Training | Person has been designated as accountable for discharge prevention and reports to management | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to designate a person accountable for discharge prevention and who reports to facility management. |  |  | OBSERVATION: Failure to designate a person accountable for discharge prevention and who reports to facility management. CORRECTIVE ACTION: Designate a person accountable for discharge prevention and who reports to facility management. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Training | 4020002 |  |  | Spill prevention briefings | Failure to conduct spill prevention briefing for oil-handling personnel at least once a year to assure adequate understanding of the SPCC Plan and maintain briefing records for at least three years. A briefing includes: 1. Known discharges or failures. 2. Malfunctioning components. 3. Any recently developed precautionary measures. | 40 CFR 1 112.7(f)(3); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(7) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 40 | General SPCC Requirements | Training | Spill prevention briefings are conducted annually and records maintained for 3 years | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to conduct spill prevention briefing for oil-handling personnel at least once a year to assure adequate understanding of the SPCC Plan and maintain briefing records for at least three years. A briefing includes: 1. Known discharges or failures. 2. Malfunctioning components. 3. Any recently developed precautionary measures. |  |  | OBSERVATION: Failure to conduct spill prevention briefings at least once a year, to maintain briefing records for at least three years, or failure to highlight or describe one or more of the following: Known discharges or failures; Malfunctioning components; Recently developed precautionary measures. CORRECTIVE ACTION: Conduct spill prevention briefings annually and maintain briefing records for three years. Provide compliance verification. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010024 |  |  | Facility security description | Failure to describe in the SPCC Plan facility security measures including: 1. How access to the oil handling, processing, and storage areas is secured and controlled. 2. How master flow and drain valves are secured. 3. How unauthorized access to starter controls on oil pumps is prevented. 4. How out-of-service and loading/unloading connections of oil pipelines is secured. 5. The appropriateness of security lighting to both prevent acts of vandalism and assist in the discovery of oil discharges. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(g) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 41 | General SPCC Requirements | Security | SPCC addresses security measures-lighting, access to handling/storage, valves/pumps/transfer equip | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to describe in the SPCC plan facility security measures including: 1. How access to the oil handling, processing, and storage areas is secured and controlled. 2. How master flow and drain valves are secured. 3. How unauthorized access to starter controls on oil pumps is prevented. 4. How out-of-service and loading/unloading connections of oil pipelines is secured. 5. The appropriateness of security lighting to both prevent acts of vandalism and assist in the discovery of oil discharges. |  |  | OBSERVATION: Failure to describe in the SPCC plan security measures required by 40 CFR Part 112.7(g), including: Securing access to oil handling, processing, and storage areas; Securing master flow and drain valves; Prevention of unauthorized access to starter controls on oil pumps; Securing loading/unloading connections of oil pipelines; Appropriateness of security lighting. CORRECTIVE ACTION: Update SPCC plan to properly address security measures required by 40 CFR Part 112.7(g). | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030001 |  |  | Facility security measures | Failure to implement security measures listed in the SPCC Plan and/or one or more of the following security measures for the facility: 1. Secure and control access to the oil handling, processing, and storage areas. 2. Secure the master flow and drain valves. 3. Prevent unauthorized access to starter controls and oil pumps. 4. Secure out-of-service and loading/unloading connections of oil pipelines. 5. Address the appropriateness of security lighting to both prevent acts of vandalism and assist in the discovery of oil discharges. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(g) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 42 | General SPCC Requirements | Security | Handling areas, valves, pumps/starter controls, load/unload connections secured, lighting adequate | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to implement security measures listed in the SPCC Plan and/or one or more of the following security measures for the facility: 1. Secure and control access to the oil handling, processing, and storage areas. 2. Secure the master flow and drain valves. 3. Prevent unauthorized access to starter controls and oil pumps. 4. Secure out-of-service and loading/unloading connections of oil pipelines. 5. Address the appropriateness of security lighting to both prevent acts of vandalism and assist in the discovery of oil discharges. |  |  | OBSERVATION: Facility failed to implement one or more security measures. CORRECTIVE ACTION: implement the following security measures for the facility: 1. Secure and control access to the oil handling, processing, and storage areas. 2. Secure the master flow and drain valves. 3. Prevent unauthorized access to starter controls and oil pumps. 4. Secure out-of-service and loading/unloading connections of oil pipelines. 5. Security lighting to both prevent acts of vandalism and assist in the discovery of oil discharges. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010025 |  |  | Loading/Unloading Racks | Failure to discuss in the SPCC Plan all requirements pertaining to a tank car or tank truck loading/unloading rack. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(h) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 43 | General SPCC Requirements | Loading/Unloading Racks | SPCC adequately discusses facility tank car and tank truck loading/unloading rack | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately discuss facility tank car and tank truck loading/unloading rack requirements in the SPCC plan. |  |  | OBSERVATION: SPCC plan does not adequately discuss facility tank car and tank truck loading/unloading rack requirements. CORRECTIVE ACTION: Amend SPCC plan to adequately discuss facility tank car and tank truck loading/unloading rack requirements. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030002 |  |  | Secondary containment at loading/unloading racks | Failure to ensure loading/unloading rack drainage flows to catchment basin or treatment facility designed to handle discharges, or use a quick drainage system when a tank car or tank truck loading/unloading rack is present at the facility. The containment system must be designed to hold at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. | 40 CFR 1 112.7(h)(1); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(5) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 44 | General SPCC Requirements | Loading/Unloading Racks | Loading rack containment has capacity to contain single largest compartment of tank car/truck | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure loading/unloading rack drainage flows to catchment basin or treatment facility designed to handle discharges, or use a quick drainage system when a tank car or tank truck loading/unloading rack is present at the facility. The containment system must be designed to hold at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. |  |  | OBSERVATION: Failure to ensure loading/unloading rack drainage flows to catchment basin or treatment facility designed to handle discharges, or use a quick drainage system when a tank car or tank truck loading/unloading rack is present at the facility, and is designed to hold at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. CORRECTIVE ACTION: Ensure loading/unloading rack drainage flows to containment or treatment system with at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030003 |  |  | Warning to prevent vehicular departure at loading/unloading rack | Failure to provide an interlocked warning light or physical barriers, warning signs, wheel chocks, or vehicle brake interlock system in the area adjacent to the loading/unloading rack to prevent vehicles from departing before complete disconnection of flexible or fixed oil transfer lines when a loading/unloading rack is present at the facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(h)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 45 | General SPCC Requirements | Loading/Unloading Racks | Vehicular departure warning system in place at facility with a loading/unloading rack | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide an interlocked warning light or physical barriers, warning signs, wheel chocks, or vehicle brake interlock system in the area adjacent to the loading/unloading rack to prevent vehicles from departing before complete disconnection of flexible or fixed oil transfer lines when a loading/unloading rack is present at the facility. |  |  | OBSERVATION: Failure to provide an interlocked warning light or physical barriers, warning signs, wheel chocks, or vehicle brake interlock system in the area adjacent to the loading/unloading rack to prevent vehicles from departing before complete disconnection of flexible or fixed oil transfer lines when a loading/unloading rack is present at the facility. CORRECTIVE ACTION: Provide interlocked warning lights, physical barriers, warning signs, wheel chocks or vehicle brake interlock system in the area adjacent to the loading/unloading rack to prevent vehicles from departing before complete disconnection of flexible or fixed oil transfer lines | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010040 |  |  | Brittle fracture evaluation documentation | Failure to document evaluation of field-constructed aboveground tanks or containers for risk of discharge or failure due to brittle fracture or other catastrophe after tank undergoes repairs, alterations, reconstruction, or change in service. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(i) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 46 | General SPCC Requirements | Brittle Fracture | Documented evaluation of field-constructed tanks for risk of discharge due to brittle fracture | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document evaluation of field-constructed aboveground tanks or containers for risk of discharge or failure due to brittle fracture or other catastrophe after tank undergoes repairs, alterations, reconstruction, or change in service. |  |  | OBSERVATION: Failure to document the evaluation of all field-constructed tanks for their risk of discharge due to brittle fracture or other catastrophe. This pertains to the [repair, alteration, reconstruction, change in service] of [describe affected tanks] that are currently at risk of discharge or failure due to brittle fracture. CORRECTIVE ACTION: Immediately conduct and document an evaluation of the impacted tanks and take any appropriate corrective action. | [6 empty] | No | Yes | No | No
APSA Program | Operations/Maintenance | 4030016 |  |  | Risk Analysis – Field constructed tanks | Failure to perform a brittle fracture evaluation of field-constructed aboveground tanks after tank repair, alteration, reconstruction, or change in service that might affect the risk of a discharge, and take appropriate action. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(i) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 47 | General SPCC Requirements | Brittle Fracture | Brittle fracture evaluation of field-constructed aboveground tanks performed | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform a brittle fracture evaluation of field-constructed aboveground tanks after tank repair, alteration, reconstruction, or change in service that might affect the risk of a discharge, and take appropriate action. |  |  | OBSERVATION: Failure to perform a brittle fracture evaluation of field-constructed aboveground tanks after tank repair, alteration, reconstruction, or change in service that might affect the risk of a discharge, and take appropriate action. CORRECTIVE ACTION: Perform a brittle fracture evaluation of field-constructed aboveground tanks after tank repair, alteration, reconstruction, or change in service that might affect the risk of a discharge, and take appropriate action. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030034 |  |  | Containment for qualified oil-filled operational equipment | Failure to provide general secondary containment or failure to fulfill alternative requirements to general secondary containment for oil-filled operational equipment. | 40 CFR 1 112.7(k); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(5) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 48 | General SPCC Requirements | Oil-Filled Operation Equipment | Oil filled operational equipment containment standards are met | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide general secondary containment or failure to fulfill alternative requirements to general secondary containment for oil-filled operational equipment. |  |  | OBSERVATION: Failure to provide general secondary containment or failure to fulfill alternative requirements to general secondary containment for oil-filled operational equipment. CORRECTIVE ACTION: Provide items needed to satisfy conditions of general secondary containment or demonstrate how alternate oil containment standards for oil filled operational equipment are being met. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010027 |  |  | Facility Drainage | Failure to adequately discuss in the SPCC Plan facility drainage or drainage controls such as secondary containment around containers and other structures, equipment, and procedures for the control of a discharge. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(a)(3)(iii); 112.8(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 49 | SPCC Requirements for Onshore Facilities | Drainage | Facility drainage or drainage controls adequately discussed | 59 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately discuss in the SPCC Plan facility drainage or drainage controls such as secondary containment around containers and other structures, equipment, and procedures for the control of a discharge. |  |  | OBSERVATION: Failure to adequately discuss facility drainage or drainage controls, or no discussion of facility drainage included within the SPCC plan. CORRECTIVE ACTION: Revise SPCC plan to adequately discuss facility drainage or drainage controls. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030035 |  |  | Facility drainage from diked storage areas | Failure to ensure drainage from diked storage areas is restrained by valves, except where facility systems are designed to control such discharge, or failure to ensure manually activated pumps or ejectors are used and the condition of the accumulation is inspected prior to draining. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(b)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 50 | SPCC Requirements for Onshore Facilities | Drainage | Facility drainage adequately restrained unless conditions met | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately use valves to restrain drainage from diked storage areas unless system designed to control drainage, or failure to use manually activated pumps to empty diked areas, and/or failure to inspect condition of accumulation prior to draining. |  |  | OBSERVATION: Failure to adequately use valves to restrain drainage from diked storage areas or failure to use manually activated pumps to empty diked areas, and/or failure to inspect condition of accumulation prior to draining. CORRECTIVE ACTION: Ensure that valves remain closed to prevent drainage from diked areas, only use manually activated pumps to empty diked areas, and inspect condition of accumulation prior to draining. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030005 |  |  | Valves for drainage of diked areas | Failure to use drain valves in diked storage areas that are manual, open-and-closed design (not flapper-type drain valves). | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(b)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 51 | SPCC Requirements for Onshore Facilities | Drainage | Valves used for drainage are manual (not flapper-type) to prevent a discharge | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to use drain valves in diked storage areas that are manual, open-and-closed design (not flapper-type drain valves). |  |  | OBSERVATION: Failure to use drain valves in diked storage areas that are manual, open-and-closed design (not flapper-type drain valves). CORRECTIVE ACTION: Use drain valves in diked storage areas that are manual, open-and-closed design (not flapper-type drain valves). | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030008 |  |  | Drainage from undiked areas | Failure to design drainage from undiked areas to either: 1. Flow into catchment basins, ponds, or lagoons to retain oil or return it to the facility. OR 2. Equip the facility with a diversion system that would retain oil in the facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(b)(3), 112.8(b)(4) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 52 | SPCC Requirements for Onshore Facilities | Drainage | Drainage from undiked areas or diversion systems designed to retain final discharge in facility | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to design drainage from undiked areas to either: 1. Flow into catchment basins, ponds, or lagoons to retain oil or return it to the facility. OR 2. Equip the facility with a diversion system that would retain oil in the facility. |  |  | OBSERVATION: Failure to design drainage from undiked areas to either: 1. Flow into catchment basins, ponds, or lagoons to retain oil or return it to the facility. OR 2. Equip the facility with a diversion system that would retain oil in the facility. CORRECTIVE ACTION: Design drainage from undiked areas to flow into catchment basins ponds, or lagoons, or, equip the facility with a diversion system that would retain oil in the facility. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030009 |  |  | Lift pumps for treated drainage water | Failure to provide two lift pumps, and permanently install at least one of the pumps, if facility drainage waters are continuously treated in more than one treatment unit and pump transfer is needed. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(b)(5) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 53 | SPCC Requirements for Onshore Facilities | Drainage | Lift pumps provided for treated drainage waters when more than one treatment unit | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide two lift pumps, and permanently install at least one of the pumps, if facility drainage waters are continuously treated in more than one treatment unit and pump transfer is needed. |  |  | OBSERVATION: Failure to provide two lift pumps, and permanently install at least one of the pumps, where drainage waters are continuously treated in more than one treatment unit and pump transfer is needed. CORRECTIVE ACTION: Provide two lift pumps, and permanently install at least one of the pumps, for drainage waters that are continuously treated in more than one treatment unit and pump transfer is needed. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010029 |  |  | Bulk Storage Containers | Failure to adequately discuss in the SPCC Plan all applicable bulk storage containers, including compatibility with material stored and conditions of storage, and description of sized secondary containment capable of containing the largest single container and sufficient freeboard to contain precipitation. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.8(c)(1)&(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 54 | SPCC Requirements for Onshore Facilities | Bulk Storage Container-SPCC Plan/Compatibility | Adequate discussion of all bulk storage containers located at the facility | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately discuss in the SPCC Plan all applicable bulk storage containers, including compatibility with material stored and conditions of storage, and description of sized secondary containment capable of containing the largest single container and sufficient freeboard to contain precipitation. |  |  | OBSERVATION: SPCC plan does not adequately discuss all bulk storage containers, including compatibility with material stored and conditions of storage, and description of sized secondary containment capable of containing the largest single container and sufficient freeboard to contain precipitation. CORRECTIVE ACTION: Amend the SPCC Plan to address all bulk storage containers stored at this facility. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030012 |  |  | Tanks compatible with stored materials | Failure to use containers with material and construction compatible with material stored and conditions of storage such as pressure and temperature. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 55 | SPCC Requirements for Onshore Facilities | Bulk Storage Container-SPCC Plan/Compatibility | Material and construction of all containers are compatible with the material stored | 83 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to use containers with material and construction compatible with material stored and conditions of storage such as pressure and temperature. |  |  | OBSERVATION: Failure to use containers with material and construction compatible with material stored and conditions of storage such as pressure and temperature. CORRECTIVE ACTION: Immediately remove all oil stored in non-compatible containers. Store oil in containers with material and construction compatible with the material stored and conditions of storage such as pressure and temperature. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030047 |  |  | Tank designed for underground application used as AST | Tank facility is using a tank designed and intended for underground use, or a tank used for that purpose, as an aboveground storage tank (AST). | 19 CCR 11 1601, 1607(b) | 2025-07-01 | 2099-12-31 | 2025-07-01 | New | 56 | SPCC Requirements for Onshore Facilities | Bulk Storage Container-SPCC Plan/Compatibility | No tank designed and intended for underground use is being used as an AST | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Tank facility is using a tank designed and intended for underground use, or a tank used for that purpose, as an aboveground storage tank (AST). |  |  | OBSERVATION: Owner/Operator is using a tank designed and intended for underground use as an aboveground storage tank. CORRECTIVE ACTION: Discontinue use of underground storage tanks for aboveground storage. Empty tank and manage as permanently closed tank until properly disposed of. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030048 |  |  | Rail car, tank car, or tank vehicle used as permanent or fixed AST | Tank facility is using a rail car, tank car, or tank vehicle as a storage tank in a permanent or fixed installation. | 19 CCR 11 1601, 1607(c) | 2025-07-01 | 2099-12-31 | 2025-07-01 | New | 57 | SPCC Requirements for Onshore Facilities | Bulk Storage Container-SPCC Plan/Compatibility | No rail cars, tank cars, or tank vehicles used as a storage tank in a permanent/fixed installation | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Tank facility is using a rail car, tank car, or tank vehicle as a storage tank in a permanent or fixed installation. |  |  | OBSERVATION: Owner/Operator is using a rail car, tank car, or tank vehicle as a storage tank in a permanent or fixed installation. CORRECTIVE ACTION: Discontinue use of rail car, tank car, or tank vehicle as a storage tank in a permanent or fixed installation. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030010 |  |  | Sized secondary containment | Failure to provide and maintain secondary containment for bulk storage tank installations (except for mobile refuelers and other non-transportation-related tank trucks) sufficient to hold the capacity of the largest container and sufficient freeboard for precipitation. | 40 CFR 1 112.8(c)(2); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(5) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 58 | SPCC Requirements for Onshore Facilities | Secondary Containment | Adequately sized secondary containment provided and maintained for bulk storage containers | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide and maintain secondary containment for bulk storage tank installations (except for mobile refuelers and other non-transportation-related tank trucks) sufficient to hold the capacity of the largest container and sufficient freeboard for precipitation. |  |  | OBSERVATION: Failure to provide and maintain secondary containment for bulk storage tank installations sufficient to hold the capacity of the largest container and sufficient freeboard for precipitation. CORRECTIVE ACTION: Provide and maintain adequate secondary containment for bulk storage containers. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030041 |  |  | Tier I - Bulk storage container sized secondary containment | Failure to provide bulk storage containers with adequate secondary containment large enough to contain the entire capacity of the largest container plus additional capacity to contain precipitation when applicable, and/or failure to position/locate mobile or portable containers to prevent a discharge. | 40 CFR 1 112.6(a)(3)(ii); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(5) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 59 | SPCC Requirements for Onshore Facilities | Secondary Containment | All bulk storage containers have secondary containment to prevent a discharge at Tier I facility | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide bulk storage containers with adequate secondary containment large enough to contain the entire capacity of the largest container plus additional capacity to contain precipitation when applicable, and/or failure to position/locate mobile or portable containers to prevent a discharge. |  |  | OBSERVATION: Bulk storage containers do not have adequate secondary containment. CORRECTIVE ACTION: Provide secondary containment for bulk storage containers large enough to contain the entire capacity of the largest container plus additional capacity to contain precipitation. | [6 empty] | No | No | Yes | No
APSA Program | Operations/Maintenance | 4030043 |  |  | Secondary containment and leak detection for TIUGA piping | Failure to have secondary containment and leak detection if piping connected to a tank in an underground area (TIUGA) cannot be directly viewed for the entire length of the piping that is beneath the surface of the ground. This does not apply to: 1. Piping connected to a tank that contains new oil/used oil for lubricant or coolant in a motor engine or transmission, or oil-filled operational/manufacturing equipment. 2. Piping connected to a tank used solely in connection with a fire pump or emergency system, legally required standby system, or optional standby system. 3. Piping connected to a petroleum hazardous waste tank that complies with hazardous waste tank standards (22 CCR Ch. 15, Art. 10) and facility has been issued a unified program facility permit pursuant to HSC Section 25404.2 for generation, treatment, accumulation, or storage of hazardous waste. | HSC 6.67 25270.2(o)(1)(C)(iv) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 60 | SPCC Requirements for Onshore Facilities | Secondary Containment | Secondary containment and leak detection provided for TIUGA piping if not viewable on all sides | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have secondary containment and leak detection if piping connected to a tank in an underground area (TIUGA) cannot be directly viewed for the entire length of the piping that is beneath the surface of the ground. This does not apply to: 1. Piping connected to a tank that contains new oil/used oil for lubricant or coolant in a motor engine or transmission, or oil-filled operational/manufacturing equipment. 2. Piping connected to a tank used solely in connection with a fire pump or emergency system, legally required standby system, or optional standby system. 3. Piping connected to a petroleum hazardous waste tank that complies with hazardous waste tank standards (22 CCR Ch. 15, Art. 10) and facility has been issued a unified program facility permit pursuant to HSC Section 25404.2 for generation, treatment, accumulation, or storage of hazardous waste. |  |  | OBSERVATION: Owner/Operator failed to provide secondary containment and leak detection for piping connected to a tank in an underground area (TIUGA) that cannot be directly viewed for the entire length of the piping that is beneath the surface of the ground. [Not applicable to piping connected to tank containing new/used oil used for lube or coolant in engine/transmission, oil-filled equipment, piping connected to tank used for fire pump or emergency system, or for piping connected to permitted hazardous waste tank]. CORRECTIVE ACTION: Provide secondary containment and leak detection for piping connected to a tank in an underground area (TIUGA) that cannot be directly viewed for the entire length of the piping that is beneath the surface of the ground. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030013 |  |  | Diked areas sufficiently impervious to oil | Failure to ensure that containment systems of diked areas in all bulk storage tank installations are either: 1. Sufficiently impervious to contain discharged oil until cleaned up. OR 2. Any discharge to a drainage trench system will be safely confined in a facility catchment basin or holding pond until cleaned up. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 61 | SPCC Requirements for Onshore Facilities | Secondary Containment | Containment systems are sufficiently impervious to contain oil | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that containment systems of diked areas in all bulk storage tank installations are either: 1. Sufficiently impervious to contain discharged oil until cleaned up. OR 2. Any discharge to a drainage trench system will be safely confined in a facility catchment basin or holding pond until cleaned up. |  |  | OBSERVATION: Failure to ensure that containment systems of diked areas in all bulk storage tank installations are either: 1. Sufficiently impervious to contain discharged oil until cleaned up. OR 2. Discharge to a drainage trench system that is safely confined in a facility catchment basin or holding pond until cleaned up. CORRECTIVE ACTION: Maintain/Install containment systems, including walls and floors to be sufficiently impervious to contain oil. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030006 |  |  | Drainage inspections and valves | Failure to ensure the following before allowing drainage of uncontaminated rainwater from diked area into a storm drain or discharge of an effluent into an open watercourse, lake, or pond, bypassing the facility treatment system: 1. Keep bypass valve normally sealed closed. 2. Inspect the retained rainwater. 3. Open and reseal bypass valves under responsible supervision. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(3)(i), 112.8(c)(3)(ii), 112.8(c)(3)(iii) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 62 | SPCC Requirements for Onshore Facilities | Drainage Inspections/Records | Rainwater in diked areas is inspected before draining | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the following before allowing drainage of uncontaminated rainwater from diked area into a storm drain or discharge of an effluent into an open watercourse, lake, or pond, bypassing the facility treatment system: 1. Keep bypass valve normally sealed closed. 2. Inspect the retained rainwater 3. Open and reseal bypass valves under responsible supervision. |  |  | OBSERVATION: Failure to ensure the following before allowing drainage of uncontaminated rainwater from diked area into a storm drain or discharge of an effluent into an open watercourse, lake, or pond, bypassing the facility treatment system: 1. Keep bypass valve normally sealed closed. 2. Inspect the retained rainwater 3. Open and reseal bypass valves under responsible supervision. CORRECTIVE ACTION: Before draining rainwater from diked areas be sure to Inspect the retained rainwater, and open and reseal bypass valves under responsible supervision. Keep bypass valve normally sealed closed. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010026 |  |  | Drainage records | Failure to maintain adequate records of drainage when there is drainage of uncontaminated rainwater from diked areas into a storm drain or open watercourse; for example, records required under NPDES permit. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(3)(iv) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 63 | SPCC Requirements for Onshore Facilities | Drainage Inspections/Records | Records maintained of drainage from diked areas | 47 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain adequate records of drainage when there is drainage of uncontaminated rainwater from diked areas into a storm drain or open watercourse; for example, records required under NPDES permit. |  |  | OBSERVATION: Failure to maintain adequate records (or NPDES permit records) of drainage from diked areas. CORRECTIVE ACTION: Maintain adequate records (or NPDES permit records) of drainage from diked areas. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030017 |  |  | Corrosion Protection | Failure to protect the buried section of a partially buried or bunkered metallic tank from corrosion by coatings or cathodic protection compatible with local soil conditions. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(5) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 64 | SPCC Requirements for Onshore Facilities | Cathodic Protection | Buried section of partially buried or bunkered metallic tank has corrosion protection | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to protect the buried section of a partially buried or bunkered metallic tank from corrosion by coatings or cathodic protection compatible with local soil conditions. |  |  | OBSERVATION: Failure to protect the buried section of a partially buried or bunkered metallic tank from corrosion. CORRECTIVE ACTION: Provide corrosion protection for partially buried tanks. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030046 |  |  | Corrosion protection of piping and components | Failure to ensure all piping and supporting components that are susceptible to corrosion and associated with an aboveground storage tank are provided with protection from external corrosion and designed to prevent galvanic corrosion. | 19 CCR 11 1601, 1606 | 2025-07-01 | 2099-12-31 | 2025-07-01 | New | 65 | SPCC Requirements for Onshore Facilities | Cathodic Protection | All piping and supporting components associated with AST are protected from external corrosion | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure all piping and supporting components that are susceptible to corrosion and associated with an aboveground storage tank are provided with protection from external corrosion and designed to prevent galvanic corrosion. |  |  | OBSERVATION: Owner/Operator failed to ensure all piping and supporting components that are susceptible to corrosion and are associated with an AST are provided with protection from external corrosion and designed to prevent galvanic corrosion. CORRECTIVE ACTION: Make necessary modifications to piping and supporting components to provide protection from external corrosion and prevent galvanic corrosion. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010028 |  |  | Integrity testing and inspection procedures | Failure to discuss in the SPCC Plan procedures to test or inspect each aboveground container for integrity in accordance with industry standards: 1. On a regular schedule. 2. After material repairs are made. 3. By qualified personnel. 4. The frequency and type of testing and inspections based on container size, configuration, and design. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.8(c)(6) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 66 | SPCC Requirements for Onshore Facilities | Inspections & Testing | SPCC discusses procedures to test/inspect storage containers for integrity per industry standards | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to discuss in the SPCC Plan procedures to test or inspect each aboveground container for integrity in accordance with industry standards: 1. On a regular schedule. 2. After material repairs are made. 3. By qualified personnel. 4. The frequency and type of testing and inspections based on container size, configuration, and design. |  |  | OBSERVATION: SPCC Plan does not adequately discuss procedures to test or inspect each aboveground container for integrity in accordance with industry standards, and/or does not address one or more of the following: Inspections and testing completed on a regular schedule, after material repairs are made, by qualified personnel, the frequency and type of testing and inspections based on container size, configuration, and design. CORRECTIVE ACTION: Revise SPCC Plan to adequately discuss facility's procedures to test and inspect aboveground/bulk storage containers in accordance with specified industry standards. This must include, but not be limited to, inspection/testing schedule/frequency, and personnel qualifications. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030014 |  |  | Tanks inspected or tested by qualified person | Failure to ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. | 40 CFR 1 112.7(e), 112.8(c)(6); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(6) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 67 | SPCC Requirements for Onshore Facilities | Inspections & Testing | Tanks inspected and tested by qualified person in accordance with industry standards | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. |  |  | OBSERVATION: Failure to ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. CORRECTIVE ACTION: Ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030015 |  |  | Tanks inspected and/or integrity tested | Failure to test or inspect each aboveground container for integrity based on industry standards: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. | 40 CFR 1 112.7(e), 112.8(c)(6); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(6) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 68 | SPCC Requirements for Onshore Facilities | Inspections & Testing | Aboveground containers tested or inspected for integrity based on industry standards | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to test or inspect each aboveground container for integrity based on industry standards: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. |  |  | OBSERVATION: Failure to test or inspect each aboveground container for integrity based on industry standards: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. CORRECTIVE ACTION: Test or inspect each aboveground container for integrity based on industry standards on a regular schedule, after making material repairs, using non-destructive testing, inspecting each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. Maintain testing and inspection records. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030045 |  |  | Direct Viewing and leak detection for TIUGA | Failure to meet one of the following criteria for a tank in an underground area (TIUGA): 1. The structure in which the tank is located provides enough space for direct viewing of the exterior of the tank except for the part of the tank in contact with the surface of the floor. OR 2. Inspections of the interstitial space or containment structure are performed, or the tank has a mechanical or electronic device that will detect leaks in the interstitial space or containment structure and alert the tank operator. Direct viewing does not apply to a tank that stores hazardous waste petroleum and meets the requirements of CCR Title 22. | HSC 6.67 25270.2(o)(1)(C)(i), (iii), (iv)(III), 25270.2(o)(2) | 2023-07-01 | 2099-12-31 | 2023-07-01 | Revised | 69 | SPCC Requirements for Onshore Facilities | Inspections & Testing | TIUGAs meet requirements for direct viewing or inspections/ leak detection | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to meet one of the following criteria for a tank in an underground area (TIUGA): 1. The structure in which the tank is located provides enough space for direct viewing of the exterior of the tank except for the part of the tank in contact with the surface of the floor. OR 2. Inspections of the interstitial space or containment structure are performed, or the tank has a mechanical or electronic device that will detect leaks in the interstitial space or containment structure and alert the tank operator. Direct viewing does not apply to a tank that stores hazardous waste petroleum and meets the requirements of CCR Title 22. |  |  | OBSERVATION: Owner/Operator failed to meet one of the following criteria for a tank in an underground area (TIUGA): 1. The structure in which the tank is located provides enough space for direct viewing of the exterior of the tank except for the part of the tank in contact with the surface of the floor. OR; 2. Inspections of the interstitial space or containment structure are performed, or the tank has a mechanical or electronic device that will detect leaks in the interstitial space or containment structure and alert the tank operator. Direct viewing does not apply to a tank that stores hazardous waste petroleum and meets the requirements of CCR Title 22. CORRECTIVE ACTION: Begin implementing one of the two options and provide documentation of compliance. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010021 |  |  | Written records of inspections and tests | Failure to comply with one or more of the following requirements: 1. Have record of inspections and tests, including integrity tests, signed by the appropriate supervisor or inspector. 2. Keep written procedures and records of inspections and tests, including integrity tests, for at least three years. 3. Keep comparison records for bulk storage tanks subject to 40 CFR 112.8(c)(6). | 40 CFR 1 112.7(a)(1), 112.7(e), 112.8(c)(6); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(6) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 70 | SPCC Requirements for Onshore Facilities | Inspections & Testing | Written Inspection/testing procedures kept, inspection/testing records signed, kept for 3 years | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with one or more of the following requirements: 1. Have record of inspections and tests, including integrity tests, signed by the appropriate supervisor or inspector. 2. Keep written procedures and records of inspections and tests, including integrity tests, for at least three years. 3. Keep comparison records for bulk storage tanks subject to 40 CFR 112.8(c)(6). |  |  | OBSERVATION: Failure to comply with one or more of the following requirements: 1. Have record of inspections and tests, including integrity tests, signed by the appropriate supervisor or inspector. 2. Keep written procedures and records of inspections and tests, including integrity tests, for at least three years. 3. Keep comparison records for bulk storage containers subject to 40 CFR 112.8(c)(6). CORRECTIVE ACTION: Keep written inspection procedures, records of inspections and testing, signed by appropriate supervisor/inspector, for at least 3 years. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030018 |  |  | Steam return/exhaust monitored | Failure to monitor the steam return and exhaust lines of any internal heating coils for contamination if they discharge into an open watercourse, or failure to pass the steam return and exhaust lines through a settling tank, skimmer, or other separation or retention system. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(7) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 71 | SPCC Requirements for Onshore Facilities | Steam Return/Exhaust | Steam return/exhaust lines that discharge to watercourse are monitored or have treatment system | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to monitor the steam return and exhaust lines of any internal heating coils for contamination if they discharge into an open watercourse, or failure to pass the steam return and exhaust lines through a settling tank, skimmer, or other separation or retention system. |  |  | OBSERVATION: Failure to monitor the steam return and exhaust lines of any internal heating coils for contamination, or failure to pass the steam return and exhaust lines through a separation or retention system. CORRECTIVE ACTION: Monitor or implement a treatment system for steam return/exhaust of internal heating coils which discharge into a water course. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010056 |  |  | Overfill prevention | Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the devices or systems in place for each container to prevent overfills. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.8(c)(8) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 72 | SPCC Requirements for Onshore Facilities | Overfill Prevention | SPCC adequately describes overfill prevention methods, and devices/systems used for each container | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the devices or systems in place for each container to prevent overfills. |  |  | OBSERVATION: Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the devices or systems in place for each container to prevent overfills. CORRECTIVE ACTION: Update SPCC plan to properly address overfill prevention methods, including a description of the devices or systems in place for each container to prevent overfills. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010055 |  |  | Tier I - Overfill prevention | Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the systems or procedures used to prevent overfills for each container. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(3)(iii) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 73 | SPCC Requirements for Onshore Facilities | Overfill Prevention | SPCC plan adequately describes overfill prevention methods, including system or procedures used | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the systems or procedures used to prevent overfills for each container. |  |  | OBSERVATION: Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the systems or procedures used to prevent overfills for each container. CORRECTIVE ACTION: Update SPCC plan to properly address overfill prevention methods, including a description of the systems or procedures used to prevent overfills for each container. | [6 empty] | No | No | Yes | No
APSA Program | Operations/Maintenance | 4030042 |  |  | Tier I - Overfill prevention implementation | Failure to provide systems or follow procedures to prevent overfills as described in the SPCC Plan, and/or failure to routinely test to ensure proper operation. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(3)(iii) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 74 | SPCC Requirements for Onshore Facilities | Overfill Prevention | Overfill prevention systems or procedures are used and tested routinely to ensure proper operation | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide systems or follow procedures to prevent overfills as described in the SPCC Plan, and/or failure to routinely test to ensure proper operation. |  |  | OBSERVATION: Failure to provide systems or follow procedures to prevent overfills as described in the SPCC Plan, and/or failure to routinely test to ensure proper operation. CORRECTIVE ACTION: Provide systems or begin following procedures to prevent overfills as described in SPCC plan, and routinely test systems or devices used to prevent overfilling. | [6 empty] | No | No | Yes | No
APSA Program | Operations/Maintenance | 4030019 |  |  | Overfill prevention implementation | Failure to engineer or update each container installation in accordance with good engineering practice to avoid discharges and/or failure to provide at least one of the following devices on each container installation: 1. An audible or visual high liquid level alarm. 2. High liquid level pump cutoff devices. 3. Audible or code signal communications between tank gauger and pumping station. 4. A fast response system for determining liquid levels, such as computers, telepulse or direct vision gauges. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(8), 112.8(c)(8)(i), 112.8(c)(8)(ii), 112.8(c)(8)(iii), 112.8(c)(8)(iv) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 75 | SPCC Requirements for Onshore Facilities | Overfill Prevention | Each container installation has a liquid level sensing device. | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to engineer or update each container installation in accordance with good engineering practice to avoid discharges and/or failure to provide at least one of the following devices on each container installation: 1. An audible or visual high liquid level alarm. 2. High liquid level pump cutoff devices. 3. Audible or code signal communications between tank gauger and pumping station. 4. A fast response system for determining liquid levels, such as computers, telepulse or direct vision gauges. |  |  | OBSERVATION: Failure to engineer or update each container installation in accordance with good engineering practice to avoid discharges and/or failure to provide for each container installation: An audible or visual high liquid level alarm; High liquid level pump cutoff devices; Audible or code signal communications between tank gauger and pumping station; or A fast response system for determining liquid levels, such as computers, telepulse or direct vision gauges. CORRECTIVE ACTION: Provide at least one of the required items listed for each container installation. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030022 |  |  | Testing of liquid level sensing devices | Failure to regularly test liquid level sensing devices to ensure proper operation. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(8)(v) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 76 | SPCC Requirements for Onshore Facilities | Overfill Prevention | Liquid level sensing devices regularly tested to ensure proper operation | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to regularly test liquid level sensing devices to ensure proper operation. |  |  | OBSERVATION: Failure to regularly test liquid level sensing devices to ensure proper operation. CORRECTIVE ACTION: Test liquid level sensing devices to ensure proper operation. Submit test results | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030023 |  |  | Observation of effluent discharge to navigable waters | Failure to observe effluent treatment facilities frequently enough to detect possible system upsets that could cause a discharge as described in 40 CFR 112.1(b). | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(9) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 77 | SPCC Requirements for Onshore Facilities | Effluent Treatment | Discharge from effluent treatment facilities which discharge to navigable waterways observed | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to observe effluent treatment facilities frequently enough to detect possible system upsets that could cause a discharge as described in 40 CFR 112.1(b). |  |  | OBSERVATION: Failure to observe effluent treatment facilities frequently enough to detect possible system upsets that could cause a discharge. CORRECTIVE ACTION: Observe effluent treatment facilities frequently enough to detect possible system upsets that could cause a discharge. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030021 |  |  | Leaks addressed and oil removed | Failure to promptly correct visible discharges and promptly remove any accumulations of oil in diked areas. | 40 CFR 1 112.8(c)(10); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(8) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 78 | SPCC Requirements for Onshore Facilities | Response to Release | Visible discharges promptly corrected and any accumulation of oil in diked areas promptly removed. | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to promptly correct visible discharges and promptly remove any accumulations of oil in diked areas. |  |  | OBSERVATION: Failure to promptly correct visible discharges and promptly remove any accumulations of oil in diked areas. CORRECTIVE ACTION: Promptly correct any visible discharges and promptly remove any accumulations of oil in diked areas. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030020 |  |  | Mobile or portable storage container positioning and sized containment | Failure to position or locate mobile or portable storage containers to prevent a discharge as described in 40 CFR 112.1(b), and/or failure to provide adequate secondary containment for mobile or portable oil storage containers (excluding mobile refuelers and other non-transportation-related tank trucks) with sufficient capacity to contain the largest single compartment or container and sufficient freeboard to contain precipitation. | 40 CFR 1 112.8(c)(11); HSC 6.67 25270.4.5(a); 19 CCR 11 1601, 1611(a)(5) | 2025-07-01 | 2099-12-31 | 2025-07-01 | Revised | 79 | SPCC Requirements for Onshore Facilities | Mobile/Portable Container | Adequate secondary containment provided for mobile/portable storage containers | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to position or locate mobile or portable storage containers to prevent a discharge as described in 40 CFR 112.1(b), and/or failure to provide adequate secondary containment for mobile or portable oil storage containers (excluding mobile refuelers and other non-transportation-related tank trucks) with sufficient capacity to contain the largest single compartment or container and sufficient freeboard to contain precipitation. |  |  | OBSERVATION: Failure to position or locate mobile or portable storage containers to prevent a discharge as described in 40 CFR 112.1(b), and/or failure to provide mobile or portable oil storage containers (excluding mobile refuelers and other non-transportation-related tank trucks) with adequate secondary containment with sufficient capacity to contain the largest single compartment or container and sufficient freeboard to contain precipitation. CORRECTIVE ACTION: Position or locate mobile or portable storage containers to prevent a discharge, and/or provide adequate secondary containment for mobile or portable oil storage tanks. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010058 |  |  | Piping | Failure to include in the SPCC Plan, when required, a discussion of aboveground piping, buried piping, piping inspections, or vehicle warnings. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.8(d)(1), (4) & (5) | 2023-07-01 | 2099-12-31 | 2023-07-01 | Revised | 80 | SPCC Requirements for Onshore Facilities | Piping | SPCC Plan discusses aboveground piping, buried piping, piping inspections, and vehicle warnings | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include in the SPCC Plan a discussion of aboveground piping, buried piping, piping inspections, or vehicle warnings. |  |  | OBSERVATION: SPCC Plan does not discuss, or inadequatly describes aboveground piping, buried piping, piping inspections, or vehicle warnings. CORRECTIVE ACTION: Update SPCC Plan to include a discussion of aboveground piping, buried piping, piping inspections, and vehicle warnings. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030025 |  |  | Inspection and/or repair of buried piping | Failure to inspect for deterioration any section of buried piping that is exposed for any reason, and to undertake additional examination and corrective action if corrosion damage is found. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 81 | SPCC Requirements for Onshore Facilities | Piping | Buried piping is inspected for deterioration if exposed and repaired if corrosion damage is found | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to inspect for deterioration any section of buried piping that is exposed for any reason, and to undertake additional examination and corrective action if corrosion damage is found. |  |  | OBSERVATION: Failure to inspect for deterioration any section of buried piping that is exposed for any reason, and to undertake additional examination and corrective action if corrosion damage is found. CORRECTIVE ACTION: Inspect for deterioration any buried piping that is exposed and undertake corrective action if corrosion damage is found. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030027 |  |  | Protection of buried piping | Failure to provide buried piping that is installed or replaced on or after August 16, 2002, with a protective wrapping or coating, and to ensure it is cathodically protected or otherwise satisfies the corrosion protection standards for piping in 40 CFR part 280 or 281. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 82 | SPCC Requirements for Onshore Facilities | Piping | Buried piping is corrosion protected with protective wrapping, coating, or cathodic protection | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide buried piping that is installed or replaced on or after August 16, 2002, with a protective wrapping or coating, and to ensure it is cathodically protected or otherwise satisfies the corrosion protection standards for piping in 40 CFR part 280 or 281. |  |  | OBSERVATION: Failure to provide buried piping with protective wrapping or coating, and to ensure it is cathodically protected or otherwise satisfies corrosion protection standards for piping. CORRECTIVE ACTION: Provide buried piping with protective wrapping or coating, or cathodic protection. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030028 |  |  | Stand-by piping | Failure to cap or blank-flange the terminal connection at the transfer point and mark it as to origin when piping is not in service or is in standby service for an extended time. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(2) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 83 | SPCC Requirements for Onshore Facilities | Piping | Terminal connection capped/blank flanged at transfer point & origin marked if not in service/standby | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to cap or blank-flange the terminal connection at the transfer point and mark it as to origin when piping is not in service or is in standby service for an extended time. |  |  | OBSERVATION: Failure to cap or blank-flange the terminal connection at the transfer point and mark it as to origin when piping is not in service or is in standby service for an extended time. CORRECTIVE ACTION: Cap or blank-flange the terminal connection at the transfer point and label as to origin. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030029 |  |  | Piping supports | Failure to properly design pipe supports to minimize abrasion and corrosion, and allow for expansion and contraction. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(3) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 84 | SPCC Requirements for Onshore Facilities | Piping | Pipe supports designed to minimize abrasion and corrosion, and allow for expansion and contraction | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly design pipe supports to minimize abrasion and corrosion, and allow for expansion and contraction. |  |  | OBSERVATION: Failure to properly design pipe supports to minimize abrasion and corrosion, and allow for expansion and contraction. CORRECTIVE ACTION: Design and install pipe supports to minimize abrasion and corrosion, and allow for expansion and contraction. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030026 |  |  | Inspection of aboveground piping | Failure to regularly inspect aboveground valves, piping, and appurtenances. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(4) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 85 | SPCC Requirements for Onshore Facilities | Piping | Aboveground valves, piping, and appurtenances are regularly inspected | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to regularly inspect aboveground valves, piping, and appurtenances. |  |  | OBSERVATION: Failure to regularly inspect aboveground valves, piping, and appurtenances. CORRECTIVE ACTION: Regularly inspect aboveground valves, piping, and appurtenances. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030030 |  |  | Testing of buried piping | Failure to perform integrity and leak testing of buried piping at the time of installation, modification, construction, relocation, or replacement. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(4) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 86 | SPCC Requirements for Onshore Facilities | Piping | Integrity/leak tested buried piping when installed, modified, constructed, relocated, or replaced | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform integrity and leak testing of buried piping at the time of installation, modification, construction, relocation, or replacement. |  |  | OBSERVATION: Failure to perform integrity and leak testing of buried piping at the time of installation, modification, construction, relocation, or replacement. CORRECTIVE ACTION: Perform integrity and leak testing of buried piping at the time of installation, modification, construction, relocation, or replacement. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030031 |  |  | Warning to vehicles about aboveground piping | Failure to warn vehicle traffic regarding aboveground piping or other oil transfer operations. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(5) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 87 | SPCC Requirements for Onshore Facilities | Piping | Vehicle traffic warned of aboveground piping or other oil transfer operations | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to warn vehicle traffic regarding aboveground piping or other oil transfer operations. |  |  | OBSERVATION: Failure to warn vehicle traffic about aboveground piping or other oil transfer operations. CORRECTIVE ACTION: Warn vehicle traffic about aboveground piping or other oil transfer operations. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030044 |  |  | Excluded TIUGA with less than 55-gallon capacity | Failure of an owner/operator of an excluded tank in an underground area (TIUGA) with less than 55-gallon capacity to have secondary containment, conduct monthly inspections, and/or maintain a log of inspections. | HSC 6.67 25270.2(a)(8) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 88 | Excluded TIUGA Requirements |  | Excluded TIUGA <55 gal has secondary containment, inspected monthly and log of inspections kept | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of an owner/operator of an excluded tank in an underground area (TIUGA) with less than 55-gallon capacity to have secondary containment, conduct monthly inspections, and/or maintain a log of inspections. |  |  | OBSERVATION: Owner/operator of an excluded tank in an underground area (TIUGA) with less than 55-gallon capacity failed to have secondary containment, conduct monthly inspections, and/or maintain a log of inspections. CORRECTIVE ACTION: Provide secondary containment, conduct monthly inspections and maintain log for excluded TIUGA or include in your SPCC plan. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010037 |  |  | Excluded oil-filled electrical equipment | Failure to prepare an appropriate SPCC Plan or amend an existing SPCC Plan when the facility does not meet the criteria for exclusion for oil-filled electrical equipment. | HSC 6.67 25270.2(a)(4), 25270.4.5(a) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 89 | Oil Filled Electrical Equipment |  | Oil filled electrical equipment exclusions have been met, and where not met is included in SPCC plan | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an appropriate SPCC Plan or amend an existing SPCC Plan when the facility does not meet the criteria for exclusion for oil-filled electrical equipment. |  |  | OBSERVATION: Failure to complete SPCC plan or include oil-filled electrical equipment in SPCC plan for any oil-filled electrical equipment that does not meet provisions of excluded oil-filled electrical equipment. CORRECTIVE ACTION: Maintain oil-filled electrical equipment so that it meets the exclusion criteria or include the oil-filled equipment in the SPCC Plan. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030032 |  |  | Conditionally exempt facility conditions | Failure of a conditionally exempt facility to allow the UPA to conduct a periodic inspection, install secondary containment when the UPA determines that it is necessary, and/or conduct daily visual inspections to protect the waters of the state. | HSC 6.67 25270.4.5(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 90 | Conditionally Exempt Facilities |  | Exempt facility allowed UPA inspections, has secondary containment, conducted daily inspections. | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a conditionally exempt facility to allow the UPA to conduct a periodic inspection, install secondary containment when the UPA determines that it is necessary, and/or conduct daily visual inspections to protect the waters of the state. |  |  | OBSERVATION: Failure to allow the UPA to conduct a periodic inspection, install secondary containment when the UPA determines that it is necessary, and/or conduct daily visual inspections to protect the waters of the state. CORRECTIVE ACTION: Allow the UPA to conduct a periodic inspection, install secondary containment when the UPA determines that it is necessary, and/or conduct daily visual inspections to protect the waters of the state. | [6 empty] | Yes | No | No | No
APSA Program | Administration/Documentation | 4010032 |  |  | Annual tank facility statement | Failure to submit a tank facility statement on or before January 1 annually unless a current Business Plan has been submitted. | HSC 6.67 25270.6(a)(1), 25270.6(a)(2) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 91 | General Facility Requirements |  | Tank Facility Statement or Business Plan has been submitted | 59 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a Tank Facility Statement or Business Plan. |  |  | OBSERVATION: Failure to submit a Tank Facility Statement or Business Plan. CORRECTIVE ACTION: Submit a Tank Facility Statement or Business Plan. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010060 |  |  | APSA Facility Information submittal | Failure to annually submit in conjunction with the submittal of the tank facility statement or hazardous materials business plan any of the following information into the statewide information management system, if applicable or failure to report the information accurately: 1) Conditionally exempt from SPCC Plan status; 2) Date of SPCC Plan certification or last 5-year review, whichever is more recent; 3) Total aggregate petroleum storage capacity of a tank facility in gallons; or 4) Number of tanks in an underground area. | 19 CCR 11 1601, 1614(a), 1614(b) 1614(c) | 2025-07-01 | 2099-12-31 | 2025-07-01 | New | 92 | General Facility Requirements |  | Annual submittal of APSA Facility Information has been completed and is accurate | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to annually submit in conjunction with the submittal of the tank facility statement or hazardous materials business plan any of the following information into the statewide information management system, if applicable or failure to report the information accurately: 1) Conditionally exempt from SPCC Plan status; 2) Date of SPCC Plan certification or last 5-year review, whichever is more recent; 3) Total aggregate petroleum storage capacity of a tank facility in gallons; or 4) Number of tanks in an underground area. |  |  | OBSERVATION: Owner/Operator failed to complete the annual reporting of APSA Facility Information including one or more of the following: Conditionally exempt from SPCC Plan status, Date of SPCC Plan certification or last 5-year review (whichever is most recent), Total aggregate petroleum storage capacity in gallons, and number of tanks in underground areas, or reported incorrect information. CORRECTIVE ACTION: Complete the APSA Facility Information reporting in the statewide information management system and ensure the information reported is accurate. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010061 |  |  | APSA Facility Information submittal updates | Failure to electronically update the APSA Facility Information within 30 days of the notice from the UPA. | 19 CCR 11 1601, 1614(f) | 2025-07-01 | 2099-12-31 | 2025-07-01 | New | 93 | General Facility Requirements |  | APSA Facility Information has been updated in CERS within 30 days of request by UPA | 83 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically update the APSA Facility Information within 30 days of the notice from the UPA. |  |  | OBSERVATION: Owner/Operator failed to update reported APSA Facility Information within 30 days of notice from the UPA. CORRECTIVE ACTION: Update the APSA Facility Information in the statewide information management system as requested by the UPA . | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Release/Leaks/Spills | 4040001 |  |  | Release Reporting | Failure to report immediately upon discovery spills or other releases of one barrel (42 gallons) or more of petroleum in or on any waters of the State in accordance with Section 13272(a) of the California Water Code to Cal OES and UPA or 911. | HSC 6.67 25270.8 | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 94 | General Facility Requirements |  | Spills/releases of 42 gallons or more of petroleum reported upon discovery to Cal OES & UPA or 911 | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to report immediately upon discovery spills or other releases of one barrel (42 gallons) or more of petroleum in or on any waters of the State in accordance with Section 13272(a) of the California Water Code to Cal OES and UPA or 911. |  |  | OBSERVATION: Failure to report immediately upon discovery spills or other releases of one barrel (42 gallons) or more of petroleum in or on any waters of the State in accordance with Section 13272(a) of the California Water Code to Cal OES and UPA or 911. CORRECTIVE ACTION: Immediately upon discovery report spills or other releases of one barrel (42 gallons) or more of petroleum in or on any waters of the State in accordance with Section 13272(a) of the California Water Code to Cal OES and UPA or 911. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010033 |  |  | APSA Fee | Failure to pay the APSA Program fee. | HSC 6.67 25270.6(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 95 | General Facility Requirements |  | APSA program fee paid | 21 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to pay the APSA Program fee. |  |  | OBSERVATION: Fee for the APSA Program were not paid as required by statute. CORRECTIVE ACTION: Pay the APSA Program fee. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030036 |  |  | Permanently closed tanks | Failure to properly close tanks when making a claim of "permanently closed." | HSC 6.67 25270.4.5(a); 40 CFR 1 112.1(b)(3), 112.2 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 96 | General Facility Requirements |  | All/any permanently closed tanks are properly closed under the definition in 40 CFR 112.2 | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly permanently close all/any tanks under the definition of “Permanently Closed “ in 40 CFR 112.2. 1) All liquid and sludge has been removed from each container and connecting line. 2) All connecting lines and piping have been disconnected from the container blanked off. 3) All valves have been closed and locked. 4) Conspicuous signs have been posted on the container stating that it is a permanently closed container and denoting the date of closure. |  |  | OBSERVATION: Owner/Operator failed to comply with one or more of the following permanent closure requirements: 1. All liquid and sludge has been removed from each container and connecting line; 2. All connecting lines and piping have been disconnected from the container blanked off; 3. All valves have been closed and locked; 4. Conspicuous signs have been posted on the container stating that it is a permanently closed container and denoting the date of closure. CORRECTIVE ACTION: Tanks that are not being used and are not addressed in the SPCC plan must either be included in your plan or meet the permanent closure requirements noted above. Provide verification to the CUPA of proper closure of the tanks. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010044 |  |  | Substantial Harm Criteria | Failure to complete and maintain at the facility the Substantial Harm Criteria certification form when owner or operator determines that the facility could not be reasonably expected to cause substantial harm to the environment. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.20(e) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 97 | General Facility Requirements |  | Substantial Harm Criteria certification maintained at the facility as required | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to complete and maintain at the facility the Substantial Harm Criteria certification form when owner or operator determines that the facility could not be reasonably expected to cause substantial harm to the environment. |  |  | OBSERVATION: Failure to complete and maintain at the facility the Substantial Harm Criteria certification form when the owner or operator determined that the facility could not be reasonably expected to cause substantial harm to the environment. CORRECTIVE ACTION: Complete and maintain at the facility the Substantial Harm Criteria certification form. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010 |  |  | APSA-Administration/Documentation - General | Administration/Documentation - General | HSC 6.67 Multiple Sections; 40 CFR 1 112 | 07/01/2011 | 2099-12-31 | 07/01/2011 | Revised | 98 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4015 |  |  | APSA-Administration/Documentation - General Local Ordinance | Administration/Documentation - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 99 | General Facility Requirements |  | Administration/Documentation - General Local Ordinance | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Training | 4020 |  |  | Training - General | Training - General | HSC 6.67 Multiple Sections; 40 CFR 1 112 | 07/01/2011 | 2099-12-31 | 07/01/2011 | Revised | 100 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Training | 4025 |  |  | APSA-Training - General Local Ordinance | Training - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 101 | General Facility Requirements |  | Training - General Local Ordinance | 34 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030 |  |  | APSA-Operations/Maintenance - General | Operations/Maintenance - General | HSC 6.67 Multiple Sections; 40 CFR 1 112 | 07/01/2011 | 2099-12-31 | 07/01/2011 | Revised | 102 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4035 |  |  | APSA-Operations/Maintenance - General Local Ordinance | Operations/Maintenance - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 103 | General Facility Requirements |  | Operations/Maintenance - General Local Ordinance | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Release/Leaks/Spills | 4040 |  |  | APSA-Release/Leaks/Spills - General | Release/Leaks/Spills - General | HSC 6.67 Multiple Sections; 40 CFR 1 112 | 07/01/2011 | 2099-12-31 | 07/01/2011 | Revised | 104 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Release/Leaks/Spills | 4045 |  |  | APSA-Release/Leaks/Spills - General Local Ordinance | Release/Leaks/Spills - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 105 | General Facility Requirements |  | Release/Leaks/Spills - General Local Ordinance | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 4050 |  |  | APSA-Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | HSC 6.67 Multiple Sections; 40 CFR 1 112 | 07/01/2011 | 2099-12-31 | 07/01/2011 | Revised | 106 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 4055 |  |  | APSA-Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 107 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes

## Spreadsheet Notes
Please note the following regarding these spreadsheets:
These spreadsheets may be used by UPAs/PAs to create/update electronic inspection checklists for all Unified Programs.
These spreadsheets are updated each year after the CERS Violation Library has been updated.
The revised versions of these spreadsheets are made available generally 2-3 months before the CERS Violation Library changes go live in CERS.
The version of these spreadsheets that shows edits displays added text as underlined and deleted text with strikethrough, both of which are in red. Minor spelling corrections or formatting changes may not be displayed, but if any changes did occur the Violation Type Number cell and the cells that were updated are highlighted yellow and the Comment column says Revised. This is true even if the only thing that changed was the Checklist Item Order value. The same is true for the Clean version of the spreadsheets but only the final version of text is shown. Actual revisions are not detailed on the Clean version, so there is no underlined text or strikethrough and all text is black, but revised cells are highlighted in yellow. Note that the Comments column cells are not highlighted. New violations in the Edited version show the text in all cells in red and underlined. New violations in the Clean version also show all text in red, but not underlined. All cells of New violations in the Edited and Clean versions are not highlighted in yellow.
The column titled Comments says Existing for any violation that was not revised during this update period, Revised for any violation that had any cell updated, and New for new violations. Note that a violation is identified as Revised if any revision is made. However, a new Begin Date is only assigned if changes occurred to the CERS info (see below) and the change was deemed to be substantive by CalEPA. When there are Revised violations that have a new Begin Date assigned, in CERS they assign a new End Date to the previous (expiring) version of the violation, which is one day before the Begin Date of the Revised versions. To maintain the previous versions of revised violations in your system, so they will continue to be displayed on reports as they should for the date they were cited, you will likely need to assign an End Date of 6/30/2025 to the expiring versions of Revised violations since the new Begin Date of the Revised versions will be 7/1/2025. The expiring versions of violations are not displayed in these spreadsheets. A separate spreadsheet is available showing all expiring versions of violations with the End Date as 6/30/2025. That sreadsheet, and the sheets showing edits, would also include any Deleted violations. There were no Deleted violations in this update.
The word Deleted is entered in the Comments column for deleted violations, for which there is no revised version, and the Checklist Item Order value is blank, and as a result, deleted violations, if any, show up at the end of the sheets that shows edits. These deleted violations that have no new revised version are not included on the clean versions.
The Begin Dates will match the Begin Dates in CERS. If a violation only had CUPA column info updated this does not result in a new Begin Date. Only CERS info changes deemed substantive result in a revised violation with a new Begin Date.
CERS Info refers the information provided in columns A-K. This information matches violation information in CERS.
CUPA Info refers to the information provided in all columns to the right of column K. This information is not in CERS.
Each row is a separate violation and the spreadsheets are sorted by Checklist Item Order, which represents the intended order on the checklists that the violations will be displayed.
Inspection Checklist Item Text is the text that will show on the inspection checklist for that violation. This field was originally set up to only allow for 100 characters, which is the reason for abbreviations and limited detail at times.
The character limit in CERS for violation comments is 1000 characters. There are some prewritten Inspector Comments (Observation and Corrective Action) that are over 1000 characters. Depending on your system this may result in only the first 1000 characters being transferred to CERS or it may result in a failure to transfer any of the information, if an inspector utilizes a default inspection comment that is >1000 characters.
When the spreadsheets were first developed the Default Degree of Violation (Class) was set for all violations. You may want to make this field blank in your inspection system so inspectors must set the class versus relying on a default class which may not always be correct given the specific circumstances.
The far right columns of each spreadsheet will have one or more columns for the type(s) of facilities for that program. i.e. HMBP will only have one, but UST will have three (DW, SW, Full). Violations will be set as Yes in these columns if they apply to that facility type and No if not. So those violations with a Yes in the UST DW column will show up on an inspection checklist for DW UST sites, and those with a No will not. Those with a Yes in the SW column will show on a checklist for SW sites. There is a Yes for every violation in the Full column so all violations will show on a checklist for Full, which, for UST, would be for a facility that includes both SW and DW components. This same method is used on all program sheets with multiple facility types. All programs except HMBP and RCRA LQG have multiple facility types. There is only a Full column for UST and TP spreadsheets.