## HMBP
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Comments | Updated On

## UST
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading (Optional) | Inspection Checklist Sub-Heading (Optional) | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop-Down | Default Degree of Violation | Required Item? | Points (Optional) | Comply By Days (Optional) | Violation Descriptive Text | TCR DESIGNATION | Violation Corrective Text (Optional) | Inspector Comment 1 (Optional) | Inspector Comment 2 (Optional) | Inspector Comment 3 (Optional) | Inspector Comment 4 (Optional) | Inspector Comment 5 (Optional) | UST FULL | UST DW | UST SW
UST Program | Operations/Maintenance | 2030042 | Release Detection (USEPATCR 9d) |  | Pressurized Double-Walled Pipe - Line Integrity Test (USEPATCR 9d) (USEPA Priority) | Failure to perform one of the following line integrity test(s): 1) A 12 month test for pressurized double-walled piping that does not utilize fail safe and positive shut down, or 2) Within 30 days of the date of the completion of a repair to the primary piping. | 23 CCR 16 2636(f)(3), 2643(c)(3); HSC 6.7 25291(f), 25290.2(g), 25292(e) | 2018-10-01 | 2025-06-30 | 2025-06-30 | Expired Version of Revised Violation | 15 | File Review | Testing | Line integrity test completed on DW press piping every 12 mths if no fail safe / + shutdown (TCR 9d) | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform one of the following line integrity test(s): 1) A 12 month test for pressurized double-walled piping that does not utilize fail safe and positive shut down, or 2) Within 30 days of the date of the completion of a repair to the primary piping. | 9d |  | OBSERVATION: Owner/Operator did not perform and pass annual line integrity test for double-walled pressurized piping that does not utilize fail safe or positive shut down, or did not complete test within 30 days of the completion of a repair to the primary piping. CORRECTIVE ACTION: Perform and pass annual line integrity test for pressurized piping that does not utilize fail safe or shut down, and within 30 days of completing any repairs to the primary piping. Submit verification. | OBSERVATION: Annual line tightness testing was last performed on [date] and was due by [month/year]. Testing has not been completed and is [# months late] months past due. This test is required annually. CORRECTIVE ACTION: Immediately schedule this test and provide 48 hours notification to the CUPA. Please be aware that a follow up inspection will be charged at our current hourly rate | OBSERVATION: Annual line tightness testing was last performed on [date] and was completed on [date] , [# months late] months past due. This test is required annually. CORRECTIVE ACTION: Take all necessary precautions to ensure testing is performed in a timely manner. |  |  | Yes | Yes | No
UST Program | Operations/Maintenance | 2030045 |  |  | Red Tag Tampering (USEPA Priority) | Red Tag has been removed, defaced, altered, or otherwise tampered with so that the information on the tag is not legible. | 23 CCR 16 2717.1(g) | 2011-07-01 | 2025-06-30 | 2025-06-30 | Expired Version of Revised Violation | 79 | General Operating Requirements | Red Tag | Red Tag information is legible and has not been removed or tampered with | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Red Tag has been removed, defaced, altered, or otherwise tampered with so that the information on the tag is not legible. |  |  | OBSERVATION: Owner/operator failed to ensure that Red Tag was not tampered with. CORRECTIVE ACTION: Owner/operator shall ensure that Red Tag is not tampered with. |  |  |  |  | Yes | Yes | Yes
Note on N1: With the Checklist Item Order column in mind, this text represents text that will group one or more sub-headings and violations. If no Inspection Checklist Heading, the checklist items will not be grouped. Example: Leak Detection 100 Characters Max
Note on O1: With the Checklist Item Order field in mind and as a sub-item to Checklist Heading, this text represents text that will group one or more violations. If no Checklist Sub-Heading, the checklist items will fall under the Checklist Heading. Example: “Single Wall” 100 Characters Max
Note on P1: This is what appears on the checklist for the inspector. It should be descriptive and relatively short. May be the same as Name if sufficiently descriptive. Note: Decade recommends expressing the checklist item “in the positive.” For example, “Facility performs enhanced leak detection testing before the tank is placed in use” (positive) vs. “Failure to perform enhanced leak detection testing before the tank is placed in use” (negative). 100 Characters Max
Note on Q1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on R1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on S1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on T1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on U1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on V1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Example: Y or N
Note on W1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Example: Y or N
Note on X1: For this checklist item, display the option to set/override the Degree of Violation (e.g., Class 1, Class2, Minor) Example: Y or N
Note on Y1: Is this violation typically recorded as a Class 1, Class 2, or Minor Violation. Blank (no default) is also a valid option. Example: Y or N
Note on Z1: If marked Y, then the inspection cannot be completed without selecting IN, OUT, NA, or NO. Otherwise, mark this item N. Example: Y or N
Note on AA1: Indicate the number of points that should be added/deducted when this item is marked OUT of compliance. Example: 5
Note on AB1: Indicate the number of days following the first Notice of Violation on which the regulator expects compliance. Example: 30
Note on AC1: This static text may appear on a printed inspection report when inspections are conducted electronically. May use “Description” column from the Unified Program Violation Library.
Note on AD1: For Summary Reporting, this field shall specify if the cited violation relates to Release Detection. Example: Y or N
Note on AE1: This static text may appear on a printed inspection report when inspections are conducted electronically.
Note on AF1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AG1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AH1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AI1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AJ1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AK1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AL1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AM1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.

## HWG
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | HazWaste SQG | HazWaste LQG
Hazardous Waste Generator | Training | 3020002 |  |  | Large Quantity Generator: Employee Hazardous Waste Training | Failure to provide employees with hazardous waste training program of class room, computer-based or electronic instructions or on-the-job training that teaches facility personnel to perform their duties in a way that ensures the facility's compliance with the requirements of 22 CCR Chapter 12, and/or failure to provide training within 180 days after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. | 22 CCR 12 66262.17(a)(7); 22 CCR 15 66265.16 | 2024-10-01 | 2025-06-30 | 2025-06-30 | Expired Version of Revised Violation | 8 | Recordkeeping/ Documentation | Training | Facility personnel are trained within 6 mths after start date or new position and annually | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide employees with hazardous waste training program of class room, computer-based or electronic instructions or on-the-job training that teaches facility personnel to perform their duties in a way that ensures the facility's compliance with the requirements of 22 CCR Chapter 12, and/or failure to provide training within the first six months after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. |  |  | OBSERVATION: Owner/Operator failed to provide employees with hazardous waste training program of class room, computer-based or electronic instructions or on-the-job training within the first six months after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. CORRECTIVE ACTION: Provide required hazardous waste training to employees and ensure future training is provided within the required time frames and annually. Submit a copy of training documentation to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030022 |  |  | Small Quantity Generator: Incompatible Waste Storage | Failure to: (1) Store incompatible wastes and/or material in the same container or an unwashed container without ensuring it does not (a) generate extreme heat or pressure, fire or explosion, or violent reaction; (b) produce uncontrolled toxic mists, fumes, dusts, or gases in sufficient quantities to threaten human health or the environment; (c) produce uncontrolled flammable fumes or gases in sufficient quantities to pose a risk of fire or explosions; (d) damage the structural integrity of the device or facility containing the waste; or (e) through other like means threaten human health or the environment; or (2) Separate a container accumulating hazardous waste that is incompatible with any waste or material stored in any other container, piles, open tanks, or surface impoundments by means of a dike, berm, wall, or other device. | 22 CCR 12 66262.15(a)(3), 66262.16(b)(2)(E); 22 CCR 15 66265.17(b) | 2024-10-01 | 2025-06-30 | 2025-06-30 | Expired Version of Revised Violation | 41 | Hazardous Waste Management | Container Management | Incompatible waste in containers managed properly to prevent a reaction | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to: (1) Store incompatible wastes and/or material in the same container or an unwashed container without ensuring it does not (a) generate extreme heat or pressure, fire or explosion, or violent reaction; (b) produce uncontrolled toxic mists, fumes, dusts, or gases in sufficient quantities to threaten human health or the environment; (c) produce uncontrolled flammable fumes or gases in sufficient quantities to pose a risk of fire or explosions; (d) damage the structural integrity of the device or facility containing the waste; or (e) through other like means threaten human health or the environment; or (2) Separate a container accumulating hazardous waste that is incompatible with any waste or material stored in any other container, piles, open tanks, or surface impoundments by means of a dike, berm, wall, or other device. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [LIST HAZARDOUS WASTES] located in the [LOCATION] are not compatible and were observed stored in a manner that could result a reaction. CORRECTIVE ACTION: Transfer or separate the containers of incompatible wastes noted above to other compatible containers or by separating containers to prevent a reaction and submit photos to the CUPA demonstrating compliance. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030046 |  |  | Universal Waste Handler: Offsite Shipments | Failure of the universal waste handler to transfer universal waste to another universal waste handler, or appropriate destination facility. Failure to package, label, mark and placard shipments and prepare shipping papers for any universal waste that meets the hazardous materials definition in accordance with DOT 49 CFR parts 171-180. | 22 CCR 23 66273.38; 49 CFR 1 172 | 2018-10-01 | 2025-06-30 | 2025-06-30 | Expired Version of Revised Violation | 101 | Universal Waste | UW Management | UWH properly prepares, handles and retains shipping papers for all universal waste shipped | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the universal waste handler to transfer universal waste to another universal waste handler, or appropriate destination facility. Failure to package, label, mark and placard shipments and prepare shipping papers for any universal waste that meets the hazardous materials definition in accordance with DOT 49 CFR parts 171-180. |  |  | OBSERVATION: Universal Waste Handler (UWH)failed to properly package, label, mark, placard, or prepare and retain shipping papers for all universal waste being shipped to another universal waste handler, destination facility, or foreign facility. [ENTER SPECIFIC OBSERVATION] CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that all universal waste noted above have been properly packaged, labeled, marked, placarded, or prepared and retain shipping papers. | OBSERVATION: Universal Waste Handler failed to send UW to another Universal Waste Handler or a permitted destination facility as observed by [ENTER OBSERVED SHIPPING/DISPOSAL VIOLATION]. CORRECTIVE ACTION: The UWH shall immediately submit a written statement to the CUPA documenting how the facility will properly manage and recycle all UW generated on site. | [5 empty] | Yes | Yes

## RCRA LQG
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | RCRA LQG
RCRA Large Quantity Generator | Administration/Documentation | 3110011 |  | 262.C | RCRA: Contingency Plan Emergency Action Plan | Failure to include all of the following in the Contingency Plan: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. (If the owner or operator has already prepared a Spill Prevention, Control, and Countermeasures (SPCC) Plan or some other emergency or contingency plan, the owner or operator need only amend that plan to incorporate hazardous waste management provisions.) OR: Failure to review and immediately amend whenever: (1) Applicable regulations are revised; (2) The plan fails in an emergency; (3) The generator facility changes—in its design, construction, operation, maintenance, or other circumstances—in a way that materially increases the potential for fires, explosions, or releases of hazardous waste or hazardous waste constituents, or changes the response necessary in an emergency; (4) The list of emergency coordinators changes; or (5) The list of emergency equipment changes. | 22 CCR 12 66262.17(a)(6), 66262.261, 66262.263 | 2024-10-01 | 2025-06-30 | 2025-06-30 | Expired Version of Revised Violation | 5 | Recordkeeping/ Documentation | Contingency Plan | Contingency plan contains all required content and reviewed and amended when required | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include all of the following in the Contingency Plan: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. (If the owner or operator has already prepared a Spill Prevention, Control, and Countermeasures (SPCC) Plan or some other emergency or contingency plan, the owner or operator need only amend that plan to incorporate hazardous waste management provisions.) OR: Failure to review and immediately amend whenever: (1) Applicable regulations are revised; (2) The plan fails in an emergency; (3) The generator facility changes in its design, construction, operation, maintenance, or other circumstances in a way that materially increases the potential for fires, explosions, or releases of hazardous waste or hazardous waste constituents, or changes the response necessary in an emergency; (4) The list of emergency coordinators changes; or (5) The list of emergency equipment changes. |  |  | OBSERVATION: The Contingency Plan does not contain all required content [LIST MISSING CONTENT], OR; Facility failed to review and immediately amend whenever: (1) Applicable regulations are revised; (2) The plan fails in an emergency; (3) The generator facility changes in its design, construction, operation, maintenance, or other circumstances in a way that materially increases the potential for fires, explosions, or releases of hazardous waste or hazardous waste constituents, or changes the response necessary in an emergency; (4) The list of emergency coordinators changes; or (5) The list of emergency equipment changes. CORRECTIVE ACTION: Revise the Contingency Plan to include all required content and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130042 |  |  | Universal Waste Handler: Offsite Shipments | Failure of the universal waste handler to transfer universal waste to another universal waste handler, or appropriate destination facility. Failure to package, label, mark and placard shipments and prepare shipping papers for any universal waste that meets the hazardous materials definition in accordance with DOT 49 CFR parts 171-180. | 22 CCR 23 66273.38; 49 CFR 1 172 | 2018-10-01 | 2025-06-30 | 2025-06-30 | Expired Version of Revised Violation | 83 | Universal Waste | UW Management | UWH properly prepares, handles and retains shipping papers for all universal waste shipped | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the universal waste handler to transfer universal waste to another universal waste handler, or appropriate destination facility. Failure to package, label, mark and placard shipments and prepare shipping papers for any universal waste that meets the hazardous materials definition in accordance with DOT 49 CFR parts 171-180. |  |  | OBSERVATION: Universal Waste Handler (UWH) failed to properly package, label, mark, placard, or prepare and retain shipping papers for all universal waste being shipped to another universal waste handler, destination facility, or foreign facility. [ENTER SPECIFIC OBSERVATION] CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that all universal waste noted above have been properly packaged, labeled, marked, placarded, or prepared and retain shipping papers. | OBSERVATION: Universal Waste Handler failed to send UW to another Universal Waste Handler or a permitted destination facility as observed by [ENTER OBSERVED SHIPPING/DISPOSAL VIOLATION]. CORRECTIVE ACTION: The UWH shall immediately submit a written statement to the CUPA documenting how the facility will properly manage and recycle all UW generated on site. | [5 empty] | Yes

## TP
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | TP full list | TP CA | TP CECL | TP CEL | TP CESQT | TP CESW | TP PBR

## HHW
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | PHHWCF | THHWCF

## APSA
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | AST Conditionally Exempt | AST Non_Qualified | AST Tier I | AST Tier II
APSA Program | Administration/Documentation | 4010003 |  |  | Professional engineer certification | Failure to have a licensed professional engineer properly review and certify the SPCC Plan. | 40 CFR 1 112.3(d); HSC 6.67 25270.4.5(a) | 2016-06-01 | 2025-06-30 | 2025-06-30 | Expired Version of Revised Violation | 5 | Requirement to Prepare and Implement |  | Professional engineer has properly reviewed and certified the SPCC Plan | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have a licensed professional engineer properly review and certify the SPCC Plan. |  |  | OBSERVATION: PE failed to properly review and/or certify the SPCC Plan for one or more of the requirements. CORRECTIVE ACTION: Submit SPCC that has been properly reviewed and certified by a PE. | [6 empty] | No | Yes | No | No
APSA Program | Administration/Documentation | 4010009 |  |  | Five-year SPCC Plan review and documentation of the review | Failure to complete a review and evaluation of the SPCC Plan at least once every five years, document the completion of the review, and sign a statement as to whether the SPCC Plan will be amended. | 40 CFR 1 112.5 (b); HSC 6.67 25270.4.5 (a) | 2017-11-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 14 | Five Year Review |  | 5 year review performed on SPCC and documented | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to complete a review and evaluation of the SPCC Plan at least once every five years, document the completion of the review, and sign a statement as to whether the SPCC Plan will be amended. |  |  | OBSERVATION: Failure to perform and/or document the five-year review of the SPCC plan. CORRECTIVE ACTION: Complete and document the 5 year review of SPCC Plan and submit verification of proper completion. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010021 |  |  | Written records of inspections and tests | Failure to comply with one or more of the following requirements: 1. Have record of inspections and tests, including integrity tests, signed by the appropriate supervisor or inspector. 2. Keep written procedures and records of inspections and tests, including integrity tests, for at least three years. 3. Keep comparison record for bulk storage containers subject to 40 CFR 112.8(c)(6). | 40 CFR 1 112.7(a)(1), 112.7(e), 112.8(c)(6); HSC 6.67 25270.4.5(a) | 2020-10-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 66 | SPCC Requirements for Onshore Facilities | Inspections & Testing | Written Inspection/testing procedures kept, inspection/testing records signed, kept for 3 years | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with one or more of the following requirements: 1. Have record of inspections and tests, including integrity tests, signed by the appropriate supervisor or inspector. 2. Keep written procedures and records of inspections and tests, including integrity tests, for at least three years. 3. Keep comparison records for bulk storage tanks subject to 40 CFR 112.8(c)(6). |  |  | OBSERVATION: Failure to comply with one or more of the following requirements: 1. Have record of inspections and tests, including integrity tests, signed by the appropriate supervisor or inspector. 2. Keep written procedures and records of inspections and tests, including integrity tests, for at least three years. 3. Keep comparison records for bulk storage containers subject to 40 CFR 112.8(c)(6). CORRECTIVE ACTION: Keep written inspection procedures, records of inspections and testing, signed by appropriate supervisor/inspector, for at least 3 years. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010047 |  |  | Qualified Facility - Certification of SPCC Plan | Failure to have management or a professional engineer certify the SPCC Plan and comply with certification requirements at a qualified facility. | 40 CFR 1 112.6(a)(1),112.6(b); HSC 6.67 25270.4.5 (a) | 2017-11-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 7 | Requirement to Prepare and Implement |  | Qualified Facility's SPCC plan has been self or PE certified. | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to have management or a professional engineer certify the SPCC Plan and comply with certification requirements at a qualified facility. |  |  | OBSERATION: SPCC Plan has not been properly certified by management or professional engineer. CORRECTIVE ACTION: Facility must certify or have professional engineer certify the SPCC Plan. | [6 empty] | No | No | Yes | Yes
APSA Program | Administration/Documentation | 4010057 |  |  | SPCC Plan complete | Failure to prepare an SPCC Plan that meets all applicable requirements. | 40 CFR 1 112.3, 112.6; HSC 6.67 25270.4.5(a | 2017-11-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 2 | Requirement to Prepare and Implement |  | SPCC plan has been prepared that meets all applicable requirements | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an SPCC Plan that meets all applicable requirements. |  |  | OBSERVATION: Failure to prepare an SPCC Plan that meets all applicable requirements. CORRECTIVE ACTION: Complete or revise SPCC plan that meets all applicable requirements. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Training | 4020001 |  |  | Employee training requirements | Failure to provide the following training to all oil-handling personnel : 1. Operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. 5. Contents of the SPCC Plan. | 40 CFR 1 112.7(f)(1); HSC 6.67 25270.4.5(a) | 2016-06-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 37 | General SPCC Requirements | Training | Training provided for op/maint of equip, discharge procedures, laws/regs, general fac ops, and SPCC | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide the following training to all oil-handling personnel: 1. Operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. 5. Contents of the SPCC Plan. |  |  | OBSERVATION: Failure to provide training to all oil-handling personnel regarding one or more of the following: 1. The operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. AND 5. The contents of the SPCC Plan. CORRECTIVE ACTION: Provide training in: 1. The operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. AND 5. The contents of the SPCC Plan. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Training | 4020002 |  |  | Spill prevention briefings | Failure to conduct spill prevention briefing for oil-handling personnel at least once a year to assure adequate understanding of the SPCC Plan, including : 1. Known discharges or failures. 2. Malfunctioning components. 3. Any recently developed precautionary measures. | 40 CFR 1 112.7(f)(3); HSC 6.67 25270.4.5(a) | 2020-10-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 39 | General SPCC Requirements | Training | Spill prevention briefings are conducted annually | 49 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to conduct spill prevention briefing for oil-handling personnel at least once a year to assure adequate understanding of the SPCC Plan, including: 1. Known discharges or failures. 2. Malfunctioning components. 3. Any recently developed precautionary measures. |  |  | OBSERVATION: Failure to conduct spill prevention briefings at least once a year, or failure to highlight or describe one or more of the following: Known discharges or failures; Malfunctioning components; Recently developed precautionary measures. CORRECTIVE ACTION: Conduct spill prevention briefings annually. Provide compliance verification. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030002 |  |  | Secondary containment at loading/unloading racks | Failure to ensure loading/unloading rack drainage flows to catchment basin or treatment facility designed to handle discharges, or use a quick drainage system when a tank car or tank truck loading/unloading rack is present at the facility. The containment system must be designed to hold at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. | 40 CFR 1 112.7(h)(1); HSC 6.67 25270.4.5(a) | 2016-06-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 43 | General SPCC Requirements | Loading/Unloading Racks | Loading rack containment has capacity to contain single largest compartment of tank car/truck | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure loading/unloading rack drainage flows to catchment basin or treatment facility designed to handle discharges, or use a quick drainage system when a tank car or tank truck loading/unloading rack is present at the facility. The containment system must be designed to hold at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. |  |  | OBSERVATION: Failure to ensure loading/unloading rack drainage flows to catchment basin or treatment facility designed to handle discharges, or use a quick drainage system when a tank car or tank truck loading/unloading rack is present at the facility, and is designed to hold at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. CORRECTIVE ACTION: Ensure loading/unloading rack drainage flows to containment or treatment system with at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030010 |  |  | Sized secondary containment | Failure to provide and maintain secondary containment for bulk storage tank installations (except for mobile refuelers and other non-transportation-related tank trucks) sufficient to hold the capacity of the largest container and sufficient freeboard for precipitation. | 40 CFR 1 112.8(c)(2); HSC 6.67 25270.4.5(a) | 2017-11-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 55 | SPCC Requirements for Onshore Facilities | Secondary Containment | Adequately sized secondary containment provided and maintained for bulk storage containers | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide and maintain secondary containment for bulk storage tank installations (except for mobile refuelers and other non-transportation-related tank trucks) sufficient to hold the capacity of the largest container and sufficient freeboard for precipitation. |  |  | OBSERVATION: Failure to provide and maintain secondary containment for bulk storage tank installations sufficient to hold the capacity of the largest container and sufficient freeboard for precipitation. CORRECTIVE ACTION: Provide and maintain adequate secondary containment for bulk storage containers. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030014 |  |  | Tanks inspected or tested by qualified person | Failure to ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. | 40 CFR 1 112.7(e), 112.8(c)(6); HSC 6.67 25270.4.5(a) | 2020-10-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 63 | SPCC Requirements for Onshore Facilities | Inspections & Testing | Tanks inspected and tested by qualified person in accordance with industry standards | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. |  |  | OBSERVATION: Failure to ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. CORRECTIVE ACTION: Ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030015 |  |  | Tanks inspected and/or integrity tested | Failure to test or inspect each aboveground container for integrity based on industry standards: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. | 40 CFR 1 112.7(e), 112.8(c)(6); HSC 6.67 25270.4.5(a) | 2024-10-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 64 | SPCC Requirements for Onshore Facilities | Inspections & Testing | Aboveground containers tested or inspected for integrity based on industry standards | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to test or inspect each aboveground container for integrity based on industry standards: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. |  |  | OBSERVATION: Failure to test or inspect each aboveground container for integrity based on industry standards: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. CORRECTIVE ACTION: Test or inspect each aboveground container for integrity based on industry standards on a regular schedule, after making material repairs, using non-destructive testing, inspecting each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. Maintain testing and inspection records. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030020 |  |  | Mobile or portable storage container positioning and sized containment | Failure to position or locate mobile or portable storage containers to prevent a discharge as described in 40 CFR 112.1(b), and/or failure to provide adequate secondary containment for mobile or portable oil storage containers (excluding mobile refuelers and other non-transportation-related tank trucks) with sufficient capacity to contain the largest single compartment or container and sufficient freeboard to contain precipitation. | 40 CFR 1 112.8(c)(11); HSC 6.67 25270.4.5(a) | 2017-11-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 75 | SPCC Requirements for Onshore Facilities | Mobile/Portable Container | Adequate secondary containment provided for mobile/portable storage containers | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to position or locate mobile or portable storage containers to prevent a discharge as described in 40 CFR 112.1(b), and/or failure to provide adequate secondary containment for mobile or portable oil storage containers (excluding mobile refuelers and other non-transportation-related tank trucks) with sufficient capacity to contain the largest single compartment or container and sufficient freeboard to contain precipitation. |  |  | OBSERVATION: Failure to position or locate mobile or portable storage containers to prevent a discharge as described in 40 CFR 112.1(b), and/or failure to provide mobile or portable oil storage containers (excluding mobile refuelers and other non-transportation-related tank trucks) with adequate secondary containment with sufficient capacity to contain the largest single compartment or container and sufficient freeboard to contain precipitation. CORRECTIVE ACTION: Position or locate mobile or portable storage containers to prevent a discharge, and/or provide adequate secondary containment for mobile or portable oil storage tanks. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030021 |  |  | Leaks addressed and oil removed | Failure to promptly correct visible discharges and promptly remove any accumulations of oil in diked areas. | 40 CFR 1 112.8(c)(10); HSC 6.67 25270.4.5(a) | 2017-11-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 74 | SPCC Requirements for Onshore Facilities | Response to Release | Visible discharges promptly corrected and any accumulation of oil in diked areas promptly removed. | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to promptly correct visible discharges and promptly remove any accumulations of oil in diked areas. |  |  | OBSERVATION: Failure to promptly correct visible discharges and promptly remove any accumulations of oil in diked areas. CORRECTIVE ACTION: Promptly correct any visible discharges and promptly remove any accumulations of oil in diked areas. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030034 |  |  | Containment for qualified oil-filled operational equipment | Failure to provide general secondary containment or failure to fulfill alternative requirements to general secondary containment for oil-filled operational equipment. | 40 CFR 1 112.7(k); HSC 6.67 25270.4.5(a) | 2016-06-01 | 2025-07-01 | 2025-07-01 | Expired Version of Revised Violation | 47 | General SPCC Requirements | Oil-Filled Operation Equipment | Oil filled operational equipment containment standards are met | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide general secondary containment or failure to fulfill alternative requirements to general secondary containment for oil-filled operational equipment. |  |  | OBSERVATION: Failure to provide general secondary containment or failure to fulfill alternative requirements to general secondary containment for oil-filled operational equipment. CORRECTIVE ACTION: Provide items needed to satisfy conditions of general secondary containment or demonstrate how alternate oil containment standards for oil filled operational equipment are being met. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030037 |  |  | General containment | Failure to provide appropriate secondary containment and/or diversionary structures or equipment for the following: 1) Bulk storage containers, 2) Mobile or portable containers, 3) Oil-filled equipment, 4) Piping and related appurtenances, 5) Mobile refuelers or non-transportation-related tank cars, and 6) Transfer areas, equipment and activities and ensure that the entire containment system, including walls and floor, are capable of containing oil and constructed so that any discharge will not escape the containment system before cleanup occurs. | 40 CFR 1 112.7(c); HSC 6.67 25270.4.5(a) | 2027-11-01 | 2025-06-30 | 2025-06-30 | Expired Version of Revised Violation | 31 | General SPCC Requirements | Containment | Appropriate (general) containment/diversionary structures/equipment have been provided | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide appropriate secondary containment and/or diversionary structures or equipment for the following: 1. Bulk storage containers, 2. Mobile or portable containers, 3. Oil-filled equipment, 4. Piping and related appurtenances, 5. Mobile refuelers or non-transportation-related tank cars, and 6. Transfer areas, equipment and activities and ensure that the entire containment system, including walls and floor, are capable of containing oil and constructed so that any discharge will not escape the containment system before cleanup occurs. |  |  | OBSERVATION: Failure to provide the appropriate general containment/diversionary structures/equipment for the following: bulk storage containers, mobile or portable containers, oil-filled equipment, piping and related appurtenances, mobile refuelers or non-transportation-related tank cars, and transfer areas. CORRECTIVE ACTION: Provide appropriate general containment measures and/or diversionary structures/equipment capable of containing oil and constructed so that any discharge will not escape the containment system before cleanup occurs. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030041 |  |  | Tier I - Bulk storage container sized secondary containment | Failure to provide bulk storage containers with adequate secondary containment large enough to contain the entire capacity of the largest container plus additional capacity to contain precipitation when applicable, and/or failure to position/locate mobile or portable containers to prevent a discharge. | 40 CFR 1 112.6(a)(3)(ii); HSC 6.67 25270.4.5(a) | 2017-11-01 | 2025-06-30 | 2025-06-30 | Expired Version of Revised Violation | 56 | SPCC Requirements for Onshore Facilities | Secondary Containment | All bulk storage containers have secondary containment to prevent a discharge at Tier I facility | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide bulk storage containers with adequate secondary containment large enough to contain the entire capacity of the largest container plus additional capacity to contain precipitation when applicable, and/or failure to position/locate mobile or portable containers to prevent a discharge. |  |  | OBSERVATION: Bulk storage containers do not have adequate secondary containment. CORRECTIVE ACTION: Provide secondary containment for bulk storage containers large enough to contain the entire capacity of the largest container plus additional capacity to contain precipitation. | [6 empty] | No | No | Yes | No