## HMBP
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | HMBP
Business Plan Program | Administration/Documentation | 1010001 |  |  | Hazardous Materials Business Plan Implementation | Failure to adequately establish and implement a business plan when storing/handling a hazardous material at or above reportable quantities. | HSC 6.95 25507 | 2014-07-01 | 2099-12-31 | 2016-06-17 10:16 | Existing | 1 | Administration |  | Established/implemented a business plan when handling hazardous materials in reportable quantities | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to establish and implement a business plan when storing hazardous materials at or above the reportable threshold quantities. |  |  | OBSERVATION: The business failed to establish and implement a business plan when handling hazardous materials at or above the reportable threshold quantities. CORRECTIVE ACTION: Establish and implement a business plan for the facility. Submit documentation of correction to the unified program agency. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010002 |  |  | Hazardous Materials Business Plan Submittal | Failure to complete and electronically submit initially, annually, or triennially, a business plan when storing/handling a hazardous material at or above reportable quantities. | HSC 6.95 25505, 25508(a)(1) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 2 | Administration |  | Business plan electronically submitted initially, annually, or triennially | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete and electronically submit initially, annually, or triennially, a business plan when storing/handling a hazardous material at or above reportable quantities. |  |  | OBSERVATION: The business failed to complete and electronically submit initially, annually, or triennially, a business plan when handling hazardous materials at or above the reportable threshold quantities. CORRECTIVE ACTION: Complete and electronically submit a business plan. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010017 |  |  | Hazardous Materials Business Plan Readily Available | Failure to have a business plan readily available to personnel of the business or the unified program facility with responsibilities for emergency response or training. | HSC 6.95 25505(c) | 2016-06-01 | 2099-12-31 | 2016-05-16 10:29 | Existing | 3 | Administration |  | Business plan readily available to site personnel responsible for emergency response or training | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to have a business plan readily available to personnel of the business or the unified program facility with responsibilities for emergency response or training. |  |  | OBSERVATION: The business failed to have the hazardous material business plan readily available to personnel of the business or the unified program facility with responsibilities for emergency response or training. CORRECTIVE ACTION: Provide a readily available business plan to personnel of the business or the unified program facility with responsibilities for emergency response or training. Document that appropriate personnel have the business plan readily available. | OBSERVATION: The business failed to have the hazardous material business plan readily available to personnel of the business or the unified program facility with responsibilities for emergency response or training. CORRECTIVE ACTION: Provide a readily available business plan to personnel of the business or the unified program facility with responsibilities for emergency response or training. | [5 empty] | Yes
Business Plan Program | Administration/Documentation | 1010008 |  |  | Annual Review / Certification | Failure to annually review and electronically certify that the business plan is complete and accurate on or before the required due date. | HSC 6.95 25508.2 | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 4 | Administration |  | Business plan reviewed and electronically certified as complete/accurate on or before the due date | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to annually review and electronically certify that the business plan is complete and accurate on or before the required due date. |  |  | OBSERVATION: The business failed to electronically submit and certify that the business plan is complete, accurate, and in compliance with EPCRA on or before the required due date. CORRECTIVE ACTION: Electronically submit and certify that the business plan is complete, accurate, and in compliance with EPCRA within 30 days. On an ongoing basis, electronically submit and certify the business plan annually on or before the required due date. | OBSERVATION: The business failed to electronically submit and certify that the business plan is complete, accurate, and in compliance with EPCRA on or before the required due date. CORRECTIVE ACTION: Electronically submit and certify that the business plan is complete, accurate, and in compliance with EPCRA on or before the required due date. | [5 empty] | Yes
Business Plan Program | Administration/Documentation | 1010006 |  |  | Hazardous Materials Business Plan Updates | Failure to electronically update business plan within 30 days of any one of the following events: 1) A 100 percent or more increase in the quantity of a previously disclosed material. 2) Any handling of a previously undisclosed hazardous materials at or above reportable quantities. 3) A change of business address, business ownership, or business name. 4) A substantial change in the handler's operations that requires modification to any portion of the business plan. | HSC 6.95 25508.1(a)-(f) | 2016-06-01 | 2099-12-31 | 2016-05-16 10:29 | Existing | 5 | Administration |  | Updated within 30 days of 100% increase or new haz; change of address/owner/name; or change in ops | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically update business plan within 30 days of any one of the following events: 1) A 100 percent or more increase in the quantity of a previously disclosed material. 2) Any handling of a previously undisclosed hazardous materials at or above reportable quantities. 3) A change of business address, business ownership, or business name. 4) A substantial change in the handler's operations that requires modification to any portion of the business plan. |  |  | OBSERVATION: The business failed to update business plan within 30 days when one of the following occurs: a 100 percent or more increase in the quantity of a previously disclosed material; any handling of a previously undisclosed hazardous material; a change of business address, business ownership, or business name; or a substantial change in the handler's operations that requires modification to any portion of the business plan. CORRECTIVE ACTION: Update all submittal elements effected by the change(s) and electronically submit the update within 30 days. | [6 empty] | Yes
Business Plan Program | Release/Leaks/Spills | 1040001 |  |  | Release Reporting | Failure to report a release or threatened release of a hazardous material to the unified program agency and to Cal OES. | 19 CCR 4 2631; HSC 6.95 25510(a) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 6 | Administration |  | Actual or threatened release reported to the unified program agency and Cal OES | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to report a release or threatened release of a hazardous material to the unified program agency and Cal OES. |  |  | OBSERVATION: The business failed to immediately report a release or threatened release of a hazardous material to the unified program agency and Cal OES. CORRECTIVE ACTION: Immediately report a release or threatened release of a hazardous material to the unified program agency and Cal OES. | OBSERVATION: The business failed to immediately report a release or threatened release of a hazardous material to the unified program agency and Cal OES. CORRECTIVE ACTION: Immediately report a release or threatened release of a hazardous material to the unified program agency and Cal OES. Submit documentation to the unified program agency demonstrating that all applicable personnel have been properly trained on release reporting. | OBSERVATION: The business failed to report a release or threatened release when the release poses a significant present or potential hazard to human health and safety, property, or the environment. CORRECTIVE ACTION: Immediately notify Cal OES and CUPA. Provide all required information and supporting documentation that may be deemed necessary. |  |  |  |  | Yes
Business Plan Program | Administration/Documentation | 1010011 |  |  | Property Owner Notification | Failure to notify property owner in writing that the business is subject to the business plan program and has complied with its provisions. | HSC 6.95 25505.1 | 2014-07-01 | 2099-12-31 | 2014-06-26 | Existing | 7 | Administration |  | Property owner notified in writing that business is in compliance with business plan requirements | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to notify property owner in writing that the business is subject to the business plan program and has complied with its provisions. |  |  | OBSERVATION: The business failed to notify property owner in writing that the business is subject to the business plan program and has complied with its provisions. CORRECTIVE ACTION: Notify the property owner in writing that the business is subject to the business plan program and has complied with its provisions. Submit documentation of correction to the unified program agency. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010012 |  |  | Property Owner Business Plan | Failure to provide a copy of the business plan to the owner or the owner's agent within five working days after receiving a request for a copy from the owner or the owner's agent. | HSC 6.95 25505.1 | 2014-07-01 | 2099-12-31 | 2014-06-26 | Existing | 8 | Administration |  | Lessee provided copy of business plan to owner within 5 days after request | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide a copy of the business plan to the owner or the owner's agent within five working days after receiving a request for a copy from the owner or the owner's agent. |  |  | OBSERVATION: The business failed to provide a copy of the business plan to the owner or the owner's agent within five working days after receiving a request for a copy from the property owner or their agent. CORRECTIVE ACTION: Submit documentation to the unified program agency demonstrating a copy of the business plan has been provided to the property owner or their agent. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010003 |  |  | Business Activities Page and/or Business Owner/Operator Identification Page | Failure to electronically submit the Business Activities Page and/or Business Owner Operator Identification Page, or failure to report complete or accurate information on these forms. | 19 CCR 4 2652(a)(1); HSC 6.95 25508(a)(1), 25508(a)(3) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Existing | 9 | Owner/Operator Information |  | Business Owner/Operator ID and Business Activities pages electronically submitted and are accurate | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit the Business Activities Page and/or Business Owner Operator Identification Page, or failure to report complete or accurate information on these forms. |  |  | OBSERVATION: The business failed to electronically submit the Business Activities Page and/or Business Owner Operator Identification Page, or failed to report complete or accurate information on these forms. CORRECTIVE ACTION: Complete and electronically submit the Business Activities Page and/or Business Owner Operator Identification Page. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010004 |  |  | Hazardous Materials Inventory | Failure to electronically submit complete and accurate hazardous material inventory information for all hazardous materials on site at or above reportable quantities. | HSC 6.95 25506, 25505(a)(1), 25508(a)(1), 25508(a)(3) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 10 | Inventory |  | Complete and accurate Hazardous Materials Inventory information electronically submitted | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit complete and accurate hazardous material inventory information for all hazardous materials on site at or above reportable quantities. |  |  | OBSERVATION: The business failed to electronically submit complete and accurate chemical inventory information for all hazardous materials on site at or above reportable quantities. CORRECTIVE ACTION: Electronically submit complete and accurate chemical inventory information for all hazardous materials on site at or above reportable quantities. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010018 |  |  | Hazardous Materials Consumer Product Handling | Failure to complete and electronically submit a business plan, or required hazardous materials reporting, when handling a consumer product that is a hazardous material in a quantity equal to or greater than the reportable threshold and stored at a facility that manufactures the product, or is a warehouse or distribution center with no direct sales to consumers, or where the product is dispensed on the retail premises. | HSC 6.95 25507(b)(5)(B)(i), 25508(a)(1) | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 11 | Consumer Product/Retail Establishment |  | Consumer product reported when stored at place of manufacture, warehouse, or where dispensed | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete and electronically submit a business plan, or required hazardous materials reporting, when handling a consumer product that is a hazardous material in a quantity equal to or greater than the reportable threshold, and stored at a facility that manufactures the product, is a warehouse or distribution center with no direct sales to consumers, or where the product is dispensed on the retail premises. |  |  | OBSERVATION: Owner/Operator failed to complete and electronically submit a business plan, or required hazardous materials reporting, when handling a consumer product that is a hazardous material in a quantity equal to or greater than the reportable threshold, and stored at a facility that manufactures the product, is a warehouse or distribution center with no direct sales to consumers, or where the product is dispensed on the retail premises. CORRECTIVE ACTION: Complete required business plan reporting and report all consumer products which are not excluded from reporting requirements, and as directed by the UPA. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010019 |  |  | Hazardous Materials Consumer Product Retail Establishment | Failure to complete and electronically submit a business plan, or required hazardous materials reporting, when handling a consumer product that is a hazardous material at a retail establishment in a quantity equal to or greater than the reportable threshold if the product is not intended for personal, family, or household purposes, or is not present in the same form, concentration, or quantity as a product prepackaged for distribution to a consumer for personal, family or household purposes; or 1. The product has a NFPA or HMIS rating of 3 or 4 and is stored, at any time, in quantities equal to, or greater than, 165 gallons for a liquid, 600 cubic feet for a compressed gas, or 1,500 pounds for a solid; or 2. The product poses a significant potential hazard, and the UPA requires the product to be reported. | HSC 6.95 25507(b)(5)(B)(ii), 25508(a)(1) | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 12 | Consumer Product/Retail Establishment |  | Consumer product at retail establish. reported if exemption criteria not met or if required by UPA | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete and electronically submit a business plan, or required hazardous materials reporting, when handling a consumer product that is a hazardous material at a retail establishment in a quantity equal to or greater than the reportable threshold if the product is not intended for personal, family, or household purposes, or is not present in the same form, concentration, or quantity as a product prepackaged for distribution to a consumer for personal, family or household purposes; or 1. The product has a NFPA or HMIS rating of 3 or 4 and is stored, at any time, in quantities equal to, or greater than, 165 gallons for a liquid, 600 cubic feet for a compressed gas, or 1,500 pounds for a solid; or 2. The product poses a significant potential hazard, and the UPA requires the product to be reported. |  |  | OBSERVATION: Owner/Operator failed to complete and electronically submit a business plan, or required hazardous materials reporting, when handling a consumer product that is a hazardous material at a retail establishment in a quantity equal to or greater than the reportable threshold if the product is not intended for personal, family, or household purposes, or is not present in the same form, concentration, or quantity as a product prepackaged for distribution to a consumer for personal, family or household purposes, OR; the product has a NFPA or HMIS rating of 3 or 4 and is stored, at any time, in quantities equal to, or greater than, 165 gallons, 600 cubic feet, or 1,500 pounds, OR; the product is stored at or above the standard reportable threshold, poses a significant potential hazard, and the UPA requires the product to be reported. CORRECTIVE ACTION: Complete required business plan reporting and report all consumer products which are not excluded from reporting requirements, and as directed by the UPA. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010005 |  |  | Site Map | Failure to electronically submit a site map with all required content. | HSC 6.95 25505(a)(2), 25508(a)(1), 25508(a)(3) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 11 13 | Site Map |  | Site Map with all required content electronically submitted | 59 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit a site map with all required content. |  |  | OBSERVATION: The business failed to electronically submit a site map with all required content including: north orientation, loading area, internal roads, adjacent streets, storm and sewer drains, access and exit points, emergency shut offs, evacuation staging area, hazardous materials/waste storage areas and emergency response equipment. CORRECTIVE ACTION: Electronically submit a site map with all required content. | OBSERVATION: The business failed to complete and electronically submit a site map with all required content. CORRECTIVE ACTION: Complete and electronically submit a site map with all required content. | [5 empty] | Yes
Business Plan Program | Administration/Documentation | 1010010 |  |  | Emergency Response Plan and Procedures | Failure to establish and/or electronically submit an adequate emergency response plan and procedures for a release or threatened release of a hazardous material. *Verify agricultural handler exemption HSC 25507.1 | 19 CCR 4 2658; HSC 6.95 25505(a)(3), 25508(a)(1), 25508(a)(3) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 12 14 | Emergency Response Plan |  | Electronically submitted adequate response plan/procedures for release/threatened release of hazmat | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to establish and/or electronically submit an adequate emergency response plan and procedures for a release or threatened release of a hazardous material. *Verify agricultural handler exemption HSC 25507.1 |  |  | OBSERVATION: The business failed to establish and electronically submit adequate emergency response procedures for a release or threatened release of a hazardous material. CORRECTIVE ACTION: Establish and electronically submit adequate emergency response procedures for a release or threatened release of a hazardous material within 30 days. | [6 empty] | Yes
Business Plan Program | Training | 1020001 |  |  | Training Program Not Included or Not Adequate | Failure to establish and/or electronically submit an adequate training program in safety procedures in the event of a release or threatened release of a hazardous material. *Verify agricultural handler exemption HSC 25507.1 | 19 CCR 4 2659(a); HSC 6.95 25505(a)(4), 25508(a)(1), 25508(a)(3) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 13 15 | Training Program |  | Established and electronically submitted adequate training program | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to establish and/or electronically submit an adequate training program in safety procedures in the event of a release or threatened release of a hazardous material. *Verify agricultural handler exemption HSC 25507.1 |  |  | OBSERVATION: The business failed to establish and electronically submit an adequate employee training plan, which is reasonable and appropriate for the size of the business and the nature of the hazardous material handled. CORRECTIVE ACTION: Establish and electronically submit an adequate employee training plan, which is reasonable and appropriate for the size of the business and the nature of the hazardous material handled. | OBSERVATION: The business failed to establish and electronically submit an adequate employee training plan, which is reasonable and appropriate for the size of the business and the nature of the hazardous material(s) handled. CORRECTIVE ACTION: Establish and electronically submit an adequate training plan, which is reasonable and appropriate for the size of the business and the nature of the hazardous material(s) handled. | [5 empty] | Yes
Business Plan Program | Training | 1020002 |  |  | Training Not Provided and/or Documented | Failure to provide initial and annual training to all employees in safety procedures in the event of a release or threatened release of a hazardous material or failure to document and maintain training records for a minimum of three years. | HSC 6.95 25505(a)(4); 19 CCR 4 2659(b) | 2014-07-01 | 2099-12-31 | 2014-06-26 | Revised | 14 16 | Training Program |  | Provided initial and annual training and maintained training records for a minimum of three years | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide initial and annual training to all employees in safety procedures in the event of a release or threatened release of a hazardous material or failure to document and maintain training records for a minimum of three years. |  |  | OBSERVATION: The business failed to provide initial and annual training to all employees in safety procedures in the event of a release or threatened release of a hazardous material including familiarity with the emergency response plan or failure to document and maintain training records for a minimum of three years. CORRECTIVE ACTION: Establish and electronically submit an employee training program containing provisions to ensure initial and annual training for all employees in safety procedures in the event of a release or threatened release of a hazardous material and document and maintain training records for a minimum of three years. | OBSERVATION: The business failed to provide initial and annual training to all employees in safety procedures in the event of a release or threatened release of a hazardous material; or failed to document and maintains training records for a minimum of three years. CORRECTIVE ACTION: Establish and electronically submit an employee training program containing provisions for training applicable staff in release reporting procedures. Submit documentation to the unified program agency demonstrating appropriate personnel have received initial training and maintain ongoing annual training records for a minimum of three years. | OBSERVATION: The business did not provide one or more of the following: initial employee training, adequate employee training, annual employee training and/or maintain records of employee training. CORRECTIVE ACTION: Provide all employees with required training that includes: safe handling hazardous materials, emergency response procedures, and proper use of response equipment. Maintain records of training available for 3 years. |  |  |  |  | Yes
Business Plan Program | Administration/Documentation | 1010016 |  |  | Remote Unstaffed Facility | Failure to establish and electronically submit a business plan when not meeting the remote unstaffed facility exemption requirements. | HSC 6.95 25505, 25506, 25507.2, 25508(a)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 15 17 | Remote, Unstaffed |  | Remote unstaffed facility exemption requirements are met when not submitting a business plan | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to establish and electronically submit a business plan when not meeting the remote unstaffed facility exemption requirements. |  |  | OBSERVATION: This facility does not meet one or more of the following requirements: located at least half mile away from nearest occupies structure, inventory stored in limited quantities, facility is secured, warning signs posted, electronically submit a one time business plan and fee, onsite verification by the UPA. When not meeting all of these requirements, the facility is subject to all business plan requirements. CORRECTIVE ACTION: Establish and electronically submit a complete business plan. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010014 |  |  | Agricultural Handler Emergency Response Plan | Failure to electronically submit the emergency response plan and procedures when not meeting the agricultural handler exemption requirements. | 19 CCR 4 2670, 2671; HSC 6.95 25507.1(a), 25508(a)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 16 18 | Agricultural Handlers |  | Agricultural handler exemption requirements are met when not submitting an emergency response plan | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit the emergency response plan and procedures when not meeting the agricultural handler exemption requirements. |  |  | OBSERVATION: Agricultural facility did not comply with one or more of the following requirement: annually submit a business plan, post required signs on buildings and/or provide required training to employees. When not meeting all of these requirements, an emergency response plan is required to be established and electronically submitted. CORRECTIVE ACTION: Establish and electronically submit an emergency response plan. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010015 |  |  | Agricultural Handler Training Program | Failure to electronically submit the training program in safety procedures when not meeting the agricultural handler exemption requirements. | 19 CCR 4 2670, 2671; HSC 6.95 25507.1(a), 25508(a)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 17 19 | Agricultural Handlers |  | Agricultural handler exemption requirements are met when not submitting a training program | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit the training program in safety procedures when not meeting the agricultural handler exemption requirements. |  |  | OBSERVATION: Agricultural facility did not comply with one or more of the following requirement: annually submit a business plan, post required signs on buildings and/or provide required training to employees. When not meeting all of these requirements, a training plan is required to be established and electronically submitted. CORRECTIVE ACTION: Establish and electronically submit a training plan. | [6 empty] | Yes
Business Plan Program | Operations/Maintenance | 1030001 |  |  | Agricultural handlers warning signs | Failure of agricultural handler to post warning signs on buildings where pesticides, petroleum, or fertilizers are stored, that are visible from any direction of probable approach, contain all required information, and are in appropriate language | 19 CCR 4 2670, 2671; HSC 6.95 25507.1(a)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 18 20 | Agricultural Handlers |  | Warning signs posted on buildings where pesticides, petroleum, or fertilizers are stored | 88 | yes | yes | Yes | yes | yes | yes | yes | Minor | Yes |  | 30 | Failure of agricultural handler to post warning signs on buildings where pesticides, petroleum, or fertilizers are stored, that are visible from any direction of probable approach, contain all required information, and are in appropriate language |  |  | OBSERVATION: Owner/Operator failed to post warning signs on buildings where pesticides, petroleum, or fertilizers are stored that are visible from any direction of probable approach, contain all required information, and are in appropriate language. CORRECTIVE ACTION: Post warning signs on buildings where pesticides, petroleum, or fertilizers are stored, and meet all posting requirements. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010020 |  |  | Hazardous Materials Supplier Records | Failure to provide sale or provision records, within 5 days of a request from an UPA. | HSC 6.95 25507.5 | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 21 | Sale/Provision Record |  | Hazardous materials sale or provision records submitted to UPA within 5 days of request | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide sale or provision records, within 5 days of a request from an UPA. |  |  | OBSERVATION: Owner/Operator failed to provide sale or provision records, within 5 days of a request from an UPA. CORRECTIVE ACTION: Submit copies of requested hazardous materials sale or provision records as requested by the UPA. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010021 |  |  | Hazardous Materials Transfer Disclosure | Failure of a handler to notify and disclose a hazardous material transfer, when directed by an UPA. | HSC 6.95 25508.3 | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 22 | Transfer Disclosure |  | Notified UPA, when instructed to do so, of hazardous materials transfer | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a handler to notify and disclose a hazardous material transfer, when directed by an UPA. |  |  | OBSERVATION: Owner/Operator failed to notify and disclose a hazardous material transfer, after being directed to do so by the UPA. CORRECTIVE ACTION: Provide required disclosure information for hazardous materials that have been, or are to be, transferred to another location, if the quantities are equal to, or greater than, 165 gallons, 600 cubic feet, or 1500 pounds. | [6 empty] | Yes
Business Plan Program | Administration/Documentation | 1010 |  |  | HMBP-Administration/Documentation - General | Administration/Documentation - General | 19 CCR 4 Multiple Sections; HSC 6.95 Multiple Sections | 2011-07-01 | 2099-12-31 | 2014-06-26 14:39 | Revised | 19 23 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes
Business Plan Program | Administration/Documentation | 1015 |  |  | HMBP-Administration/Documentation - General Local Ordinance | Administration/Documentation - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 20 24 | General Facility Requirements |  | Administration/Documentation - General Local Ordinance | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General Local Ordinance | [9 empty] | Yes
Business Plan Program | Training | 1020 |  |  | HMBP-Training - General | Training - General | 19 CCR 4 Multiple Sections; HSC 6.95 Multiple Sections | 2011-07-01 | 2099-12-31 | 2014-06-26 | Revised | 21 25 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes
Business Plan Program | Training | 1025 |  |  | HMBP-Training - General Local Ordinance | Training - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 22 26 | General Facility Requirements |  | Training - General Local Ordinance | 34 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General Local Ordinance | [9 empty] | Yes
Business Plan Program | Operations/Maintenance | 1030 |  |  | HMBP-Operations/Maintenance - General | Operations/Maintenance - General | 19 CCR 4 Multiple Sections; HSC 6.95 Multiple Sections | 2011-07-01 | 2099-12-31 | 2014-06-26 | Revised | 23 27 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes
Business Plan Program | Operations/Maintenance | 1035 |  |  | HMBP-Operations/Maintenance - General Local Ordinance | Operations/Maintenance - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 24 28 | General Facility Requirements |  | Operations/Maintenance - General Local Ordinance | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General Local Ordinance | [9 empty] | Yes
Business Plan Program | Release/Leaks/Spills | 1040 |  |  | HMBP-Release/Leaks/Spills - General | Release/Leaks/Spills - General | 19 CCR 4 Multiple Sections; HSC 6.95 Multiple Sections | 2011-07-01 | 2099-12-31 | 2014-06-26 | Revised | 25 29 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes
Business Plan Program | Release/Leaks/Spills | 1045 |  |  | HMBP-Release/Leaks/Spills - General Local Ordinance | Release/Leaks/Spills - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 26 30 | General Facility Requirements |  | Release/Leaks/Spills - General Local Ordinance | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General Local Ordinance | [9 empty] | Yes
Business Plan Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 1050 |  |  | HMBP-Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 19 CCR 4 Multiple Sections; HSC 6.95 Multiple Sections | 2011-07-01 | 2099-12-31 | 2014-06-26 | Revised | 27 31 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes
Business Plan Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 1055 |  |  | HMBP- Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 28 32 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | [9 empty] | Yes

## CalARP
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | CalARP Level 1 | CalARP Level 2 | CalARP Level 3 | CalARP Level 4
CalARP Program | Administration/Documentation | 5010001 |  |  | Applicability: Table 1 or 2 | Failure to comply with the provisions of 19 CCR 4.5 pursuant to the time frames identified in Section 2745.1(b) if a stationary source has a process with more than a threshold quantity of a regulated substance as listed in Tables 1 or 2 of Section 2770.5. | 19 CCR 4.5 2735.4(a)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 1 | General | General Applicability | Complied with CalARP provisions when having a RS in a process listed in Table 1/2 | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to comply with the provisions of 19 CCR 4.5 pursuant to the time frames identified in Section 2745.1(b) if a stationary source has a process with more than a threshold quantity of a regulated substance as listed in Tables 1 or 2 of Section 2770.5. |  |  | OBSERVATION: The stationary source has a process with more than a threshold quantity of a regulated substance onsite as listed in Table 1/Table 2 and has not complied with the provisions of Title 19, Division 2, Chapter 4.5 by the date on which the regulated substance was first present in a process above the threshold quantity. CORRECTIVE ACTION: Contact the CUPA to determine adequate timelines for full implementation. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010002 |  |  | Applicability: Table 3 | Failure to comply with the appropriate provisions of 19 CCR 4.5 prior to the date in which a regulated substance is first present in a process above the listed threshold quantity, as listed in Table 3 of Section 2770.5. | 19 CCR 4.5 2735.4(a)(2) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 2 | General | General Applicability | Complied with CalARP provisions when having a RS in a process listed in Table 3 | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to comply with the appropriate provisions of 19 CCR 4.5 prior to the date in which a regulated substance is first present in a process above the listed threshold quantity, as listed in Table 3 of Section 2770.5. |  |  | OBSERVATION: The stationary source has a process with more than a threshold quantity of a regulated substance onsite as listed in Table 3 and has not complied with the provisions of Title 19, Division 2, Chapter 4.5 by the date on which the regulated substance was first present in a process above the threshold quantity. CORRECTIVE ACTION: Contact the CUPA to determine adequate timelines for full implementation. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010003 |  |  | Applicability: Tables 1 or 2 and Table 3 | Failure to comply with the provisions of 19 CCR 4.5 pursuant to the time frames identified in Section 2745.1(b) if a stationary source has a process with more than a threshold quantity of a regulated substance as listed in Tables 1 or 2 and Table 3 of Section 2770.5. | 19 CCR 4.5 2735.4(a)(3) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 3 | General | General Applicability | Complied with CalARP provisions when having a RS in a process listed in Table 1/2 and 3 | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to comply with the provisions of 19 CCR 4.5 pursuant to the time frames identified in Section 2745.1(b) if a stationary source has a process with more than a threshold quantity of a regulated substance as listed in Tables 1 or 2 and Table 3 of Section 2770.5. |  |  | OBSERVATION: The stationary source has a process with more than a threshold quantity of a regulated substance onsite as listed in Table 1/Table 2/ and Table 3 and has not complied with the provisions of Title 19, Division 2, Chapter 4.5 by the date on which the regulated substance was first present in a process above the threshold quantity. CORRECTIVE ACTION: Contact the CUPA to determine adequate timelines for full implementation. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010004 |  |  | General Requirements: Risk Management Plan Coordination | Failure of the owner or operator of a stationary source to closely coordinate with the UPA to implement the requirements of 19 CCR 4.5 and to determine the appropriate level of documentation required for a Risk Management Plan to comply with Sections 2745.3 through 2745.9. | 19 CCR 4.5 2735.5(a) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 4 | General | Coordination | Closely coordinated with the UPA to implement the CalARP requirements | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator of a stationary source to closely coordinate with the UPA to implement the requirements of 19 CCR 4.5 and to determine the appropriate level of documentation required for a Risk Management Plan to comply with Sections 2745.3 through 2745.9. |  |  | OBSERVATION: The owner/operator of the stationary source failed to closely coordinate with the CUPA to implement the requirements of Title 19, Division 2, Chapter 4.5 and to determine the appropriate level of documentation required for a Risk Management Plan to comply with sections 2745.3 through 2745.9. CORRECTIVE ACTION: Contact the CUPA to coordinate implementation of the requirements and to determine the appropriate level documentation required for a Risk Management Plan. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010006 |  |  | General Requirements: Program 1 Requirements - Emergency Response | Failure to ensure that response actions have been coordinated with local emergency planning and response agencies | 19 CCR 4.5 2735.5(d)(3) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 5 | General | Coordination | Ensured response actions have been coordinated with local emergency planning and response agencies. | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that response actions have been coordinated with local emergency planning and response agencies |  |  | OBSERVATION: The owner/operator of the stationary source failed to ensure that response actions have been coordinated with local emergency planning and response agencies. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that response actions have been coordinated with local emergency planning and response agencies. | [6 empty] | Yes | No | No | No
CalARP Program | Administration/Documentation | 5010009 |  |  | CalARP Program Management System: Program Level 2 or 3 | Failure to develop a management system to oversee the implementation of the risk management program elements. | 19 CCR 4.5 2735.6(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 6 | General | Management System - Program Level 2 or 3 | Developed a management system to oversee the implementation of the risk management program elements. | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to develop a management system to oversee the implementation of the risk management program elements. |  |  | OBSERVATION: The owner/operator of the stationary source failed to develop a management system to oversee the implementation of the risk management program elements. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating a management system to oversee the implementation of the risk management program elements has been developed. | [6 empty] | No | Yes | Yes | No
CalARP Program | Administration/Documentation | 5010010 |  |  | CalARP Program Management System: Program Level 2 or 3 - Overall Responsibility | Failure to assign a qualified person or position who has the overall responsibility for the development, implementation, and integration of the risk management program elements. | 19 CCR 4.5 2735.6(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 7 | General | Management System - Program Level 2 or 3 | Assigned a qualified person or position who has the overall responsibility for the RMP elements. | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to assign a qualified person or position who has the overall responsibility for the development, implementation, and integration of the risk management program elements. |  |  | OBSERVATION: The owner/operator of the stationary source failed to assign a qualified person or position who has the overall responsibility for the development, implementation, and integration of the risk management program elements. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating a qualified person or position who has the overall responsibility for the development, implementation, and integration of the risk management program elements has been assigned. | [6 empty] | No | Yes | Yes | No
CalARP Program | Administration/Documentation | 5010011 |  |  | CalARP Program Management System: Program Level 2 or 3 - Org Chart | Failure to document the following when responsibility for implementing individual requirements of 19 CCR 4.5 is assigned to persons other than the person identified in 19 CCR section 2735.6(b): 1. Names or positions. 2. Lines of authority defined through an organization chart or similar document. | 19 CCR 4.5 2735.6(c) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 8 | General | Management System - Program Level 2 or 3 | Documented the names or positions and lines of authority through an organization chart or document. | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to document the following when responsibility for implementing individual requirements of 19 CCR 4.5 is assigned to persons other than the person identified in 19 CCR section 2735.6(b): 1. Names or positions. 2. Lines of authority defined through an organization chart or similar document. |  |  | OBSERVATION: The owner/operator of the stationary source failed to document the names or positions and lines of authority defined through an organization chart or similar document when responsibility for implementing individual requirements of 19 CCR 4.5 is assigned to persons other than the qualified person or position who has the overall responsibility for the development, implementation, and integration of the risk management program elements. CORRECTIVE ACTION: Submit a copy of the organization chart or similar document to the CUPA defining the names or positions and lines of authority of the person(s) responsible for implementing individual requirements of the risk program elements. | [6 empty] | No | Yes | Yes | No
CalARP Program | Administration/Documentation | 5010005 |  |  | General Requirements: Risk Management Plan - Program Level 1 | Failure to submit an RMP which includes all requirements described in Sections 2745.3 through 2745.5 and 2745.8 through 2745.9. | 19 CCR 4.5 2735.5(b)(1), 2735.5(d), 2745.1(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 9 | RMP Components and Submission | RMP Submission - Program Level 1 | Submitted a RMP which includes all requirements in Section 2745.3 to 2745.5 and 2745.8 to 2745.9 | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit an RMP which includes all requirements described in Sections 2745.3 through 2745.5 and 2745.8 through 2745.9. |  |  | OBSERVATION: The owner/operator of the stationary source failed to submit a Risk Management Plan which includes all requirements described in Sections 2745.3 through 2745.5 and 2745.8 through 2745.9. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan to the CUPA that includes all requirements described in Sections 2745.3 through 2745.5 and 2745.8 through 2745.9. | [6 empty] | Yes | No | No | No
CalARP Program | Administration/Documentation | 5010007 |  |  | General Requirements: Risk Management Plan - Program Level 2, 3, or 4 | Failure to submit an RMP which includes all requirements described in Sections 2745.3 through 2745.9. | 19 CCR 4.5 2735.5(b)(1), 2745.1(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 10 | RMP Components and Submission | RMP Submission - Program Level 2, 3, or 4 | Submitted a RMP which includes all requirements in Section 2745.3 through 2745.9 | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit an RMP which includes all requirements described in Sections 2745.3 through 2745.9. |  |  | OBSERVATION: The owner/operator of the stationary source failed to submit a Risk Management Plan which includes all requirements described in Sections 2745.3 through 2745.9. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan to the CUPA that includes all requirements described in Sections 2745.3 through 2745.9. | [6 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010018 |  |  | Submission: Risk Management Plan Existing Stationary Source - Table 3 | Failure of a stationary source to submit a Risk Management Plan to the UPA after the owner or operator has received a notice from the UPA requesting submission of a Risk Management Plan. | CHSC 25536(b) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 11 | RMP Components and Submission | RMP Submission | RMP submitted to UPA after request to submit was received | 57 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of a stationary source to submit a Risk Management Plan to the UPA after the owner or operator has received a notice from the UPA requesting submission of a Risk Management Plan. |  |  | OBSERVATION: Owner/Operator failed to submit a Risk Management Plan (RMP) to the UPA after being notified by the UPA to submit the RMP. CORRECTIVE ACTION: Complete and submit RMP to the UPA by [specify compliance date]. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010016 |  |  | Submission to USEPA: Risk Management Plan - Table 1 or 2 | Failure to submit the RMP information required by the USEPA to the USEPA per the schedule below: 1. Three years after the date on which a regulated substance is first listed under Section 68.130, Part 68, Title 40 of CFR; or 2. The date on which a regulated substance is first present in a process, above the threshold quantity, as listed on Section 2770.5 Table 1 or 2. | 19 CCR 4.5 2745.1(b)(1), 2745.1(b)(2) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 12 | RMP Components and Submission | RMP Submission | Submitted the RMP information required by the USEPA to the USEPA | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to submit the RMP information required by the USEPA to the USEPA per the schedule below: 1. Three years after the date on which a regulated substance is first listed under Section 68.130, Part 68, Title 40 of CFR; or 2. The date on which a regulated substance is first present in a process, above the threshold quantity, as listed on Section 2770.5 Table 1 or 2. |  |  | OBSERVATION: The owner/operator failed to submit the Risk Management Plan information required by the USEPA to the USEPA within three years after the date on which a regulated substance is first listed under Section 68.130, Part 68, Title 40 of CFR. CORRECTIVE ACTION: Submit the Risk Management Plan information required by the USEPA to the USEPA. | OBSERVATION: The owner/operator failed to submit the Risk Management Plan information required by the USEPA to the USEPA prior to the date on which a regulated substance is first present in a process, above the threshold quantity, as listed on Section 2770.5 Table 1 or 2. CORRECTIVE ACTION: Submit the Risk Management Plan information required by the USEPA to the USEPA. | [5 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010017 |  |  | Submission to UPA: Risk Management Plan - Table 1 or 2 | Failure to submit a copy of the USEPA required RMP information according to the time frame set forth in 2745.1(b) to the UPA. | 19 CCR 4.5 2745.1(c) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 13 | RMP Components and Submission | RMP Submission | Submitted the RMP information required by the USEPA to the UPA within required time frame | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to submit a copy of the USEPA required RMP information according to the time frame set forth in 2745.1(b) to the UPA. |  |  | OBSERVATION: The owner/operator failed to submit the Risk Management Plan information required by the USEPA to the UPA within three years after the date on which a regulated substance is first listed under Section 68.130, Part 68, Title 40 of CFR. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan information required by the USEPA to the UPA. | OBSERVATION: The owner/operator failed to submit the RMP information required by the USEPA to the CUPA prior to the date on which a regulated substance is first present in a process, above the threshold quantity, as listed on Section 2770.5 Table 1 or 2. CORRECTIVE ACTION: Submit a copy of the RMP information required by the USEPA to the CUPA. | [5 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010019 |  |  | Submission: Risk Management Plan New or Modified Stationary Source - Table 3 | Failure of a new or modified stationary source to submit a Risk Management Plan to the UPA prior to the date in which a regulated substance is first present in a process above the listed threshold quantity. | 19 CCR 4.5 2745.1(d) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 14 | RMP Components and Submission | RMP Submission | Submitted a RMP to the UPA prior to the date a RS is in a process above the threshold quantity | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure of a new or modified stationary source to submit a Risk Management Plan to the UPA prior to the date in which a regulated substance is first present in a process above the listed threshold quantity. |  |  | OBSERVATION: (Program 1 facility) The owner/operator failed to submit a Risk Management Plan to the CUPA prior to the date in which a regulated substance is first present in a process above the listed threshold quantity. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan to the CUPA that includes the information required by Sections 2745.3 through 2745.5 and 2745.8 through 2745.9. | OBSERVATION: (Program 2 or 3 facility) The owner/operator failed to submit a Risk Management Plan to the CUPA prior to the date in which a regulated substance is first present in a process above the listed threshold quantity. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan to the CUPA that includes the information required by Sections 2745.3 through 2745.9. | [5 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010020 |  |  | Submission: Risk Management Plan Classified Information | Failure to exclude classified information from the Risk Management Plan. | 19 CCR 4.5 2745.1(h) | 2016-06-01 | 2099-12-31 | 2016-05-31 | Existing | 15 | RMP Components and Submission | RMP Submission | Excluded classified information from the RMP | 44 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to exclude classified information from the Risk Management Plan. |  |  | OBSERVATION: The owner/operator failed to exclude classified information in the Risk Management Plan. CORRECTIVE ACTION: Submit a copy of the Risk Management Plan to the CUPA with an annex for classified information. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010021 |  |  | Risk Management Plan Review Process: Consultation and Review - Certified Complete by Qualified Person | Failure to ensure that the Risk Management Plan is certified complete by a qualified person and the stationary source owner or operator. | 19 CCR 4.5 2745.2(a) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 16 | RMP Components and Submission | RMP Submission | Ensured that the RMP is certified complete by a qualified person and the owner or operator | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that the Risk Management Plan is certified complete by a qualified person and the stationary source owner or operator. |  |  | OBSERVATION: The owner/operator failed to ensure that the Risk Management Plan is certified complete by a qualified person and the stationary source owner or operator. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the Risk Management Plan has been certified complete by a qualified person and the stationary source owner or operator. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010023 |  |  | RMP Certification: Program Level 1 | Failure to submit in the Risk Management Plan the certification statement provided in Section 2735.5(d)(4) | 19 CCR 4.5 2745.9(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 17 | RMP Components and Submission | RMP Certification - Program Level 1 | Submitted in the RMP the required certification statement (Prog 1) | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit in the Risk Management Plan the certification statement provided in Section 2735.5(d)(4) |  |  | OBSERVATION: The owner/operator failed to submit in the Risk Management Plan the certification statement provided in Section 2735.5(d)(4). CORRECTIVE ACTION: Submit the certification statement provided in Section 2735.5(d)(4) to the CUPA. | [6 empty] | Yes | No | No | No
CalARP Program | Administration/Documentation | 5010024 |  |  | RMP Certification: Program Level 2, 3, or 4 | Failure to submit in the Risk Management Plan a single certification that, to the best of the signer’s knowledge, information, and belief formed after reasonable inquiry, the information submitted is true, accurate, and complete. | 19 CCR 4.5 2745.9(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 18 | RMP Components and Submission | RMP Certification - Program Level 2, 3, or 4 | Submitted in the RMP the required certification statement (Prog 2, 3, or 4) | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit in the Risk Management Plan a single certification that, to the best of the signer’s knowledge, information, and belief formed after reasonable inquiry, the information submitted is true, accurate, and complete. |  |  | OBSERVATION: The owner/operator failed to submit in the Risk Management Plan a single certification that, to the best of the signer’s knowledge, information, and belief formed after reasonable inquiry, the information submitted is true, accurate, and complete. CORRECTIVE ACTION: Submit a single certification to the CUPA that, to the best of the signer’s knowledge, information, and belief formed after reasonable inquiry, the information submitted is true, accurate, and complete. | [6 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010025 |  |  | RMP Updates: Table 1 or 2 | Failure to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the UPA as follows: 1. At least once every five years from the date of its initial submission or most recent update required by section 2745.10(a)(2) through (7); 2. No later than three years after a newly regulated substance is first listed by the United States Environmental Protection Agency; 3. No later than the date on which a new regulated substance is first present in an already covered process above a threshold quantity; 4. No later than the date on which a regulated substance is first present above a threshold quantity in a new process; 5. Within six months of a change that requires a revised process hazard analysis or hazard review. 6. Within six months of a change that requires a revised offsite consequence analysis as provided in section 2750.7; 7. Within six months of a change that alters the program level that applied to any covered process. | 19 CCR 4.5 2745.10(a) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 19 | RMP Components and Submission | RMP Updates | Revised, updated, and submitted the RMP to the USEPA and UPA per required timelines (Table 1 or 2) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the UPA as follows: 1. At least once every five years from the date of its initial submission or most recent update required by section 2745.10(a)(2) through (7); 2. No later than three years after a newly regulated substance is first listed by the United States Environmental Protection Agency; 3. No later than the date on which a new regulated substance is first present in an already covered process above a threshold quantity; 4. No later than the date on which a regulated substance is first present above a threshold quantity in a new process; 5. Within six months of a change that requires a revised process hazard analysis or hazard review. 6. Within six months of a change that requires a revised offsite consequence analysis as provided in section 2750.7; 7. Within six months of a change that alters the program level that applied to any covered process. |  |  | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the UPA at least once every five years from the date of its initial submission or most recent update required by Section 2745.10(a)(2) through (7). CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the UPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA no later than three years after a newly regulated substance is first listed by the United States Environmental Protection Agency. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA no later than the date on which on which a new regulated substance is first present in an already covered process above a threshold quantity. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA no later than the date on which a regulated substance is first present above a threshold quantity in a new process. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA within six months of a change that requires a revised process hazard analysis or hazard review. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA within six months of a change that requires a revised offsite consequence analysis as provided in Section 2750.7. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the United States Environmental Protection Agency and the CUPA within six months of a change that alters the program level that applied to any covered process. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the United States Environmental Protection Agency and the CUPA. | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010026 |  |  | RMP Updates: Table 3 | Failure to revise, update, and submit the Risk Management Plan to the UPA as follows: 1. At least once every five years from the date of its initial submission or most recent update required by section 2745.10(b)(2) through (7); 2. No later than three years after a newly regulated substance is first listed by the California Office of Emergency Services. 3. No later than the date on which a new regulated substance is first present in an already covered process above a threshold quantity; 4. No later than the date on which a regulated substance is first present above a threshold quantity in a new process; 5. Within six months of a change that requires a revised process hazard analysis or hazard Review. 6. Within six months of a change that requires a revised offsite consequence analysis as provided in section 2750.7; 7. Within six months of a change that alters the program level that applied to any covered process. | 19 CCR 4.5 2745.10(b) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 20 | RMP Components and Submission | RMP Updates | Revised, updated, and submitted the RMP to the USEPA and UPA per required timelines (Table 3) | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to revise, update, and submit the Risk Management Plan to the UPA as follows: 1. At least once every five years from the date of its initial submission or most recent update required by section 2745.10(b)(2) through (7); 2. No later than three years after a newly regulated substance is first listed by the California Office of Emergency Services. 3. No later than the date on which a new regulated substance is first present in an already covered process above a threshold quantity; 4. No later than the date on which a regulated substance is first present above a threshold quantity in a new process; 5. Within six months of a change that requires a revised process hazard analysis or hazard Review. 6. Within six months of a change that requires a revised offsite consequence analysis as provided in section 2750.7; 7. Within six months of a change that alters the program level that applied to any covered process. |  |  | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the UPA at least once every five years from the date of its initial submission or most recent update required by section 2745.10(b)(2) through (7). CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the UPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA no later than three years after a newly regulated substance is first listed by the California Emergency Management Agency. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA no later than the date on which on which a new regulated substance is first present in an already covered process above a threshold quantity. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA no later than the date on which a regulated substance is first present above a threshold quantity in a new process. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA within six months of a change that requires a revised process hazard analysis or hazard review. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA within six months of a change that requires a revised offsite consequence analysis as provided in Section 2750.7. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | OBSERVATION: The owner/operator failed to revise, update, and submit the Risk Management Plan to the CUPA within six months of a change that alters the program level that applied to any covered process. CORRECTIVE ACTION: Revise, update, and submit a copy of the Risk Management Plan to the CUPA. | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010027 |  |  | RMP Updates: Table 1 or 2 De-registration | Failure to submit a de-registration to the United States Environmental Protection Agency and the UPA within six months indicating that the stationary source is no longer covered | 19 CCR 4.5 2745.10(c) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 21 | RMP Components and Submission | RMP Updates | Submitted a de-registration to the USEPA and UPA within six months of the RS removal. | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a de-registration to the United States Environmental Protection Agency and the UPA within six months indicating that the stationary source is no longer covered |  |  | OBSERVATION: The owner/operator failed to submit a de-registration to the United States Environmental Protection Agency and the UPA within six months indicating that the stationary source is no longer covered. CORRECTIVE ACTION: Submit a copy of the de-registration to the United States Environmental Protection Agency and the UPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010028 |  |  | RMP Updates: Table 3 De-registration | Failure to submit a de-registration to the UPA within six months indicating that the stationary source is no longer covered. | 19 CCR 4.5 2745.10(d) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 22 | RMP Components and Submission | RMP Updates | Submitted a de-registration to the UPA within six months of the RS removal. | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a de-registration to the UPA within six months indicating that the stationary source is no longer covered. |  |  | OBSERVATION: The owner/operator failed to submit a de-registration to the UPA within six months indicating that the stationary source is no longer covered. CORRECTIVE ACTION: Submit a copy of the de-registration to the UPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010029 |  |  | RMP Updates: Change of Owner or Operator | Failure to contact the UPA within 30 days of a change of owner or operator to update the registration information. | 19 CCR 4.5 2745.10(f) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 23 | RMP Components and Submission | RMP Updates | Contacted the UPA within 30 days of a change of owner or operator to update the registration | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to contact the UPA within 30 days of a change of owner or operator to update the registration information. |  |  | OBSERVATION: The owner/operator failed to contact the UPA within 30 days of a change of owner or operator to update the registration information. CORRECTIVE ACTION: Update the registration information and submit a copy to the UPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010030 |  |  | Required RMP Corrections: New Accident History Information | Failure to correct and submit the data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l), for any accidental release meeting the five year accident history reporting criteria of Section 2750.9, with respect to that accident within six months of the release or by the time the Risk Management Plan is updated under Section 2745.10, whichever is earlier. | 19 CCR 4.5 2745.10.5(a) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 24 | RMP Components and Submission | RMP Corrections | Corrected and submitted required RMP data after accident/incident investigation | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to correct and submit the data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l), for any accidental release meeting the five year accident history reporting criteria of Section 2750.9, with respect to that accident within six months of the release or by the time the Risk Management Plan is updated under Section 2745.10, whichever is earlier. |  |  | OBSERVATION: The owner/operator failed to correct and submit the data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l), for any accidental release meeting the five year accident history reporting criteria of Section 2750.9, with respect to that accident within six months of the release. CORRECTIVE ACTION: Submit a copy of the revised data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l) to the UPA. | OBSERVATION: The owner/operator failed to correct and submit the data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l) with respect to that accident by the time the Risk Management Plan is to be updated under Section 2745.10. CORRECTIVE ACTION: Submit a copy of the revised data required in the Risk Management Plan under sections 2745.5, 2745.6(j), and 2745.7(l) to the CUPA. | [5 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010031 |  |  | Required RMP Corrections: Emergency Contact Information | Failure to correct and submit the emergency contact information in the Risk Management Plan required under Section 2740.1(d)(6) within one month of any change | 19 CCR 4.5 2745.10.5(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 25 | RMP Components and Submission | RMP Corrections | Corrected and submitted the emergency contact information in the RMP within one month of any change | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to correct and submit the emergency contact information in the Risk Management Plan required under Section 2740.1(d)(6) within one month of any change |  |  | OBSERVATION: The owner/operator failed to correct and submit the emergency contact information in the Risk Management Plan required under Section 2740.1(d)(6) within one month of any change. CORRECTIVE ACTION: Correct and submit a copy of the emergency contact information in the Risk Management Plan required under Section 2740.1(d)(6) to the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010032 |  |  | Covered Process Modification: Prenotification | Failure to notify the UPA in writing of the intent to modify the stationary source at least five calendar days before implementing any modifications or no later than 48 hours following the modification if prenotification is not reasonable. | 19 CCR 4.5 2745.11(a)(1) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 26 | RMP Components and Submission | Covered Process Modification | Notified the UPA in writing at least five calendar days before implementing any modifications | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to notify the UPA in writing of the intent to modify the stationary source at least five calendar days before implementing any modifications or no later than 48 hours following the modification if prenotification is not reasonable. |  |  | OBSERVATION: The owner/operator failed to notify the UPA in writing of the intent to modify the stationary source at least five calendar days before implementing any modifications or no later than 48 hours following the modification if prenotification is not reasonable. CORRECTIVE ACTION: Submit a statement to the UPA demonstrating how the owner/operator will notify the UPA in writing of the intent to modify the stationary source at least five calendar days before implementing any modifications or no later than 48 hours following the modification if prenotification is not reasonable. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010033 |  |  | Covered Process Modification: Establish Procedures to Manage Proposed Modification | Failure to establish procedures to manage the proposed modification, which shall be substantially similar to the procedures specified in Sections 2760.6 and 2760.7, and notify the UPA that the procedures have been established. | 19 CCR 4.5 2745.11(a)(2) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 27 | RMP Components and Submission | Covered Process Modification | Established procedures to manage a proposed modification and notified UPA | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to establish procedures to manage the proposed modification, which shall be substantially similar to the procedures specified in Sections 2760.6 and 2760.7, and notify the UPA that the procedures have been established. |  |  | OBSERVATION: The owner/operator failed to establish procedures to manage the proposed modification, which shall be substantially similar to the procedures specified in Sections 2760.6 and 2760.7, and notify the UPA that the procedures have been established. CORRECTIVE ACTION: Establish procedures to manage the proposed modification and notify the UPA in writing that this was completed. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010262 |  |  | Covered Process Modification: Revise Appropriate Documents within 60 Days | Failure to revise the appropriate documents as required pursuant to section 2745.11(a), expeditiously, but not later than 60 days from the date of the stationary source modification. | 19 CCR 4.5 2745.11(b) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 28 | RMP Components and Submission | Covered Process Modification | Revised appropriate documents within 60 days after covered process modification | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to revise the appropriate documents as required pursuant to section 2745.11(a), expeditiously, but not later than 60 days from the date of the stationary source modification. |  |  | OBSERVATION: Owner/operator failed to revise the appropriate documents as required pursuant to section 2745.11(a), expeditiously, but not later than 60 days from the date of the stationary source modification. CORRECTIVE ACTION: Consult with UPA to determine which documents must be revised and complete document revisions. Submit documentation of revisions. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010034 |  |  | Certificate of Occupancy | Failure of a new or modified stationary source to comply with Section 65850.2(b) of the Government Code prior to the issuance of a certificate of occupancy | 19 CCR 4.5 2745.12 | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 29 | RMP Components and Submission | Certificate of Occupancy | Complied with Government Code Section 65850.2(b) prior to issuance of a certificate of occupancy | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a new or modified stationary source to comply with Section 65850.2(b) of the Government Code prior to the issuance of a certificate of occupancy |  |  | OBSERVATION: The owner/operator failed to comply with Section 65850.2(b) of the Government Code prior to the issuance of a certificate of occupancy. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating you have complied with Section 65850.2(b) of the Government Code. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010022 |  |  | Risk Management Plan Review Process: Deficiency Notice | Failure to correct deficiencies within 60 calendar days from receipt of the notification of Risk Management Plan deficiencies. | 19 CCR 4.5 2745.2(b)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 30 | RMP Components and Submission | RMP Review | Corrected deficiencies within 60 calendar days from receipt of the notification of RMP deficiencies | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to correct deficiencies within 60 calendar days from receipt of the notification of Risk Management Plan deficiencies. |  |  | OBSERVATION: The owner/operator failed to correct deficiencies within 60 calendar days from receipt of the notification of Risk Management Plan deficiencies. CORRECTIVE ACTION: Revise and submit a copy of the Risk Management Plan to the CUPA that includes all corrections identified in the deficiency notice. | OBSERVATION: The owner/operator failed to correct deficiencies within 90 calendar days (60 calendar days plus a one time 30 calendar days extension) from receipt of the notification of Risk Management Plan deficiencies. CORRECTIVE ACTION: Revise and submit a copy of the Risk Management Plan to the CUPA that includes all corrections identified in the deficiency notice. | [5 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010008 |  |  | General Requirements: Risk Management Plan Registration | Failure to include a registration in the Risk Management Plan that reflects all covered processes. | 19 CCR 4.5 2735.5(b)(2) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 31 | Registration |  | Included a registration in the RMP that reflects all covered processes | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to include a registration in the Risk Management Plan that reflects all covered processes. |  |  | OBSERVATION: The owner/operator of the stationary source failed to include a registration in the Risk Management Plan that reflects all covered processes. CORRECTIVE ACTION: Submit a copy of the registration to the CUPA that reflects all covered processes. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010012 |  |  | Registration: Table 1 or 2 | Failure to complete the registration information required in 2740.1(d) and submit it with the Risk Management Plan to the United States Environmental Protection Agency, with a copy provided to the UPA. | 19 CCR 4.5 2740.1(a) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 32 | Registration |  | Completed the registration information and submitted it with the RMP to the USEPA and the UPA | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to complete the registration information required in 2740.1(d) and submit it with the Risk Management Plan to the United States Environmental Protection Agency, with a copy provided to the UPA. |  |  | OBSERVATION: The owner/operator of the stationary source failed to complete the registration information required in Section 2740.1(d) and submit it with the Risk Management Plan to the United States Environmental Protection Agency, with a copy provided to the CUPA. CORRECTIVE ACTION: Complete and submit a copy of the registration information required in Section 2740.1(d) to the USEPA and the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/ Documentation | 5010013 |  |  | Registration: Table 3 | Failure to complete the registration information required in section 2740.1(d) and submit it with the Risk Management Plan to the UPA. | 19 CCR 4.5 2740.1(b) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 33 | Registration |  | Completed the registration information and submitted it with the RMP to the UPA | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to complete the registration information required in section 2740.1(d) and submit it with the Risk Management Plan to the UPA. |  |  | OBSERVATION: The owner/operator of the stationary source failed to complete the registration information required in Section 2740.1(d) and submit it with the Risk Management Plan to the CUPA. CORRECTIVE ACTION: Complete and submit a copy of the registration information required in section 2740.1(d) to the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010014 |  |  | Registration: UPA Request | Failure to submit a registration to the UPA prior to submittal of the Risk Management Plan upon request. | 19 CCR 4.5 2740.1(c) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 34 | Registration |  | Submitted a registration with a certification of accuracy to the UPA prior to submittal of the RMP | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to submit a registration to the UPA prior to submittal of the Risk Management Plan upon request. |  |  | OBSERVATION: The owner/operator of the stationary source failed to submit a registration with a certification of accuracy to the CUPA (Upon request) prior to submittal of the Risk Management Plan. CORRECTIVE ACTION: Complete and submit a copy of the registration information required in section 2740.1(d) with a certification of accuracy to the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010015 |  |  | Registration: Data | Failure to include the data required in 2740.1 (d)(1) through (d)(20) in the registration. | 19 CCR 4.5 2740.1(d) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 35 | Registration |  | Included the data required in Section 2740.1 (d)(1) through (d)(20) in the registration | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include the data required in 2740.1 (d)(1) through (d)(20) in the registration. |  |  | OBSERVATION: The owner/operator of the stationary source failed to include all the data required in Section 2740.1(d)(1) through (d)(20) in the registration. CORRECTIVE ACTION: Complete and resubmit a copy of the registration including all information required in Section 2740.1(d)(1) through (d)(20) to the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010035 |  |  | Hazard Assessment: Program Level 1 - Worst-Case Release Scenario | Failure to prepare a worst-case release scenario analysis as provided in Section 2750.3 | 19 CCR 4.5 2750.1 | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 36 | Hazard Assessment | General Applicability | Prepared a worst-case release scenario analysis | 47 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to prepare a worst-case release scenario analysis as provided in Section 2750.3 |  |  | OBSERVATION: The owner/operator failed to prepare a worst-case release scenario analysis. CORRECTIVE ACTION: Prepare the worst-case release scenario analysis as provided in Section 2750.3 and submit a copy to the UPA. | OBSERVATION: The owner/operator failed to prepare a worst-case release scenario analysis that complies with all requirements in Section 2750.3. CORRECTIVE ACTION: Revise and resubmit a copy of the worst-case release scenario analysis to the CUPA and ensure that it complies with all requirements in Section 2750.3. | [5 empty] | Yes | No | No | No
CalARP Program | Administration/Documentation | 5010036 |  |  | Hazard Assessment: Program Level 1 - Five-Year Accident History | Failure to complete the five-year accident history as provided in Section 2750.9 | 19 CCR 4.5 2750.1 | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 37 | Hazard Assessment | General Applicability | Completed the five-year accident history | 40 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to complete the five-year accident history as provided in Section 2750.9 |  |  | OBSERVATION: The owner/operator failed to complete the five-year accident history. CORRECTIVE ACTION: Prepare the five-year accident history as provided in Section 2750.9. and submit a copy to the UPA. | OBSERVATION: The owner/operator failed to complete the five-year accident history that complies with all requirements in Section 2750.9. CORRECTIVE ACTION: Revise and resubmit a copy of the five-year accident history to the CUPA and ensure that it complies with all requirements in Section 2750.9. | [5 empty] | Yes | No | No | No
CalARP Program | Administration/Documentation | 5010037 |  |  | Hazard Assessment: Program Level 2, 3, or 4 | Failure to comply with any of the following: 1. Offsite Consequence Analysis Parameters. (19 CCR 4.5 2750.2) 2. Worst-Case Release Scenario Analysis. (19 CCR 4.5 2750.3) 3. Alternative Release Scenario Analysis. (19 CCR 4.5 2750.4) 4. Defining Offsite Impacts to the Population. (19 CCR 4.5 2750.5) 5. Defining Offsite Impacts to the Environment. (19 CCR 4.5 2750.6) 6. Offsite Consequence Analysis Review and Update. (19 CCR 4.5 2750.7) 7. Offsite Consequence Analysis Documentation. (19 CCR 4.5 2750.8) 8. Five-year Accident History. (19 CCR 4.5 2750.9) | 19 CCR 4.5 2750.1 | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 38 | Hazard Assessment | General Applicability | Conducted a hazard assessment meeting the requirements of 2750.2-2750.9 | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to comply with any of the following: 1. Offsite Consequence Analysis Parameters. (19 CCR 4.5 2750.2) 2. Worst-Case Release Scenario Analysis. (19 CCR 4.5 2750.3) 3. Alternative Release Scenario Analysis. (19 CCR 4.5 2750.4) 4. Defining Offsite Impacts to the Population. (19 CCR 4.5 2750.5) 5. Defining Offsite Impacts to the Environment. (19 CCR 4.5 2750.6) 6. Offsite Consequence Analysis Review and Update. (19 CCR 4.5 2750.7) 7. Offsite Consequence Analysis Documentation. (19 CCR 4.5 2750.8) 8. Five-year Accident History. (19 CCR 4.5 2750.9) |  |  | OBSERVATION: The owner/operator failed to conduct a hazard assessment that complies with Sections 2750.2 through 2750.9. CORRECTIVE ACTION: Conduct a hazard assessment that complies with Sections 2750.2 through 2750.9 and submit a copy to the UPA. | OBSERVATION: The owner/operator failed to conduct a hazard assessment that complies with all requirements in Sections 2750.2 through 2750.9. CORRECTIVE ACTION: Revise and resubmit a copy of the hazard assessment to the CUPA and ensure that it complies with all requirements in Sections 2750.2 through 2750.9. | [5 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010119 |  |  | Record Keeping | Failure to maintain records supporting the implementation of 19 CCR 4.5 for five years unless otherwise provided in Article 6. | 19 CCR 4.5 2775.1 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 39 | Other Requirements | Recordkeeping | Maintained records supporting the implementation of CalARP for five years unless otherwise provided | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain records supporting the implementation of 19 CCR 4.5 for five years unless otherwise provided in Article 6. |  |  | OBSERVATION: The owner/operator failed to maintain records supporting the implementation of 19 CCR 4.5 for five years unless otherwise provided in Article 6 of that chapter. CORRECTIVE ACTION: Submit a copy of the missing records to the CUPA. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010120 |  |  | Technical Assistance - Coordination | Failure to closely coordinate with the UPA to ensure that appropriate technical standards are applied to the implementation of 19 CCR 4.5. | 19 CCR 4.5 2785.1 (a) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 40 | Other Requirements | Recordkeeping | Coordinated with UPA to ensure appropriate technical standards are applied to implement CalARP | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to closely coordinate with the UPA to ensure that appropriate technical standards are applied to the implementation of 19 CCR 4.5. |  |  | OBSERVATION: The owner/operator failed to closely coordinate with the UPA to ensure that appropriate technical standards are applied to the implementation of 19 CCR 4.5. CORRECTIVE ACTION: Coordinate with the UPA to ensure that appropriate technical standards are applied to the implementation of 19 CCR 4.5. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010121 |  |  | Technical Assistance - Request Assistance | Failure to request assistance from the UPA when necessary to address compliance with 19 CCR 4.5 or safety issues regarding unfamiliar processes. | 19 CCR 4.5 2785.1 (b) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 41 | Other Requirements | Recordkeeping | Requested assistance from the UPA when necessary to address compliance/safety issues with CalARP | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to request assistance from the UPA when necessary to address compliance with 19 CCR 4.5 or safety issues regarding unfamiliar processes. |  |  | OBSERVATION: The owner/operator failed to request assistance from the UPA when necessary to address compliance with 19 CCR 4.5 or safety issues regarding unfamiliar processes. CORRECTIVE ACTION: Coordinate with the UPA to address compliance with 19 CCR 4.5 or safety issues regarding unfamiliar processes. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010115 |  |  | Emergency Response Applicability (Non Responding): Program Level 2 or 3 | Failure of owner or operator of a stationary source whose employees will not respond to accidental releases of regulated substances to meet the following: 1. For stationary sources with any regulated toxic substances held in a process above the threshold quantity, the stationary source is included in the community emergency response plan developed under Section 11003 of Title 42 of the United States Code (USC), is included in the city or county Hazardous Materials Area plans, and/or is included in the business plan program, pursuant to Section 25507 of the Health & Safety Code. The owner or operator must document that response actions have been coordinated with the local fire department and hazardous materials response agencies; 2. For stationary sources with only regulated flammable substances held in a process above the threshold quantity, the owner or operator must document that response actions have been coordinated with the local fire department and hazardous materials response agencies; and, 3. Appropriate mechanisms and written procedures are in place to notify emergency responders when there is a need for a response. | 19 CCR 4.5 2765.1(b) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 42 | Emergency Response Program | Emergency Response Applicability | Stationary source whose employees will not respond to releases met all applicable requirements | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of owner or operator of a stationary source whose employees will not respond to accidental releases of regulated substances to meet the following: 1. For stationary sources with any regulated toxic substances held in a process above the threshold quantity, the stationary source is included in the community emergency response plan developed under Section 11003 of Title 42 of the United States Code (USC), is included in the city or county Hazardous Materials Area plans, and/or is included in the business plan program, pursuant to Section 25507 of the Health & Safety Code. The owner or operator must document that response actions have been coordinated with the local fire department and hazardous materials response agencies; 2. For stationary sources with only regulated flammable substances held in a process above the threshold quantity, the owner or operator must document that response actions have been coordinated with the local fire department and hazardous materials response agencies; and, 3. Appropriate mechanisms and written procedures are in place to notify emergency responders when there is a need for a response. |  |  | OBSERVATION: The owner/operator of a facility that does not respond to accidental releases of regulated substances failed to meet the following: If only regulated toxic substances, is included in the community emergency response plan, is included in the city or county Hazardous Materials Area plans, and/or is included in the business plan program, and/or the owner/operator failed to document that response actions have been coordinated with the local fire department and hazardous materials response agencies; If only regulated flammable substances, the owner or operator failed to document that response actions have been coordinated with the local fire department and hazardous materials response agencies; and/or appropriate mechanisms and written procedures are not in place to notify emergency responders when there is a need for a response. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has met the requirements noted above. | [6 empty] | No | Yes | Yes | No
CalARP Program | Administration/Documentation | 5010116 |  |  | Emergency Response Program (Responding): Program Level 2, 3, or 4 | Failure to develop, implement, and maintain at the stationary source an emergency response program that includes the following elements: 1. Procedures for informing and interfacing with the public and local emergency response agencies about accidental releases, emergency planning, and emergency response. 2. Documentation of proper first-aid and emergency medical treatment necessary to treat accidental human exposures. 3. Procedures and measures for emergency response after an accidental release of a regulated substance. 4. Procedures for the use of emergency response equipment and for its inspection, testing, and maintenance are developed by the stationary source. 5. Training for all employees in relevant procedures and relevant aspects of the Incident Command System. 6. Procedures to review and update the emergency response plan to reflect changes at the stationary source are developed and employees are informed of these changes. | 19 CCR 4.5 2765.2(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 43 | Emergency Response Program | Emergency Response Program - Responding | Responding facility developed and implemented an emergency response program | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to develop, implement, and maintain at the stationary source an emergency response program that includes the following elements: 1. Procedures for informing and interfacing with the public and local emergency response agencies about accidental releases, emergency planning, and emergency response. 2. Documentation of proper first-aid and emergency medical treatment necessary to treat accidental human exposures. 3. Procedures and measures for emergency response after an accidental release of a regulated substance. 4. Procedures for the use of emergency response equipment and for its inspection, testing, and maintenance are developed by the stationary source. 5. Training for all employees in relevant procedures and relevant aspects of the Incident Command System. 6. Procedures to review and update the emergency response plan to reflect changes at the stationary source are developed and employees are informed of these changes. |  |  | OBSERVATION: The owner/operator failed to develop, implement, and maintain an emergency response (ER) program that addresses the following: procedures for informing and interfacing with the public and local ER agencies about releases, emergency planning, and emergency response; documentation of proper first-aid and emergency medical treatment needed to treat human exposures; procedures and measures for ER after a release of a regulated substance; procedures for the use of ER equipment and for its inspection, testing, and maintenance; training for all employees in procedures and aspects of the Incident Command System relevant to their responsibilities; procedures to review and update the emergency response plan to reflect changes at the stationary source, and how employees are to be informed of these changes. CORRECTIVE ACTION: Develop and submit an emergency response program to the CUPA that addresses all of the requirements noted above. | [6 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010117 |  |  | Emergency Response Program - (Responding): Coordination with the Community ERP - Program Level 2, 3, or 4 | Failure to coordinate the emergency response plan with the community emergency response plan developed under Section 11003 of Title 42 of the United States Code. | 19 CCR 4.5 2765.2(c) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 44 | Emergency Response Program | Emergency Response Program - Responding | Coordinated the ERP with the community ERP | 42 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to coordinate the emergency response plan with the community emergency response plan developed under Section 11003 of Title 42 of the United States Code. |  |  | OBSERVATION: The owner/operator failed to coordinate the emergency response plan with the community emergency response plan developed under Section 11003 of Title 42 of the United States Code. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator coordinated the emergency response plan with the community emergency response plan developed under Section 11003 of Title 42 of the United States Code. | [6 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010118 |  |  | Emergency Response Program (Responding): Provide requested info to LEPC or ER officials - Program Level 2, 3, or 4 | Failure to promptly provide to the local emergency planning committee or emergency response officials information necessary for developing and implementing the community emergency response plan upon request. | 19 CCR 4.5 2765.2(c) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 45 | Emergency Response Program | Emergency Response Program - Responding | Provided LEPC or ER officials information for developing and implementing the community ERP | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to promptly provide to the local emergency planning committee or emergency response officials information necessary for developing and implementing the community emergency response plan upon request. |  |  | OBSERVATION: The owner/operator failed to promptly provide to the local emergency planning committee or emergency response officials information necessary for developing and implementing the community emergency response plan upon request. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has provided to the local emergency planning committee or emergency response officials information necessary for developing and implementing the community emergency response plan upon request. | [6 empty] | No | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010038 |  |  | Program Level 2: Safety Information - General | Failure to compile and maintain the following up-to-date safety information related to the regulated substances, processes, and equipment: 1. Material Safety Data Sheets that meet the requirements of Section 5189 of Title 8 of CCR; 2. Maximum intended inventory of equipment in which the regulated substances are stored or processed; 3. Safe upper and lower temperatures, pressures, flows and compositions; 4. Equipment specifications; 5. Codes and standards used to design, build & operate the process. | 19 CCR 4.5 2755.1(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 46 | Program 2 Prevention Program | Safety Information | Compiled and maintained up-to-date safety information related to the RS, processes, and equipment | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to compile and maintain the following up-to-date safety information related to the regulated substances, processes, and equipment: 1. Material Safety Data Sheets that meet the requirements of Section 5189 of Title 8 of CCR; 2. Maximum intended inventory of equipment in which the regulated substances are stored or processed; 3. Safe upper and lower temperatures, pressures, flows and compositions; 4. Equipment specifications; 5. Codes and standards used to design, build & operate the process. |  |  | OBSERVATION: The owner/operator failed to compile and maintain the following up-to-date safety information related to the regulated substances, processes, and equipment: Material Safety Data Sheets related to the regulated substance(s); maximum intended inventory of equipment in which the regulated substances are stored or processed; safe upper and lower temperatures, pressures, flows and compositions; equipment specifications; Codes and standards used to design, build & operate the process. CORRECTIVE ACTION: Submit a copy of the following up-to-date safety information related to the regulated substances, processes, and equipment to the CUPA: Material Safety Data Sheets related to the regulated substance(s); maximum intended inventory of equipment in which the regulated substances are stored or processed; safe upper and lower temperatures, pressures, flows and compositions; equipment specifications; Codes and standards used to design, build & operate the process. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010039 |  |  | Program Level 2: Safety Information - Process Design | Failure to ensure that the process is designed in compliance with recognized and generally accepted good engineering practices. | 19 CCR 4.5 2755.1(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 47 | Program 2 Prevention Program | Safety Information | Ensured the process is designed in compliance with recognized and accepted engineering practices | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that the process is designed in compliance with recognized and generally accepted good engineering practices. |  |  | OBSERVATION: The owner/operator failed to ensure that the process is designed in compliance with recognized and generally accepted good engineering practices. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating you have ensured that the process is designed in compliance with recognized and generally accepted good engineering practices. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010040 |  |  | Program Level 2: Safety Information - Update | Failure to update the safety information if a major change occurs that makes the information inaccurate. | 19 CCR 4.5 2755.1(c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 48 | Program 2 Prevention Program | Safety Information | Updated the safety information when a major change occurs that makes the information inaccurate | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to update the safety information if a major change occurs that makes the information inaccurate. |  |  | OBSERVATION: The owner/operator failed to update the safety information when a major change occurred that made the information inaccurate. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating you have updated the safety information. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010041 |  |  | Program Level 2: Hazard Review - General | Failure to conduct a review of the hazards associated with the regulated substances, process, and procedures that identifies the following: 1. The hazards associated with the process and regulated substances; 2. Opportunities for equipment malfunctions or human errors that could cause an accidental release; 3. The safeguards used or needed to control the hazards or prevent equipment malfunction or human error; 4. Any steps used or needed to detect or monitor releases. | 19 CCR 4.5 2755.2(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 49 | Program 2 Prevention Program | Hazard Review | Conducted a review of the hazards associated with the RS, process, and procedures | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to conduct a review of the hazards associated with the regulated substances, process, and procedures that identifies the following: 1. The hazards associated with the process and regulated substances; 2. Opportunities for equipment malfunctions or human errors that could cause an accidental release; 3. The safeguards used or needed to control the hazards or prevent equipment malfunction or human error; 4. Any steps used or needed to detect or monitor releases. |  |  | OBSERVATION: The owner/operator failed to conduct a review of the hazards associated with the regulated substance(s), process(es), and procedures that identifies: the hazards associated with the process and regulated substances; opportunities for equipment malfunctions or human errors that could cause an accidental release; the safeguards used or needed to control the hazards or prevent equipment malfunction or human error; any steps used or needed to detect or monitor releases. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator conducted a review of the hazards associated with the regulated substance(s), process(es), and procedures that addresses all the requirements noted above. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010042 |  |  | Program Level 2: Hazard Review - Consultation | Failure to consult with the UPA to decide which hazard review methodology is best suited to determine and evaluate the hazards of the process being analyzed. | 19 CCR 4.5 2755.2(b) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 50 | Program 2 Prevention Program | Hazard Review | Consulted with the UPA to decide which hazard review methodology is best suited for the process | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to consult with the UPA to decide which hazard review methodology is best suited to determine and evaluate the hazards of the process being analyzed. |  |  | OBSERVATION: The owner/operator failed to consult with the UPA to decide which hazard review methodology is best suited to determine and evaluate the hazards of the process being analyzed. CORRECTIVE ACTION: Consult with the UPA to decide which hazard review methodology is best suited to determine and evaluate the hazards of the process being analyzed. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010123 |  |  | Program Level 2: Hazard Review - Team | Failure to perform the hazard review by a team familiar with process operations, including at least one employee who has experience and knowledge specific to the process being reviewed. | 19 CCR 4.5 2755.2(c) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 51 | Program 2 Prevention Program | Hazard Review | HR performed by team familiar with process and person with experience/knowledge specific to process | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to perform the hazard review by a team familiar with process operations, including at least one employee who has experience and knowledge specific to the process being reviewed. |  |  | OBSERVATION: The owner/operator failed to perform the hazard review with a team familiar with process operations, including at least one employee who has experience and knowledge specific to the process being reviewed. CORRECTIVE ACTION: Perform a hazard review with a team familiar with process operations and include at least one employee who has experience and knowledge specific to the process being reviewed. Submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010043 |  |  | Program Level 2: Hazard Review - Design, Fabrication, Operation | Failure to determine whether the process is designed, fabricated, and operated in accordance with applicable standards or rules. | 19 CCR 4.5 2755.2(c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 52 | Program 2 Prevention Program | Hazard Review | Determined the process is designed, fabricated, and operated in accordance with applicable standards | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to determine whether the process is designed, fabricated, and operated in accordance with applicable standards or rules. |  |  | OBSERVATION: The owner/operator failed to determine whether the process(es) /is/are/ designed, fabricated, and operated in accordance with applicable standards or rules. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating you have determined whether the process(es) /is/are/ designed, fabricated, and operated in accordance with applicable standards or rules. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010044 |  |  | Program Level 2: Hazard Review - External Events | Failure to include the consideration of external events, including seismic events. | 19 CCR 4.5 2755.2(d) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 53 | Program 2 Prevention Program | Hazard Review | Included the consideration of external events, including seismic events in the hazard review | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to include the consideration of external events, including seismic events. |  |  | OBSERVATION: The owner/operator failed to include the consideration of external events, including seismic events in the hazard review. CORRECTIVE ACTION: Submit a copy of the hazard review to the CUPA that includes the consideration of external events, including seismic events. | OBSERVATION: The owner/operator failed to include the consideration of seismic events in the hazard review. CORRECTIVE ACTION: Submit a copy of the hazard review to the CUPA that includes the consideration of seismic events. | [5 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010045 |  |  | Program Level 2: Hazard Review - Recommendations/Resolutions | Failure to address the following in the hazard review: 1. Document the results of the hazard review and ensure problems identified are resolved; 2. Complete these actions on a timetable agreed upon with the UPA, or within two and one-half (2.5) years of performing the hazard review, or the next planned turnaround, for those items that require a turnaround; 3. Document the final resolution taken to address each recommendation and actual completion date. | 19 CCR 4.5 2755.2(e) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 54 | Program 2 Prevention Program | Hazard Review | Hazard review results and resolutions documented, and completed within required time frame | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to address the following in the hazard review: 1. Document the results of the hazard review and ensure problems identified are resolved; 2. Complete these actions on a timetable agreed upon with the UPA, or within two and one-half (2.5) years of performing the hazard review, or the next planned turnaround, for those items that require a turnaround; 3. Document the final resolution taken to address each recommendation and actual completion date. |  |  | OBSERVATION: The owner/operator failed to document the results of the hazard review, document final resolutions taken, or complete these actions within required time frame. CORRECTIVE ACTION: Submit a copy of the results of the hazard review to the UPA, including documentation demonstrating that problems identified are being resolved. | OBSERVATION: The owner/operator failed to ensure that problems identified in the hazard review were resolved. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that problems identified in the hazard review are being resolved. | OBSERVATION: The owner/operator failed to document the resolution(s) taken to address the hazard review recommendations). CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the resolutions taken to address the hazard review recommendations have been documented. |  |  |  |  | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010046 |  |  | Program Level 2: Hazard Review - 5 Year Update | Failure to update and revalidate the hazard review at least once every 5 years. | 19 CCR 4.5 2755.2(f) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 55 | Program 2 Prevention Program | Hazard Review | Updated and revalidated the hazard review at least once every 5 years | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to update and revalidate the hazard review at least once every 5 years. |  |  | OBSERVATION: The owner/operator failed to update and revalidate the hazard review at least once every 5 years. CORRECTIVE ACTION: Update and revalidate the hazard review and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010047 |  |  | Program Level 2: Hazard Review - Major Change | Failure to update and revalidate the hazard review whenever a major change in the process occurs. | 19 CCR 4.5 2755.2(f) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 56 | Program 2 Prevention Program | Hazard Review | Updated and revalidated the hazard review whenever a major change in the process occurs | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to update and revalidate the hazard review whenever a major change in the process occurs. |  |  | OBSERVATION: The owner/operator failed to update and revalidate the hazard review resulting from a major change in the process. CORRECTIVE ACTION: Update the hazard review and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010048 |  |  | Program Level 2: Hazard Review - Prestart up | Failure to resolve all issues identified in the hazard review before startup of the changed process. | 19 CCR 4.5 2755.2(f) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 57 | Program 2 Prevention Program | Hazard Review | Resolved all issues identified in the hazard review before startup of the changed process | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to resolve all issues identified in the hazard review before startup of the changed process. |  |  | OBSERVATION: The owner/operator failed to resolve all issues identified in the hazard review before startup of the changed process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that all issues identified in the hazard review have been resolved. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010124 |  |  | Program Level 2: Hazard Review - Revalidation | Failure to revalidate the hazard review only once between full hazard reviews, unless the UPA agrees in writing that a full hazard review is unwarranted. | 19 CCR 4.5 2755.2(g) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 58 | Program 2 Prevention Program | Hazard Review | Hazard review only revalidated once between full hazard reviews unless UPA agrees in writing | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to revalidate the hazard review only once between full hazard reviews, unless the UPA agrees in writing that a full hazard review is unwarranted. |  |  | OBSERVATION: The owner/operator revalidated the hazard review more than once between hazard reviews. CORRECTIVE ACTION: Perform a full hazard review and submit a copy to the UPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/ Documentation | 5010125 |  |  | Program Level 2: Hazard Review - Retention | Failure to retain hazard reviews and updates or revalidations for each process covered by 19 CCR 4.5 section 2755.2, as well as the documented resolution of recommendations described in 19 CCR 4.5 section 2755.2(e) for the life of the process. | 19 CCR 4.5 2755.2(h) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 59 | Program 2 Prevention Program | Hazard Review | Retained all HR's, updates/revalidations, and documented resolution of recommendations | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to retain hazard reviews and updates or revalidations for each process covered by 19 CCR 4.5 section 2755.2, as well as the documented resolution of recommendations described in 19 CCR 4.5 section 2755.2(e) for the life of the process. |  |  | OBSERVATION: The owner/operator failed to retain hazard reviews and updates/revalidations for each process and documented resolution of recommendations for the life of the process. CORRECTIVE ACTION: Submit any missing hazard reviews and updates/revalidations and documented resolutions to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010049 |  |  | Program Level 2: Operating Procedures - General | Failure to prepare written operating procedures that provide clear instructions or steps for safely conducting activities associated with each covered process consistent with the safety information for that process and address the following: 1. Initial startup; 2. Normal operations; 3. Temporary operations; 4. Emergency shutdown and operations; 5. Normal shutdown; 6. Startup following a normal or emergency shutdown or a major change that requires a hazard review; 7. Consequences of deviations and steps required to correct or avoid deviations; 8. Equipment inspections. | 19 CCR 4.5 2755.3(a), 2755.3(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 60 | Program 2 Prevention Program | Operating Procedures | Prepared written operating procedures that provide clear instructions for each covered process | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to prepare written operating procedures that provide clear instructions or steps for safely conducting activities associated with each covered process consistent with the safety information for that process and address the following: 1. Initial startup; 2. Normal operations; 3. Temporary operations; 4. Emergency shutdown and operations; 5. Normal shutdown; 6. Startup following a normal or emergency shutdown or a major change that requires a hazard review; 7. Consequences of deviations and steps required to correct or avoid deviations; 8. Equipment inspections. |  |  | OBSERVATION: The owner/operator failed to prepare written operating procedures that provide clear instructions or steps for safely conducting activities associated with each covered process consistent with the safety information for that process and address the following: initial startup; normal operations; temporary operations; emergency shutdown and operations; normal shutdown; startup following a normal or emergency shutdown or a major change that requires a hazard review; consequences of deviations and steps required to correct or avoid deviations; equipment inspections. CORRECTIVE ACTION: Submit written operating procedures to the CUPA that address all of the requirements noted above. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010050 |  |  | Program Level 2: Operating Procedures - Update | Failure to ensure that the operating procedures are developed and/or updated, as necessary to reflect current practice, or whenever the tasks or steps to perform on the covered process are found to be inadequate or inaccurate. | 19 CCR 4.5 2755.3(c) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 61 | Program 2 Prevention Program | Operating Procedures | Ensured that operating procedures are developed/updated as necessary | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to ensure that the operating procedures are developed and/or updated, as necessary to reflect current practice, or whenever the tasks or steps to perform on the covered process are found to be inadequate or inaccurate. |  |  | OBSERVATION: The owner/operator failed to ensure that the operating procedures are developed and/or updated as necessary to reflect current practice, or whenever the tasks or steps to perform on the covered process are found to be inadequate or inaccurate. CORRECTIVE ACTION: Develop/Update the operating procedures to reflect current practice and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020001 |  |  | Program Level 2: Training - General | Failure to ensure that each employee presently operating a process, and each employee newly assigned to a covered process has been trained or tested competent in the operating procedures provided in Section 2755.3 that pertain to their duties. | 19 CCR 4.5 2755.4(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 62 | Program 2 Prevention Program | Training | Employees operating a process have been trained or tested competent in the operating procedures | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to ensure that each employee presently operating a process, and each employee newly assigned to a covered process has been trained or tested competent in the operating procedures provided in Section 2755.3 that pertain to their duties. |  |  | OBSERVATION: The owner/operator failed to ensure that each employee presently operating a process, and each employee newly assigned to a covered process has been trained or tested competent in the operating procedures provided in Section 2755.3 that pertain to their duties. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that each employee presently operating a process, and each employee newly assigned to a covered process has been trained or tested competent in the operating procedures that pertain to their duties. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020002 |  |  | Program Level 2: Training - Refresher | Failure to provide refresher training at least every three years, and more often if necessary, to each employee operating a process to ensure that the employee understands and adheres to the current operating procedures of the process. | 19 CCR 4.5 2755.4(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 63 | Program 2 Prevention Program | Training | Employees operating a process provided refresher training on operating procedures every three years | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to provide refresher training at least every three years, and more often if necessary, to each employee operating a process to ensure that the employee understands and adheres to the current operating procedures of the process. |  |  | OBSERVATION: The owner/operator failed to provide refresher training at least every three years, and more often if necessary, to each employee operating a process to ensure that the employee understands and adheres to the current operating procedures of the process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that each employee operating a process has received refresher training. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020003 |  |  | Program Level 2: Training - Prestart up | Failure to ensure operators are trained in any updated or new procedures prior to needing to use the procedures. | 19 CCR 4.5 2755.4(d) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 64 | Program 2 Prevention Program | Training | Operators trained in updated or new procedures prior to using the procedures | 76 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to ensure operators are trained in any updated or new procedures prior to needing to use the procedures. |  |  | OBSERVATION: The owner/operator failed to ensure operators are trained in updated or new procedures prior to needing to use the procedures. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the operators are trained in any updated or new procedures. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020011 |  |  | Program Level 2: Training - Documentation | Failure to document initial and refresher training for each employee. | 19 CCR 4.5 2755.4(e) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 65 | Program 2 Prevention Program | Training | Initial and refresher training documented | 41 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to document initial and refresher training for each employee. |  |  | OBSERVATION: The owner/operator failed to document initial and refresher training for each employee. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating initial and refresher training for each employees has been conducted. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010051 |  |  | Program Level 2: Maintenance - Procedures | Failure to prepare and implement written procedures to maintain the on-going mechanical integrity of the process equipment. | 19 CCR 4.5 2755.5(a) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 66 | Program 2 Prevention Program | Maintenance | Prepared/Implemented written procedures to maintain the mechanical integrity of process equipment | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to prepare and implement written procedures to maintain the on-going mechanical integrity of the process equipment. |  |  | OBSERVATION: The owner/operator failed to prepare and implement written procedures to maintain the on-going mechanical integrity of the process equipment. CORRECTIVE ACTION: Prepare and implement written procedures to maintain the on-going mechanical integrity of the process equipment and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020004 |  |  | Program Level 2: Maintenance - Training | Failure to train or cause to be trained each employee involved in maintaining the on-going mechanical integrity of the process in: 1. The hazards of the process; 2. How to avoid or correct unsafe conditions; 3. The procedures applicable to the employee’s job tasks. | 19 CCR 4.5 2755.5(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 67 | Program 2 Prevention Program | Maintenance | Employees conducting maintenance are trained on hazards, avoiding unsafe conditions, and procedures | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to train or cause to be trained each employee involved in maintaining the on-going mechanical integrity of the process in: 1. The hazards of the process; 2. How to avoid or correct unsafe conditions; 3. The procedures applicable to the employee’s job tasks. |  |  | OBSERVATION: The owner/operator failed to train or cause to be trained each employee involved in maintaining the on-going mechanical integrity of the process in: the hazards of the process; how to avoid or correct unsafe conditions; the procedures applicable to the employee’s job tasks. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating each employee involved in maintaining the on-going mechanical integrity of the process is trained in: the hazards of the process; how to avoid or correct unsafe conditions; the procedures applicable to the employee’s job tasks. | [6 empty] | No | Yes | No | No
CalARP Program | Training | 5020005 |  |  | Program Level 2: Maintenance - Contractor Training | Failure to ensure that each contractor can document that their employees are trained to perform the maintenance and appropriate operation procedures developed under section 2755.5(a). | 19 CCR 4.5 2755.5(c) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 68 | Program 2 Prevention Program | Maintenance | Documented that contract employees are trained to perform the maintenance procedures | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to ensure that each contractor can document that their employees are trained to perform the maintenance and appropriate operation procedures developed under section 2755.5(a). |  |  | OBSERVATION: The owner/operator failed to ensure that each contractor can document that their employees are trained to perform the maintenance and appropriate operating procedures developed under section 2755.5(a). CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that each contract maintenance employee is trained to perform applicable maintenance and appropriate operating procedures. | [6 empty] | No | Yes | No | No
CalARP Program | Operations/Maintenance | 5030001 |  |  | Program Level 2: Maintenance - Inspections and Tests | Failure to perform or cause to be performed inspections and tests on process equipment that: 1. Follow recognized and generally accepted good engineering practices; 2. The frequency of inspections & tests must be consistent with applicable manufacturer’s recommendations, industry standards or codes, good engineering practices and prior operating experience. | 19 CCR 4.5 2755.5(d) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 69 | Program 2 Prevention Program | Maintenance | Maintenance inspections and tests performed per RAGAGEP, and at proper frequency | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform or cause to be performed inspections and tests on process equipment that: 1. Follow recognized and generally accepted good engineering practices; 2. The frequency of inspections & tests must be consistent with applicable manufacturer’s recommendations, industry standards or codes, good engineering practices and prior operating experience. |  |  | OBSERVATION: The owner/operator failed to perform or cause to be performed inspections and tests on process equipment that: follow recognized and generally accepted good engineering practices; the frequency of inspections & tests must be consistent with applicable manufacturer’s recommendations, industry standards or codes, good engineering practices and prior operating experience. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the owner/operator performed inspections and tests on process equipment that: follow recognized and generally accepted good engineering practices; the frequency of inspections & tests must be consistent with applicable manufacturer’s recommendations, industry standards or codes, good engineering practices and prior operating experience. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/ Documentation | 5010052 |  |  | Program Level 2: Compliance Audits - Triennial Certification | Failure to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 5 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. | 19 CCR 4.5 2755.6(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 70 | Program 2 Prevention Program | Compliance Audits | Certified the evaluation of compliance with Program Level 2 provisions at least every three years | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 5 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. |  |  | OBSERVATION: The owner/operator failed to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 5 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. CORRECTIVE ACTION: Submit a certification to the CUPA that the owner/operator has evaluated compliance with the provisions of 19 CCR 4.5 Article 5 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010053 |  |  | Program Level 2: Compliance Audits - Knowledgeable Person | Failure to conduct the compliance audit by at least one person knowledgeable in the process. | 19 CCR 4.5 2755.6(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 71 | Program 2 Prevention Program | Compliance Audits | Conducted the compliance audit by at least one person knowledgeable in the process | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to conduct the compliance audit by at least one person knowledgeable in the process. |  |  | OBSERVATION: The owner/operator failed to conduct the compliance audit with at least one person knowledgeable in the process. CORRECTIVE ACTION: Conduct the compliance audit with at least one person knowledgeable in the process. Develop a report of the compliance audit findings, including appropriate responses to each of the findings and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010054 |  |  | Program Level 2: Compliance Audits - Report of Audit Findings | Failure to develop a report of the audit findings. | 19 CCR 4.5 2755.6(c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 72 | Program 2 Prevention Program | Compliance Audits | Developed a report of the audit findings | 40 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to develop a report of the audit findings. |  |  | OBSERVATION: The owner/operator failed to develop a report of the compliance audit findings. CORRECTIVE ACTION: Develop a report of the compliance audit findings, including appropriate responses to each of the findings and submit a copy to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010055 |  |  | Program Level 2: Compliance Audits - Findings/Resolutions | Failure to: 1. Promptly determine and document an appropriate response to each of the findings of the compliance audit; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings. Otherwise these responses shall be completed one and one-half (1.5) years after performing the compliance audit, or the next planned turnaround for items requiring a turnaround (these timelines shall not apply to any compliance audit completed prior to January 1, 2015); 3. Document the actual completion dates when deficiencies were corrected. | 19 CCR 4.5 2755.6(d) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 73 | Program 2 Prevention Program | Compliance Audits | Promptly determined and documented response to audit findings, including correction of deficiencies | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to: 1. Promptly determine and document an appropriate response to each of the findings of the compliance audit; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings. Otherwise these responses shall be completed one and one-half (1.5) years after performing the compliance audit, or the next planned turnaround for items requiring a turnaround (these timelines shall not apply to any compliance audit completed prior to January 1, 2015); 3. Document the actual completion dates when deficiencies were corrected. |  |  | OBSERVATION: The owner/operator failed to promptly determine and document an appropriate response to each of the findings of the compliance audit and document the completion dates when deficiencies have been corrected. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has documented an appropriate response to each of the findings of the compliance audit including completion dates for deficiencies that have been corrected. | OBSERVATION: The owner/operator failed to document actual completion dates when deficiencies identified in the compliance audit were corrected. CORRECTIVE ACTION: Submit the documented completion dates for compliance audit deficiencies that have been corrected. | [5 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010056 |  |  | Program Level 2: Compliance Audits - Report Retention | Failure to retain the two most recent compliance audit reports. | 19 CCR 4.5 2755.6(e) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 74 | Program 2 Prevention Program | Compliance Audits | Retained the two most recent compliance audit reports | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to retain the two most recent compliance audit reports. |  |  | OBSERVATION: The owner/operator failed to retain the two most recent compliance audit reports. CORRECTIVE ACTION: Submit a copy of the two most recent compliance audit reports to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010057 |  |  | Program Level 2: Incident Investigation - General | Failure to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release. | 19 CCR 4.5 2755.7(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 75 | Program 2 Prevention Program | Incident Investigation | Investigated each incident that resulted or could reasonably have resulted in a catastrophic release | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release. |  |  | OBSERVATION: The owner/operator failed to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release. CORRECTIVE ACTION: Investigate the incident and submit a copy of the investigation findings with recommendations to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010058 |  |  | Program Level 2: Incident Investigation - Prompt Initiation | Failure to initiate an incident investigation as promptly as possible, but not later than 48 hours following the incident. | 19 CCR 4.5 2755.7(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 76 | Program 2 Prevention Program | Incident Investigation | Initiated incident investigations within 48 hours of the incident | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to initiate an incident investigation as promptly as possible, but not later than 48 hours following the incident. |  |  | OBSERVATION: The owner/operator failed to initiate an incident investigations within 48 hours of the incident. CORRECTIVE ACTION: Submit a statement to the CUPA demonstrating how incident investigations will be initiated within 48 hours of the incident. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010059 |  |  | Program Level 2: Incident Investigation - Summary | Failure to prepare a summary at the conclusion of the investigation that includes at minimum: 1. Date of incident; 2. Date investigation began; 3. Description of incident; 4. Factors that contributed to the incident; 5. Recommendations resulting from the investigation | 19 CCR 4.5 2755.7(c); 2750.9(b) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 77 | Program 2 Prevention Program | Incident Investigation | Prepared a summary of the investigation at the conclusion of the investigation | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to prepare a summary at the conclusion of the investigation that includes at minimum: 1. Date of incident; 2. Date investigation began; 3. Description of incident; 4. Factors that contributed to the incident; 5. Recommendations resulting from the investigation |  |  | OBSERVATION: The owner/operator failed to prepare a summary of the investigation at the conclusion of the investigation that includes the date of incident; date investigation began; description of incident; factors that contributed to the incident; and recommendations resulting from the investigation. CORRECTIVE ACTION: Prepare and submit a copy of the investigation to the CUPA that includes the date of incident; date investigation began; description of incident; factors that contributed to the incident; and recommendations resulting from the investigation. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010060 |  |  | Program Level 2: Incident Investigation - Findings/Resolutions | Failure to: 1. Establish a system to promptly address and resolve the incident report findings and recommendations; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings and recommendations. Otherwise these resolutions shall be completed no later than one and one-half (1.5) years after completion of the incident investigation, or two (2) years after the date of the incident, whichever is the earlier of the two dates, or the next planned turnaround for those items requiring turnaround. 3. Failure to document resolutions and corrective actions with actual completion dates. | 19 CCR 4.5 2755.7(d) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 78 | Program 2 Prevention Program | Incident Investigation | Addressed and resolved the investigation findings and recommendations and documented resolutions | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to: 1. Establish a system to promptly address and resolve the incident report findings and recommendations; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings and recommendations. Otherwise these resolutions shall be completed no later than one and one-half (1.5) years after completion of the incident investigation, or two (2) years after the date of the incident, whichever is the earlier of the two dates, or the next planned turnaround for those items requiring turnaround. 3. Failure to document resolutions and corrective actions with actual completion dates. |  |  | OBSERVATION: The owner/operator failed to address, resolve, and/or document the investigation findings, recommendations, and resolutions, and/or failed to do so within required time frame. CORRECTIVE ACTION: Address and resolve the investigation findings and recommendations. Submit a copy of the documented resolutions and corrective actions with actual completion dates to the UPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010062 |  |  | Program Level 2: Incident Investigation - Review | Failure to review the findings with all affected personnel whose job tasks are affected by the findings. | 19 CCR 4.5 2755.7(e) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 79 | Program 2 Prevention Program | Incident Investigation | Reviewed the incident investigation findings with all affected personnel | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to review the findings with all affected personnel whose job tasks are affected by the findings. |  |  | OBSERVATION: The owner/operator failed to review the investigation findings with all affected personnel whose job tasks are affected by the findings. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the investigation findings have been reviewed with all affected personnel whose job tasks are affected by the findings. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010063 |  |  | Program Level 2: Incident Investigation - Summary Retention | Failure to retain investigation summaries for five years. | 19 CCR 4.5 2755.7(f) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 80 | Program 2 Prevention Program | Incident Investigation | Retained investigation summaries for five years | 47 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to retain investigation summaries for five years. |  |  | OBSERVATION: The owner/operator failed to retain investigation summaries for five years. CORRECTIVE ACTION: Submit a copy of the missing investigation summaries for the last five years to the CUPA. | [6 empty] | No | Yes | No | No
CalARP Program | Administration/Documentation | 5010064 |  |  | Program Level 3: Process Safety Information - Regulated Substance | Failure to compile and maintain up-to-date written process safety information pertaining to the hazards of the regulated substances in the process that includes the following: 1. Toxicity information; 2. Permissible exposure limits; 3. Physical data; 4. Reactivity data and chemical compatibility data during handling, use, and application at the stationary source; 5. Corrosivity data; 6. Thermal and chemical stability data; 7. Hazardous effects of inadvertent mixing of different materials that could foreseeably occur. | 19 CCR 4.5 2760.1(a), (b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 81 | Program 3 Prevention Program | Process Safety Information | Compiled and maintained up-to-date written PSI pertaining to the hazards of the RS in the process | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to compile and maintain up-to-date written process safety information pertaining to the hazards of the regulated substances in the process that includes the following: 1. Toxicity information; 2. Permissible exposure limits; 3. Physical data; 4. Reactivity data and chemical compatibility data during handling, use, and application at the stationary source; 5. Corrosivity data; 6. Thermal and chemical stability data; 7. Hazardous effects of inadvertent mixing of different materials that could foreseeably occur. |  |  | OBSERVATION: The owner/operator failed to compile and maintain up-to-date written process safety information pertaining to the hazards of the regulated substances in the process that includes: toxicity information; permissible exposure limits; physical data; reactivity data; corrosivity data; thermal and chemical stability data; hazardous effects of inadvertent mixing of different materials that could foreseeably occur. CORRECTIVE ACTION: Compile the up-to-date written process safety information pertaining to the hazards of the regulated substances in the process that includes: toxicity information; permissible exposure limits; physical data; reactivity data; corrosivity data; thermal and chemical stability data; hazardous effects of inadvertent mixing of different materials that could foreseeable occur and submit a copy to the UPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010065 |  |  | Program Level 3: Process Safety Information - Technology | Failure to compile written process safety information concerning the technology of the process that includes the following: 1. A block flow diagram or simplified process flow diagram; 2. Process chemistry; 3. Maximum intended inventory; 4. Safe upper and lower limits for such items as temperatures, pressures, flows or compositions; 5. An evaluation of the consequences of deviations. | 19 CCR 4.5 2760.1(a), (c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 82 | Program 3 Prevention Program | Process Safety Information | Compiled and maintained up-to-date written PSI concerning the technology of the process | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to compile written process safety information concerning the technology of the process that includes the following: 1. A block flow diagram or simplified process flow diagram; 2. Process chemistry; 3. Maximum intended inventory; 4. Safe upper and lower limits for such items as temperatures, pressures, flows or compositions; 5. An evaluation of the consequences of deviations. |  |  | OBSERVATION: The owner/operator failed to compile written process safety information concerning the technology of the process that includes: a block flow diagram or simplified process flow diagram; process chemistry; maximum intended inventory; safe upper and lower limits for such items as temperatures, pressures, flows or compositions; an evaluation of the consequences of deviations. CORRECTIVE ACTION: Compile written process safety information concerning the technology of the process that includes: a block flow diagram or simplified process flow diagram; process chemistry; /maximum intended inventory; safe upper and lower limits for such items as temperatures, pressures, flows or compositions; an evaluation of the consequences of deviations and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010066 |  |  | Program Level 3: Process Safety Information - Equipment | Failure to compile written process safety information pertaining to the equipment in the process that includes the following: 1. Materials of construction; 2. Piping and instrument diagrams (P&IDs); 3. Electrical classification; 4. Relief system design and design basis; 5. Ventilation system design; 6. Design codes and standards employed; 7. Material and energy balances for processes built after June 21, 1999; 8. Safety systems (e.g., interlocks, detection, or suppression systems). | 19 CCR 4.5 2760.1(a), (d)(1) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 83 | Program 3 Prevention Program | Process Safety Information | Compiled and maintained up-to-date written PSI pertaining to the equipment in the process | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to compile written process safety information pertaining to the equipment in the process that includes the following: 1. Materials of construction; 2. Piping and instrument diagrams (P&IDs); 3. Electrical classification; 4. Relief system design and design basis; 5. Ventilation system design; 6. Design codes and standards employed; 7. Material and energy balances for processes built after June 21, 1999; 8. Safety systems (e.g., interlocks, detection, or suppression systems). |  |  | OBSERVATION: The owner/operator failed to compile written process safety information pertaining to the equipment in the process that includes: materials of construction; piping and instrument diagrams (P&IDs); electrical classification; relief system design and design basis; ventilation system design; design codes and standards employed; material and energy balances for processes built after June 21, 1999; safety systems (e.g., interlocks, detection, or suppression systems). CORRECTIVE ACTION: Compile written process safety information pertaining to the equipment in the process that includes: materials of construction; piping and instrument diagrams (P&IDs); electrical classification; relief system design and design basis; ventilation system design; design codes and standards employed; material and energy balances for processes built after June 21, 1999; safety systems (e.g., interlocks, detection, or suppression systems) and submit a copy to the UPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010067 |  |  | Program Level 3: Process Safety Information - Equipment Compliance Documentation | Failure to document that equipment complies with recognized and generally accepted good engineering practices. | 19 CCR 4.5 2760.1(d)(2) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 84 | Program 3 Prevention Program | Process Safety Information | Documented that equipment complies with recognized and generally accepted good engineering practices | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to document that equipment complies with recognized and generally accepted good engineering practices. |  |  | OBSERVATION: The owner/operator failed to document that equipment complies with recognized and generally accepted good engineering practices. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that equipment complies with recognized and generally accepted good engineering practices. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010068 |  |  | Program Level 3: Process Safety Information - Existing Equipment Compliance Documentation | For existing equipment designed and constructed in accordance with codes, standards, or practices that are no longer in general use, the owner or operator has determined and documented that the equipment is designed, maintained, inspected, tested, and operating in a safe manner. | 19 CCR 4.5 2760.1(d)(3) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 85 | Program 3 Prevention Program | Process Safety Information | Documented that equipment is designed, maintained, inspected, tested, and operating in a safe manner | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | For existing equipment designed and constructed in accordance with codes, standards, or practices that are no longer in general use, the owner or operator has determined and documented that the equipment is designed, maintained, inspected, tested, and operating in a safe manner. |  |  | OBSERVATION: The owner/operator failed to determine and document that existing equipment designed and constructed in accordance with codes, standards, or practices that are no longer in general use are designed, maintained, inspected, tested, and operating in a safe manner. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that existing equipment is designed, maintained, inspected, tested, and operated in a safe manner. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010069 |  |  | Program Level 3: Process Hazard Analysis - Initial | Failure to conduct an initial Process Hazard Analysis on the covered processes no later than the date of submittal of the RMP. | 19 CCR 4.5 2760.2(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 86 | Program 3 Prevention Program | Process Hazard Analysis | Conducted an initial PHA on the covered processes no later than the date of submittal of the RMP | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to conduct an initial Process Hazard Analysis on the covered processes no later than the date of submittal of the RMP. |  |  | OBSERVATION: The owner/operator failed to conduct an initial Process Hazard Analysis on the covered processes no later than the date of submittal of the Risk Management Plan. CORRECTIVE ACTION: Conduct a Process Hazard Analysis on the covered process and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010070 |  |  | Program Level 3: Process Hazard Analysis | Failure to perform a Process Hazard Analysis that is appropriate to the complexity of the process and identifies, evaluates, and controls the hazards involved in the process. | 19 CCR 4.5 2760.2(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 87 | Program 3 Prevention Program | Process Hazard Analysis | Performed a PHA that is appropriate for the complexity of the process | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to perform a Process Hazard Analysis that is appropriate to the complexity of the process and identifies, evaluates, and controls the hazards involved in the process. |  |  | OBSERVATION: The owner/operator failed to perform a Process Hazard Analysis that is appropriate to the complexity of the process and identifies, evaluates, and controls the hazards involved in the process. CORRECTIVE ACTION: Conduct a Process Hazard Analysis on the covered process that is appropriate to the complexity of the process and identifies, evaluates, and controls the hazards involved in the process and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010072 |  |  | Program Level 3: Process Hazard Analysis - Consultation | Failure to work closely with the UPA in deciding which Process Hazard Analysis methodology is best suited to determine the hazards of the process being analyzed. | 19 CCR 4.5 2760.2(b) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 88 | Program 3 Prevention Program | Process Hazard Analysis | Worked with the UPA in deciding which PHA methodology is best to determine the process hazards | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to work closely with the UPA in deciding which Process Hazard Analysis methodology is best suited to determine the hazards of the process being analyzed. |  |  | OBSERVATION: The owner/operator failed to work closely with the UPA in deciding which Process Hazard Analysis methodology is best suited to determine the hazards of the process being analyzed. CORRECTIVE ACTION: Contact the UPA to decide which Process Hazard Analysis methodology is best suited to determine the hazards of the process being analyzed. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010073 |  |  | Program Level 3: Process Hazard Analysis - Methodology | Failure to use one or more of the following methodologies that are appropriate to determine and evaluate the hazards of the process being analyzed: 1. What-If; 2. Checklist; 3. What-If/Checklist; 4. Hazard and Operability Study (HAZOP); 5. Failure Mode and Effects Analysis (FMEA); 6. Fault Tree Analysis; or, 7. An appropriate equivalent methodology. | 19 CCR 4.5 2760.2(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 89 | Program 3 Prevention Program | Process Hazard Analysis | Used one or more methodologies in Section 2760.2(b) to determine and evaluate the process hazards | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to use one or more of the following methodologies that are appropriate to determine and evaluate the hazards of the process being analyzed: 1. What-If; 2. Checklist; 3. What-If/Checklist; 4. Hazard and Operability Study (HAZOP); 5. Failure Mode and Effects Analysis (FMEA); 6. Fault Tree Analysis; or, 7. An appropriate equivalent methodology. |  |  | OBSERVATION: The owner/operator failed to use one or more of the following methodologies that are appropriate to determine and evaluate the hazards of the process being analyzed: what-If; checklist; what-If/Checklist; hazard and Operability Study (HAZOP); failure Mode and Effects Analysis (FMEA); fault Tree Analysis; or an appropriate equivalent methodology. CORRECTIVE ACTION: Conduct a Process Hazard Analysis using one or more of the following methodologies: what-If; checklist; what-If/Checklist; hazard and Operability Study (HAZOP); failure Mode and Effects Analysis (FMEA); fault Tree Analysis; or an appropriate equivalent methodology. Submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010074 |  |  | Program Level 3: Process Hazard Analysis - General | Failure to address the following in the Process Hazard Analysis: 1. The hazards of the process; 2. The identification of any previous incident which had a likely potential for catastrophic consequences; 3. Engineering and administrative controls applicable to the hazards and their interrelationships such as appropriate application of detection methodologies to provide early warning of releases. (Acceptable detection methods might include process monitoring and control instrumentation with alarms, and detection hardware such as hydrocarbon sensors.); 4. Consequences of failure of engineering and administrative controls; 5. Stationary source siting; 6. Human factors; 7. A qualitative evaluation of a range of the possible safety and health effects of failure of controls; and, 8. External events, including seismic events. | 19 CCR 4.5 2760.2(c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 90 | Program 3 Prevention Program | Process Hazard Analysis | PHA addresses hazards, previous incidents, engineering/admin controls, siting, human factors, etc. | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to address the following in the Process Hazard Analysis: 1. The hazards of the process; 2. The identification of any previous incident which had a likely potential for catastrophic consequences; 3. Engineering and administrative controls applicable to the hazards and their interrelationships such as appropriate application of detection methodologies to provide early warning of releases. (Acceptable detection methods might include process monitoring and control instrumentation with alarms, and detection hardware such as hydrocarbon sensors.); 4. Consequences of failure of engineering and administrative controls; 5. Stationary source siting; 6. Human factors; 7. A qualitative evaluation of a range of the possible safety and health effects of failure of controls; and, 8. External events, including seismic events. |  |  | OBSERVATION: The owner/operator failed to address the following in the Process Hazard Analysis: the hazards of the process; the identification of any previous incident which had a likely potential for catastrophic consequences; engineering and administrative controls applicable to the hazards and their interrelationships such as appropriate application of detection methodologies to provide early warning of releases; consequences of failure of engineering and administrative controls; stationary source siting; human factors; a qualitative evaluation of a range of the possible safety and health effects of failure of controls; and external events, including seismic events. CORRECTIVE ACTION: Conduct a Process Hazard Analysis that addresses the requirements noted above and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010075 |  |  | Program Level 3: Process Hazard Analysis - Team Qualifications | Failure to perform the Process Hazard Analysis by a team with expertise in engineering and process operations, including at least one employee who has experience and knowledge specific to the process being evaluated, and one member who is knowledgeable in the specific Process Hazard Analysis methodology being used. | 19 CCR 4.5 2760.2(d) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 91 | Program 3 Prevention Program | Process Hazard Analysis | PHA performed by team with expertise, experience, and knowledge in the process and PHA methodology | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to perform the Process Hazard Analysis by a team with expertise in engineering and process operations, including at least one employee who has experience and knowledge specific to the process being evaluated, and one member who is knowledgeable in the specific Process Hazard Analysis methodology being used. |  |  | OBSERVATION: The owner/operator failed to perform the Process Hazard Analysis using a team with expertise in engineering and process operations, including at least one employee who has experience and knowledge specific to the process being evaluated, and one member who is knowledgeable in the specific Process Hazard Analysis methodology being used. CORRECTIVE ACTION: Conduct a Process Hazard Analysis using a team with expertise in engineering and process operations, including at least one employee who has experience and knowledge specific to the process being evaluated, and one member who is knowledgeable in the specific Process Hazard Analysis methodology being used and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010076 |  |  | Program Level 3: Process Hazard Analysis - Recommendations/Resolutions | Failure to address the following in the Process Hazard Analysis: 1. Establish a system to address the teams findings and recommendations; 2. Assure that the recommendations are resolved and documented; 3. Document what actions are to be taken; 4. Develop a written schedule of when these actions are to be completed; 5. Complete these actions on a timetable agreed upon with the UPA, or within two and one-half (2.5) years of performing the PHA, or the next planned turnaround, for those items that require a turnaround; 6. Document the final resolution taken to address each recommendation and actual completion date; and 7. Communicate the actions to operating, maintenance and other employees whose work assignments are in the process and who may be affected by the recommendations or actions. | 19 CCR 4.5 2760.2(e) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 92 | Program 3 Prevention Program | Process Hazard Analysis | PHA properly addresses all findings and recommendations and resolutions are completed and documented | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to address the following in the Process Hazard Analysis: 1. Establish a system to address the teams findings and recommendations; 2. Assure that the recommendations are resolved and documented; 3. Document what actions are to be taken; 4. Develop a written schedule of when these actions are to be completed; 5. Complete these actions on a timetable agreed upon with the UPA, or within two and one-half (2.5) years of performing the PHA, or the next planned turnaround, for those items that require a turnaround; 6. Document the final resolution taken to address each recommendation and actual completion date; and 7. Communicate the actions to operating, maintenance and other employees whose work assignments are in the process and who may be affected by the recommendations or actions. |  |  | OBSERVATION: The owner/operator failed to address the following in the Process Hazard Analysis: establish a system to promptly address the team's findings and recommendations; assure that the recommendations are resolved and documented; document what actions are to be taken; develop a written schedule of when these actions are to be completed; complete these actions on a timetable agreed upon with the UPA, or within two and one-half (2.5) years of performing the PHA, or the next planned turnaround, for those items that require a turnaround; document the final resolution taken to address each recommendation and actual completion date; communicate the actions to operating, maintenance and other employees whose work assignments are in the process and who may be affected by the recommendations or actions. CORRECTIVE ACTION: Complete and submit a Process Hazard Analysis to the UPA that addresses the requirements noted above. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010077 |  |  | Program Level 3: Process Hazard Analysis - Update/Revalidation | Failure to update and revalidate the Process Hazard Analysis at least every five years after the completion of the initial Process Hazard Analysis. | 19 CCR 4.5 2760.2(f) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 93 | Program 3 Prevention Program | Process Hazard Analysis | Updated and revalidated the PHA every five years after the completion of the initial PHA | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to update and revalidate the Process Hazard Analysis at least every five years after the completion of the initial Process Hazard Analysis. |  |  | OBSERVATION: The owner/operator failed to update and revalidate the Process Hazard Analysis at least every five years after the completion of the initial Process Hazard Analysis. CORRECTIVE ACTION: Update and revalidate the Process Hazard Analysis and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010078 |  |  | Program Level 3: Process Hazard Analysis - Retention | Failure to retain the Process Hazard Analysis and updates/revalidations for each covered process as well as the documented resolution of recommendations for the life of the process. | 19 CCR 4.5 2760.2(g) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 94 | Program 3 Prevention Program | Process Hazard Analysis | Retained all PHAs, updates/revalidations, and documented resolution of recommendations | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to retain the Process Hazard Analysis and updates/revalidations for each covered process as well as the documented resolution of recommendations for the life of the process. |  |  | OBSERVATION: The owner/operator failed to retain the Process Hazard Analysis and updates/revalidations for each covered process as well as the documented resolution of recommendations for the life of the process. CORRECTIVE ACTION: Obtain the missing Process Hazard Analysis and updates/revalidations for each covered process as well as the documented resolution of recommendations for the life of the process and submit a copy to the CUPA. | OBSERVATION: The owner/operator failed to retain the documented resolution of Process Hazard Analysis recommendations for the life of the process. CORRECTIVE ACTION: Obtain the resolution of the Process Hazard Analysis recommendations for the life of the process and submit a copy to the CUPA. | [5 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010079 |  |  | Program Level 3: Operating Procedures | Failure to develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information. | 19 CCR 4.5 2760.3(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 95 | Program 3 Prevention Program | Operating Procedures | Prepared written operating procedures that provide clear instructions for each covered process | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information. CORRECTIVE ACTION: Develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010080 |  |  | Program Level 3: Operating Procedures - Steps for Each Operating Phase | Failure to develop and implement written operating procedures that address at least the following operating phases: 1. Initial startup; 2. Normal operations; 3. Temporary operations; 4. Emergency shutdown including the conditions under which emergency shutdown is required, and the assignment of shutdown responsibility to qualified operators to ensure that emergency shutdown is executed in a safe and timely manner; 5. Emergency operations; 6. Normal shutdown; 7. Startup following a turnaround, or after an emergency shutdown. | 19 CCR 4.5 2760.3(a)(1) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 96 | Program 3 Prevention Program | Operating Procedures | Developed and implemented written operating procedures that address all operating phases | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop and implement written operating procedures that address at least the following operating phases: 1. Initial startup; 2. Normal operations; 3. Temporary operations; 4. Emergency shutdown including the conditions under which emergency shutdown is required, and the assignment of shutdown responsibility to qualified operators to ensure that emergency shutdown is executed in a safe and timely manner; 5. Emergency operations; 6. Normal shutdown; 7. Startup following a turnaround, or after an emergency shutdown. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address: initial startup; normal operations; temporary operations; emergency shutdown including the conditions under which emergency shutdown is required, and the assignment of shutdown responsibility to qualified operators to ensure that emergency shutdown is executed in a safe and timely manner; emergency operations; normal shutdown; startup following a turnaround, or after an emergency shutdown. CORRECTIVE ACTION: Develop, implement and submit copies of written operating procedures that address the deficiencies noted above. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010081 |  |  | Program Level 3: Operating Procedures - Operating Limits | Failure to develop and implement written operating procedures that address at least the following operating limits: 1. Consequences of deviation; and, 2. Steps required to correct or avoid deviation. | 19 CCR 4.5 2760.3(a)(2) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 97 | Program 3 Prevention Program | Operating Procedures | Written operating procedures address consequences of deviation and steps to avoid deviation | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop and implement written operating procedures that address at least the following operating limits: 1. Consequences of deviation; and, 2. Steps required to correct or avoid deviation. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address the consequences of deviation and the steps required to correct or avoid the deviation. CORRECTIVE ACTION: Develop and implement written operating procedures that address the consequences of deviation and the steps required to correct or avoid the deviation/ and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010082 |  |  | Program Level 3: Operating Procedures - Safety and Health Considerations | Failure to develop and implement written operating procedures that address at least the following safety and health considerations: 1. Properties of, and hazards presented by, the chemicals used in the process; 2. Precautions necessary to prevent exposure, including engineering controls, administrative controls, and personal protective equipment; 3. Control measures to be taken if physical contact or airborne exposure occurs; 4. Quality control for raw materials and control of hazardous chemical inventory levels; 5. Any special or unique hazards. | 19 CCR 4.5 2760.3(a)(3) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 98 | Program 3 Prevention Program | Operating Procedures | Written operating procedures address all required safety and health considerations | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop and implement written operating procedures that address at least the following safety and health considerations: 1. Properties of, and hazards presented by, the chemicals used in the process; 2. Precautions necessary to prevent exposure, including engineering controls, administrative controls, and personal protective equipment; 3. Control measures to be taken if physical contact or airborne exposure occurs; 4. Quality control for raw materials and control of hazardous chemical inventory levels; 5. Any special or unique hazards. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address: properties of, and hazards presented by, the chemicals used in the process; precautions necessary to prevent exposure, including engineering controls, administrative controls, and personal protective equipment; control measures to be taken if physical contact or airborne exposure occurs; quality control for raw materials and control of hazardous chemical inventory levels; any special or unique hazards. CORRECTIVE ACTION: Develop, implement, and submit copy of written operating procedures that address the deficiencies noted above. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010083 |  |  | Program Level 3: Operating Procedures - Safety Systems and their Functions | Failure to develop and implement written operating procedures that address safety systems and their functions. | 19 CCR 4.5 2760.3(a)(4) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 99 | Program 3 Prevention Program | Operating Procedures | Written operating procedures address safety systems and their functions | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop and implement written operating procedures that address safety systems and their functions. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address safety systems and their functions. CORRECTIVE ACTION: Develop and implement written operating procedures that address safety systems and their functions and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010084 |  |  | Program Level 3: Operating Procedures - Accessible | Failure to make operating procedures readily accessible to employees who work in or maintain a process. | 19 CCR 4.5 2760.3(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 100 | Program 3 Prevention Program | Operating Procedures | Operating procedures are readily accessible to employees who work in or maintain a process | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to make operating procedures readily accessible to employees who work in or maintain a process. |  |  | OBSERVATION: The owner/operator failed to make operating procedures readily accessible to employees who work in or maintain a process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating operating procedures are readily accessible to employees who work in or maintain a process. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010085 |  |  | Program Level 3: Operating Procedures - Review | Failure to review operating procedures as often as necessary to assure that they reflect current operating practice, including changes that result from changes in process chemicals, technology, and equipment, and changes to stationary sources. | 19 CCR 4.5 2760.3(c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 101 | Program 3 Prevention Program | Operating Procedures | Reviewed operating procedures to assure they reflect current operating practice | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to review operating procedures as often as necessary to assure that they reflect current operating practice, including changes that result from changes in process chemicals, technology, and equipment, and changes to stationary sources. |  |  | OBSERVATION: The owner/operator failed to review operating procedures as often as necessary to assure that they reflect current operating practice, including changes that result from changes in process chemicals, technology, and equipment, and changes to stationary sources. CORRECTIVE ACTION: Review and update the operating procedures to assure that they reflect current operating practice and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010086 |  |  | Program Level 3: Operating Procedures - Annual Certification | Failure to certify annually that the operating procedures are current and accurate. | 19 CCR 4.5 2760.3(c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 102 | Program 3 Prevention Program | Operating Procedures | Certified annually that the operating procedures are current and accurate | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to certify annually that the operating procedures are current and accurate. |  |  | OBSERVATION: The owner/operator failed to certify annually that the operating procedures are current and accurate. CORRECTIVE ACTION: Review and update the operating procedures to assure that they reflect current operating practice. Certify that the operating procedures are current and accurate and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010087 |  |  | Program Level 3: Operating Procedures - Safe Work Practices | Failure to develop and implement safe work practices to provide for the control of hazards during operations such as: 1. Logout/tagout; 2. Confined space entry; 3. Opening process equipment or piping; and 4. Control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel. | 19 CCR 4.5 2760.3(d) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 103 | Program 3 Prevention Program | Operating Procedures | Developed and implemented safe work practices to provide control of hazards during operations | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop and implement safe work practices to provide for the control of hazards during operations such as: 1. Logout/tagout; 2. Confined space entry; 3. Opening process equipment or piping; and 4. Control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel. |  |  | OBSERVATION: The owner/operator failed to develop and implement safe work practices to provide for the control of hazards during operations including: lockout/tagout; confined space entry; opening process equipment or piping; and control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel. CORRECTIVE ACTION: Develop and implement safe work practices to provide for the control of hazards during operations including: lockout/tagout; confined space entry; opening process equipment or piping; and control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Training | 5020006 |  |  | Program Level 3: Training - Initial | Failure to train each employee presently involved in operating a process, and each employee before being involved in operating a newly assigned process on the following: 1. Overview of the process; 2. Operating procedures; 3. Safety & health hazards; 4. Emergency operations including shutdown; 5. Safe work practices applicable to the employee's job tasks. | 19 CCR 4.5 2760.4(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 104 | Program 3 Prevention Program | Training | Trained employees on process overview, procedures, safety, emer. ops, and safe work practices | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to train each employee presently involved in operating a process, and each employee before being involved in operating a newly assigned process on the following: 1. Overview of the process; 2. Operating procedures; 3. Safety & health hazards; 4. Emergency operations including shutdown; 5. Safe work practices applicable to the employee's job tasks. |  |  | OBSERVATION: The owner/operator failed to train each employee presently involved in operating a process, and each employee before being involved in operating a newly assigned process on the following: overview of the process; operating procedures; safety & health hazards; emergency operations including shutdown; safe work practices applicable to the employee's job tasks. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating each employee presently involved in operating a process has been trained on the following: overview of the process; operating procedures; safety & health hazards; emergency operations including shutdown; safe work practices applicable to the employee's job tasks. | [6 empty] | No | No | Yes | No
CalARP Program | Training | 5020007 |  |  | Program Level 3: Training - Refresher | Failure to provide refresher training at least every three years, and more often if necessary, to each employee involved in operating a process to assure that the employee understands & adheres to the current operating procedures of the process. | 19 CCR 4.5 2760.4(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 105 | Program 3 Prevention Program | Training | Employees operating a process provided refresher training on operating procedures every three years | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to provide refresher training at least every three years, and more often if necessary, to each employee involved in operating a process to assure that the employee understands & adheres to the current operating procedures of the process. |  |  | OBSERVATION: The owner/operator failed to provide refresher training at least every three years, and more often if necessary, to each employee involved in operating a process to assure that the employee understands & adheres to the current operating procedures of the process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that each employee involved in operating a process has received refresher training. | [6 empty] | No | No | Yes | No
CalARP Program | Training | 5020008 |  |  | Program Level 3: Training - Documentation | Failure to prepare a training record which contains: 1. Identity of the Employee; 2. Date of training; 3. Means used to verify that the employee understood the training. | 19 CCR 4.5 2760.4(c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 106 | Program 3 Prevention Program | Training | Training records identify the employee, training date, and means to verify training was understood | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to prepare a training record which contains: 1. Identity of the Employee; 2. Date of training; 3. Means used to verify that the employee understood the training. |  |  | OBSERVATION: The owner/operator failed to prepare a training record which contains the identity of the employee; date of training; means used to verify that the employee understood the training. CORRECTIVE ACTION: Submit a copy of the training record to the CUPA which contains the identity of the employee; date of training; means used to verify that the employee understood the training. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010088 |  |  | Program Level 3: Mechanical Integrity - Procedures | Failure to establish and implement written procedures to maintain the on-going integrity of the process equipment. | 19 CCR 4.5 2760.5(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 107 | Program 3 Prevention Program | Mechanical Integrity | Established and implemented written procedures to maintain the integrity of process equipment | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to establish and implement written procedures to maintain the on-going integrity of the process equipment. |  |  | OBSERVATION: The owner/operator failed to establish and implement written procedures to maintain the on-going integrity of the process equipment. CORRECTIVE ACTION: Establish and implement written procedures to maintain the on-going integrity of the process equipment and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Training | 5020009 |  |  | Program Level 3: Mechanical Integrity - Training | Failure to train each employee involved in maintaining the on-going integrity of process equipment on the following: 1. Overview of the process and its hazards. 2. Procedures applicable to the employee’s job tasks to assure that the employee can perform the job tasks in a safe manner. | 19 CCR 4.5 2760.5(c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 108 | Program 3 Prevention Program | Mechanical Integrity | Employees conducting mechanical integrity trained on process overview/hazards & safety procedures | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to train each employee involved in maintaining the on-going integrity of process equipment on the following: 1. Overview of the process and its hazards. 2. Procedures applicable to the employee’s job tasks to assure that the employee can perform the job tasks in a safe manner. |  |  | OBSERVATION: The owner/operator failed to train each employee involved in maintaining the on-going integrity of process equipment on the following: overview of the process and its hazards; procedures applicable to the employee’s job tasks to assure that the employee can perform the job tasks in a safe manner. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that each employee involved in maintaining the on-going integrity of process equipment is trained on the following: overview of the process and its hazards; procedures applicable to the employee’s job tasks to assure that the employee can perform the job tasks in a safe manner. | [6 empty] | No | No | Yes | No
CalARP Program | Operations/Maintenance | 5030002 |  |  | Program Level 3: Mechanical Integrity - Inspection and Testing | Failure to ensure the following: 1. Inspections and tests are performed on process equipment; 2. Inspection and testing procedures follow recognized and generally accepted good engineering practices; 3. The frequency of inspections and tests of process equipment is consistent with applicable manufacturers’ recommendations and good engineering practices, and more frequently if determined to be necessary by prior operating experience; 4. Each inspection or test that has been performed on process equipment is documented and includes the date of inspection or test, name of the person who performed the inspection or test, serial number or other identifier of the equipment inspected or tested, description of the inspection or test performed, and the results of the inspection or test. | 19 CCR 4.5 2760.5(d) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 109 | Program 3 Prevention Program | Mechanical Integrity | Mechanical integrity inspections/testing performed per RAGAGEP, at proper frequency, and documented | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure the following: 1. Inspections and tests are performed on process equipment; 2. Inspection and testing procedures follow recognized and generally accepted good engineering practices; 3. The frequency of inspections and tests of process equipment is consistent with applicable manufacturers’ recommendations and good engineering practices, and more frequently if determined to be necessary by prior operating experience; 4. Each inspection or test that has been performed on process equipment is documented and includes the date of inspection or test, name of the person who performed the inspection or test, serial number or other identifier of the equipment inspected or tested, description of the inspection or test performed, and the results of the inspection or test. |  |  | OBSERVATION: The owner/operator failed to implement the following: inspections and tests are performed on process equipment; inspection and testing procedures follow recognized and generally accepted good engineering practices; the frequency of inspections and tests of process equipment is consistent with applicable manufacturers’ recommendations and good engineering practices, and more frequently if determined to be necessary by prior operating experience; each inspection or test that has been performed on process equipment is documented and includes the date of inspection or test, name of the person who performed the inspection or test, serial number or other identifier of the equipment inspected or tested, description of the inspection or test performed, and the results of the inspection or test. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has corrected the violations noted above. | [6 empty] | No | No | Yes | No
CalARP Program | Operations/Maintenance | 5030003 |  |  | Program Level 3: Mechanical Integrity - Equipment Deficiencies | Failure to correct deficiencies in equipment that are outside acceptable limits before further use or in a safe and timely manner when necessary means are taken to assure safe operation. | 19 CCR 4.5 2760.5(e) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 110 | Program 3 Prevention Program | Mechanical Integrity | Corrected deficiencies in equipment that are outside acceptable limits | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to correct deficiencies in equipment that are outside acceptable limits before further use or in a safe and timely manner when necessary means are taken to assure safe operation. |  |  | OBSERVATION: The owner/operator failed to correct deficiencies in equipment that are outside acceptable limits before further use or in a safe and timely manner when necessary means are taken to assure safe operation. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has corrected deficiencies in the equipment that is outside acceptable limits. | [6 empty] | No | No | Yes | No
CalARP Program | Operations/Maintenance | 5030004 |  |  | Program Level 3: Mechanical Integrity - Quality Assurance | Failure to ensure: 1. In the construction of new plants and equipment that equipment as it is fabricated is suitable for the process application for which it will be used. 2. Appropriate checks and inspections are performed to assure that equipment is installed properly and consistent with design specifications and the manufacturer's instructions. 3. Maintenance materials, spare parts, and equipment are suitable for the process application for which they will be used. | 19 CCR 4.5 2760.5(f) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 111 | Program 3 Prevention Program | Mechanical Integrity | Complied with quality assurance requirements: equipment & maint. material suitability & inspections | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure: 1. In the construction of new plants and equipment that equipment as it is fabricated is suitable for the process application for which it will be used. 2. Appropriate checks and inspections are performed to assure that equipment is installed properly and consistent with design specifications and the manufacturer's instructions. 3. Maintenance materials, spare parts, and equipment are suitable for the process application for which they will be used. |  |  | OBSERVATION: The owner/operator failed to assure the following: in the construction of new plants and equipment that equipment as it is fabricated is suitable for the process application for which it will be used; appropriate checks and inspections are performed to assure that equipment is installed properly and consistent with design specifications and the manufacturer's instructions; maintenance materials, spare parts, and equipment are suitable for the process application for which they will be used. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has assured the following: appropriate checks and inspections are performed to assure that equipment is installed properly and consistent with design specifications and the manufacturer's instructions; maintenance materials, spare parts, and equipment are suitable for the process application for which they will be used. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010089 |  |  | Program Level 3: Management of Change - Procedures | Failure to establish and implement written procedures to manage changes (except for “replacements in kind”) to process chemicals, technology, equipment, and procedures, and changes to stationary sources that affect a covered process. | 19 CCR 4.5 2760.6(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 112 | Program 3 Prevention Program | Management of Change | Established and implemented written procedures to manage changes to a covered process | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to establish and implement written procedures to manage changes (except for “replacements in kind”) to process chemicals, technology, equipment, and procedures, and changes to stationary sources that affect a covered process. |  |  | OBSERVATION: The owner/operator failed to establish and implement written procedures to manage changes (except for “replacements in kind”) to process chemicals, technology, equipment, and procedures, and changes to stationary sources that affect a covered process. CORRECTIVE ACTION: Establish and implement written procedures to manage changes (except for “replacements in kind”) to process chemicals, technology, equipment, and procedures, and changes to stationary sources that affect a covered process and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010090 |  |  | Program Level 3: Management of Change - Procedures | Failure to ensure the following considerations are addressed in the Management of Change procedures prior to any change: 1. The technical basis for the proposed change; 2. Impact of change on safety and health; 3. Modifications to and/or development of new operating and maintenance procedures; 4. Necessary time period for the change; 5. Authorization requirements for the proposed change. | 19 CCR 4.5 2760.6(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 113 | Program 3 Prevention Program | Management of Change | MOC procedures address tech basis for change, H&S impact, procedures, time needed & authorization | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure the following considerations are addressed in the Management of Change procedures prior to any change: 1. The technical basis for the proposed change; 2. Impact of change on safety and health; 3. Modifications to and/or development of new operating and maintenance procedures; 4. Necessary time period for the change; 5. Authorization requirements for the proposed change. |  |  | OBSERVATION: The owner/operator failed to ensure the following considerations are addressed in the Management of Change procedures prior to any change: the technical basis for the proposed change; impact of change on safety and health; modifications to and/or development of new operating and maintenance procedures; necessary time period for the change; authorization requirements for the proposed change. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the following considerations are addressed in the Management of Change procedures prior to any change: the technical basis for the proposed change; impact of change on safety and health; modifications to and/or development of new operating and maintenance procedures; necessary time period for the change; authorization requirements for the proposed change. | [6 empty] | No | No | Yes | No
CalARP Program | Training | 5020010 |  |  | Program Level 3: Management of Change - Training | Failure to ensure employees involved in operating a process and maintenance and contract employees whose job tasks would be affected by a change in the process are informed and trained in the change prior to start-up of the process or affected part of the process. | 19 CCR 4.5 2760.6(c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 114 | Program 3 Prevention Program | Management of Change | Employees involved in operating and maintaining a process are informed and trained in any changes | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to ensure employees involved in operating a process and maintenance and contract employees whose job tasks would be affected by a change in the process are informed and trained in the change prior to start-up of the process or affected part of the process. |  |  | OBSERVATION: The owner/operator failed to ensure employees involved in operating a process and maintenance and contract employees whose job tasks would be affected by a change in the process are informed and trained in the change prior to start-up of the process or affected part of the process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that employees involved in operating a process and maintenance and contract employees whose job tasks would be affected by a change in the process are informed and trained in the change. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010091 |  |  | Program Level 3: Management of Change - Process Safety Information | Failure to update process safety information if a management of change occurred that resulted in a change in the process safety information. | 19 CCR 4.5 2760.6(d) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 115 | Program 3 Prevention Program | Management of Change | Updated PSI when MOC resulted in a change to PSI | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to update process safety information if a management of change occurred that resulted in a change in the process safety information. |  |  | OBSERVATION: The owner/operator failed to update process safety information when a management of change occurred that resulted in a change in the process safety information. CORRECTIVE ACTION: Update process safety information affected by the management of change and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010092 |  |  | Program Level 3: Management of Change - Operating Procedures | Failure to update operating procedures or practices if a management of change occurred that resulted in a change in the operating procedures or practices and/or resulted in a change in the written procedures to maintain the ongoing integrity of process equipment required by Section 2760.5, such procedures or practices shall be updated prior to start-up of the process. | 19 CCR 4.5 2760.6(e) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 116 | Program 3 Prevention Program | Management of Change | Updated operating/maintenance procedures or practices prior to startup if MOC resulted in a change | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to update operating procedures or practices if a management of change occurred that resulted in a change in the operating procedures or practices and/or resulted in a change in the written procedures to maintain the ongoing integrity of process equipment required by Section 2760.5, such procedures or practices shall be updated prior to start-up of the process. |  |  | OBSERVATION: The owner/operator failed to update operating procedures or practices when a management of change occurred that resulted in a change in the procedures or practices. CORRECTIVE ACTION: Update operating procedures or practices affected by the management of change and submit a copy to the CUPA. | OBSERVATION: The owner/operator failed to update written procedures to maintain the ongoing integrity of process equipment when a management of change occurred that resulted in a change in the procedures. CORRECTIVE ACTION: Update procedures to maintain the ongoing integrity of process equipment affected by the management of change and submit a copy to the CUPA. | [5 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010093 |  |  | Program Level 3: Pre-Startup Safety Review | Failure to perform a pre-startup safety review for new stationary sources and for modified stationary sources when the modification is significant enough to require a change in the process safety information. | 19 CCR 4.5 2760.7(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 117 | Program 3 Prevention Program | Pre-Startup Review | Performed a pre-startup safety review when the modification required a change in the PSI | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to perform a pre-startup safety review for new stationary sources and for modified stationary sources when the modification is significant enough to require a change in the process safety information. |  |  | OBSERVATION: The owner/operator failed to perform a pre-startup safety review for a new stationary source when the modification is significant enough to require a change in the process safety information. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the following pre-startup safety requirements have been completed: construction and equipment was in accordance with design specifications; safety, operating, maintenance & emergency procedures are in place and are adequate; for new stationary sources, a PHA has been performed and recommendations have been resolved or implemented before startup, and modified stationary sources meet the requirements contained in the MOC; training of each employee involved in operating a process had been completed. | OBSERVATION: The owner/operator failed to perform a pre-startup safety review for a modified stationary source when the modification is significant enough to require a change in the process safety information. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the following pre-startup safety requirements have been completed: construction and equipment was in accordance with design specifications; safety, operating, maintenance & emergency procedures are in place and are adequate; for new stationary sources, a PHA has been performed and recommendations have been resolved or implemented before startup, and modified stationary sources meet the requirements contained in the MOC; training of each employee involved in operating a process had been completed. | [5 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010094 |  |  | Program Level 3: Pre-Startup Safety Review - General Requirements | Failure to ensure that the pre-startup safety review confirms, as a verification check, independent of the MOC process, the following prior to the introduction of a regulated substances to a process: 1. Construction and equipment wereis in accordance with design specifications. 2. Safety, operating, maintenance & emergency procedures are in place and are adequate. 3. For new stationary sources, a PHA has been performed and recommendations have been resolved or implemented before startup, and modified stationary sources meet the requirements contained in the MOC, Section 2760.6. 4. Training of each employee involved in operating a process had been completed. | 19 CCR 4.5 2760.7(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 118 | Program 3 Prevention Program | Pre-Startup Review | Pre-startup safety review addresses requirements in Section 2760.7(b) prior to introduction of a RS | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to ensure that the pre-startup safety review confirms, as a verification check, independent of the MOC process, the following prior to the introduction of a regulated substances to a process: 1. Construction and equipment wereis in accordance with design specifications. 2. Safety, operating, maintenance & emergency procedures are in place and are adequate. 3. For new stationary sources, a PHA has been performed and recommendations have been resolved or implemented before startup, and modified stationary sources meet the requirements contained in the MOC, Section 2760.6. 4. Training of each employee involved in operating a process had been completed. |  |  | OBSERVATION: The owner/operator failed to ensure that the pre-startup safety review confirmed the following prior to the introduction of a regulated substances to a process: construction and equipment wereis in accordance with design specifications; safety, operating, maintenance & emergency procedures are in place and are adequate; for new stationary sources, a PHA has been performed and recommendations have been resolved or implemented before startup, and modified stationary sources meet the requirements contained in the MOC; training of each employee involved in operating a process had been completed. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you have addressed all of the deficiencies noted. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/ Documentation | 5010095 |  |  | Program Level 3: Compliance Audits - Certification | Failure of the owner or operator to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 6 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. | 19 CCR 4.5 2760.8(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 119 | Program 3 Prevention Program | Compliance Audits | Certified and evaluated compliance with the provisions of this article at least every three years | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of the owner or operator to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 6 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. |  |  | OBSERVATION: The owner/operator failed to certify that they have evaluated compliance with the provisions of 19 CCR 4.5 Article 6 at least every three years to verify that the procedures and practices developed under 19 CCR 4.5 are adequate and are being followed. CORRECTIVE ACTION: Submit a certification to the CUPA that the owner/operator has evaluated compliance with the provisions of 19 CCR 4.5 Article 6 at least every three years to verify that the procedures and practices developed under chapter 19 CCR 4.5 are adequate and are being followed. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010096 |  |  | Program Level 3: Compliance Audits - Knowledgeable Person | Failure to ensure that the compliance audit is conducted by at least one person knowledgeable in the process. | 19 CCR 4.5 2760.8(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 120 | Program 3 Prevention Program | Compliance Audits | Compliance audit conducted by at least one person knowledgeable in the process | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that the compliance audit is conducted by at least one person knowledgeable in the process. |  |  | OBSERVATION: The owner/operator failed to ensure that the compliance audit is conducted by at least one person knowledgeable in the process. CORRECTIVE ACTION: Conduct the compliance audit with at least one person knowledgeable in the process. Develop a report of the compliance audit findings, including appropriate responses to each of the findings and submit a copy to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010097 |  |  | Program Level 3: Compliance Audits - Report | Failure to develop and have available for review, a report of the scope, methods used, results and findings of the audit. | 19 CCR 4.5 2760.8(c) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 121 | Program 3 Prevention Program | Compliance Audits | Developed and made available, a report of the scope, methods used, results and findings of the audit | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to develop and have available for review, a report of the scope, methods used, results and findings of the audit. |  |  | OBSERVATION: The owner/operator failed to develop and have available for review, a report of the scope, methods used, results and findings of the audit. CORRECTIVE ACTION: Develop a report of the scope, methods used, results and findings of the audit and submit a copy to the UPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010098 |  |  | Program Level 3: Compliance Audits - Findings/Resolutions | Failure to: 1. Promptly determine and document an appropriate response to each of the findings of the compliance audit; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings. Otherwise these responses shall be completed one and one-half (1.5) years after performing the compliance audit, or the next planned turnaround for items requiring a turnaround (these timelines shall not apply to any compliance audit completed prior to January 1, 2015); 3. Document the actual completion dates when deficiencies were corrected. | 19 CCR 4.5 2760.8(d) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 122 | Program 3 Prevention Program | Compliance Audits | Promptly determined and documented response to audit findings, including correction of deficiencies | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to: 1. Promptly determine and document an appropriate response to each of the findings of the compliance audit; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings. Otherwise these responses shall be completed one and one-half (1.5) years after performing the compliance audit, or the next planned turnaround for items requiring a turnaround (these timelines shall not apply to any compliance audit completed prior to January 1, 2015); 3. Document the actual completion dates when deficiencies were corrected. |  |  | OBSERVATION: The owner/operator failed to determine and document an appropriate response to each of the findings of the compliance audit and document the actual completion date when deficiencies were corrected, and/or failed to do so within the required time frame. CORRECTIVE ACTION: Document an appropriate response to each of the findings of the compliance audit, including documented completion dates when deficiencies were corrected and submit a copy to the UPA. | OBSERVATION: The owner/operator failed to document actual completion dates when deficiencies identified in the compliance audit were corrected. CORRECTIVE ACTION: Document actual completion dates when deficiencies identified in the compliance audit were corrected and submit a copy to the CUPA. | [5 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010099 |  |  | Program Level 3: Compliance Audits - Retention | Failure to retain the two most recent compliance audit reports. | 19 CCR 4.5 2760.8(e) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 123 | Program 3 Prevention Program | Compliance Audits | Retained the two most recent compliance audit reports | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to retain the two most recent compliance audit reports. |  |  | OBSERVATION: The owner/operator failed to retain the two most recent compliance audit reports conducted. CORRECTIVE ACTION: Submit a copy of the two most recent compliance audit reports to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010100 |  |  | Program Level 3: Incident Investigation | Failure to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release of a regulated substance. | 19 CCR 4.5 2760.9(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 124 | Program 3 Prevention Program | Incident Investigation | Investigated each incident that resulted or could reasonably have resulted in a catastrophic release | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release of a regulated substance. |  |  | OBSERVATION: The owner/operator failed to investigate each incident which resulted in, or could reasonably have resulted in, a catastrophic release. CORRECTIVE ACTION: Investigate the incident and submit a copy of the investigation findings with recommendations to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010101 |  |  | Program Level 3: Incident Investigation - Promptness | Failure to initiate an incident investigation as promptly as possible, but not later than 48 hours following the incident. | 19 CCR 4.5 2760.9(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 125 | Program 3 Prevention Program | Incident Investigation | Initiated incident investigations within 48 hours of the incident | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to initiate an incident investigation as promptly as possible, but not later than 48 hours following the incident. |  |  | OBSERVATION: The owner/operator failed to initiate an incident investigations within 48 hours of the incident. CORRECTIVE ACTION: Submit a statement of the CUPA demonstrating how incident investigations will be initiated within 48 hours of the incident. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010102 |  |  | Program Level 3: Incident Investigation - Team/Knowledgeable Person | Failure to establish an incident investigation team that consists of at least one person knowledgeable in the process involved, including a contract employee if the incident involved work of the contractor, and other persons with appropriate knowledge and experience to thoroughly investigate and analyze the incident. | 19 CCR 4.5 2760.9(c) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 126 | Program 3 Prevention Program | Incident Investigation | Incident investigation team consists of a person with knowledge and experience in the process | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to establish an incident investigation team that consists of at least one person knowledgeable in the process involved, including a contract employee if the incident involved work of the contractor, and other persons with appropriate knowledge and experience to thoroughly investigate and analyze the incident. |  |  | OBSERVATION: The owner/operator failed to establish an incident investigation team that consists of at least one person knowledgeable in the process involved, including a contract employee if the incident involved work of the contractor, and other persons with appropriate knowledge and experience to thoroughly investigate and analyze the incident. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that an incident investigation team has been established and consists of at least one person knowledgeable in the process involved, including a contract employee if the incident involved work of the contractor, and other persons with appropriate knowledge and experience to thoroughly investigate and analyze the incident. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010103 |  |  | Program Level 3: Incident Investigation - Report | Failure to prepare a report at the conclusion of the investigation which includes at a minimum: 1. Date the investigation began; 2. A description of the incident, including all of the data required under 2750.9(b); and, 3. Recommendations resulting from the investigation. | 19 CCR 4.5 2760.9(d) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 127 | Program 3 Prevention Program | Incident Investigation | Prepared an incident investigation report that includes the date, description and recommendations | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to prepare a report at the conclusion of the investigation which includes at a minimum: 1. Date the investigation began; 2. A description of the incident, including all of the data required under 2750.9(b); and, 3. Recommendations resulting from the investigation. |  |  | OBSERVATION: The owner/operator failed to prepare a report at the conclusion of the investigation that includes the date the investigation began; A description of the incident, including all of the data required under 2750.9(b); and recommendations resulting from the investigation. CORRECTIVE ACTION: Prepare and submit a copy of the report of the investigation to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010104 |  |  | Program Level 3: Incident Investigation - Findings/Resolutions | Failure to: 1. Establish a system to promptly address and resolve the incident report findings and recommendations; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings and recommendations. Otherwise these resolutions shall be completed no later than one and one-half (1.5) years after completion of the incident investigation, or two (2) years after the date of the incident, whichever is the earlier of the two dates, or the next planned turnaround for those items requiring turnaround. 3. Failure to document resolutions and corrective actions with actual completion dates. | 19 CCR 4.5 2760.9(e) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 128 | Program 3 Prevention Program | Incident Investigation | Established a system to promptly address and resolve the investigation findings and recommendations | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to: 1. Establish a system to promptly address and resolve the incident report findings and recommendations; 2. Enter into an agreement with the UPA on a timetable for resolution of these findings and recommendations. Otherwise these resolutions shall be completed no later than one and one-half (1.5) years after completion of the incident investigation, or two (2) years after the date of the incident, whichever is the earlier of the two dates, or the next planned turnaround for those items requiring turnaround. 3. Failure to document resolutions and corrective actions with actual completion dates. |  |  | OBSERVATION: The owner/operator failed to establish a system to address and resolve the incident report findings and recommendations, including documentation of the resolutions and corrective actions with actual completion dates, and/or failed to resolve the findings and recommendations within the required time frame. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating a system to promptly address and resolve the incident report findings and recommendations has been established. Address and resolve the investigation findings and recommendations and submit a copy of documented resolutions and corrective actions with actual completion dates to the UPA. | OBSERVATION: The owner/operator failed to document the incident investigation report resolutions and corrective actions with actual completion dates. CORRECTIVE ACTION: Address and resolve the investigation findings and recommendations and submit a copy of documented resolutions and corrective actions with actual completion dates to the CUPA. | [5 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010105 |  |  | Program Level 3: Incident Investigation - Affected Personnel | Failure to review the incident investigation report with all affected personnel whose job tasks are relevant to the incident findings including contract employees where applicable. | 19 CCR 4.5 2760.9(f) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 129 | Program 3 Prevention Program | Incident Investigation | Reviewed the incident investigation report with all affected personnel | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to review the incident investigation report with all affected personnel whose job tasks are relevant to the incident findings including contract employees where applicable. |  |  | OBSERVATION: The owner/operator failed to review the incident investigation report with all affected personnel whose job tasks are relevant to the incident findings including contract employees where applicable. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the incident investigation report has been reviewed with all affected personnel whose job tasks are relevant to the incident findings including contract employees where applicable. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010106 |  |  | Program Level 3: Incident Investigation - Retention | Failure to retain the incident investigation reports for five years. | 19 CCR 4.5 2760.9(g) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 130 | Program 3 Prevention Program | Incident Investigation | Retained the incident investigation reports for five years | 58 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to retain the incident investigation reports for five years. |  |  | OBSERVATION: The owner/operator failed to retain investigation reports for five years. CORRECTIVE ACTION: Submit a copy of the missing investigation reports for the last five years to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010107 |  |  | Program Level 3: Employee Participation - Plan | Failure to develop a written plan of action regarding the implementation of employee participation. | 19 CCR 4.5 2760.10(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 131 | Program 3 Prevention Program | Employee Participation | Developed a written plan of action regarding the implementation of employee participation | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to develop a written plan of action regarding the implementation of employee participation. |  |  | OBSERVATION: The owner/operator failed to develop a written plan of action regarding the implementation of employee participation. CORRECTIVE ACTION: Develop and submit a written plan of action regarding the implementation of employee participation to the CUPA. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010108 |  |  | Program Level 3: Employee Participation - Employee Consultation | Failure to consult with employees and their representatives on the conduct and development of the Process Hazard Analysis and on the development of the other elements of process safety management. | 19 CCR 4.5 2760.10(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 132 | Program 3 Prevention Program | Employee Participation | Consulted with employees/representatives on conduct and development of the PHA and PSM elements | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to consult with employees and their representatives on the conduct and development of the Process Hazard Analysis and on the development of the other elements of process safety management. |  |  | OBSERVATION: The owner/operator failed to consult with employees and their representatives on the conduct and development of the Process Hazard Analysis and on the development of the other elements of process safety management. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has consulted with employees and their representatives on the conduct and development of the Process Hazard Analysis and on the development of the other elements of process safety management. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010109 |  |  | Program Level 3: Employee Participation - Access | Failure to provide employees and their representatives with access to the Process Hazards Analysis and to all other information required to be developed under 19 CCR Chapter 4.5. | 19 CCR 4.5 2760.10(c) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 133 | Program 3 Prevention Program | Employee Participation | Provided employees/representatives with access to the PHA and all other CalARP information | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to provide employees and their representatives with access to the Process Hazards Analysis and to all other information required to be developed under 19 CCR Chapter 4.5. |  |  | OBSERVATION: The owner/operator failed to provide employees and their representatives with access to the Process Hazards Analysis and all other information required to be developed under Title 19, Division 2, Chapter 4.5. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has provided employees and their representatives with access to the Process Hazards Analysis and all other information required to be developed under Title 19, Division 2, Chapter 4.5. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010110 |  |  | Program Level 3: Hot Work Permit | Failure to issue a hot work permit for hot work operations conducted on or near a covered process. | 19 CCR 4.5 2760.11(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 134 | Program 3 Prevention Program | Hot Work Permit | Issued a hot work permit for hot work operations conducted on or near a covered process | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to issue a hot work permit for hot work operations conducted on or near a covered process. |  |  | OBSERVATION: The owner/operator failed to issue a hot work permit for hot work operations conducted on or near a covered process. CORRECTIVE ACTION: Submit a statement to the CUPA demonstrating the owner/operator has reviewed the fire prevention and protection requirements in 8 CCR 5189 (Process Safety Management of Acutely Hazardous Materials) and will issue hot work permits for all future hot work operations. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010111 |  |  | Program Level 3: Hot Work Permit - General Requirements | Failure to ensure the hot work permit documents the following: 1. The fire prevention and protection requirements in 8 CCR 5189 (Process Safety Management of Acutely Hazardous Materials) have been implemented prior to beginning the hot work operations. 2. The date(s) authorized for hot work. 3. The object on which hot work is to be performed identified. | 19 CCR 4.5 2760.11(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 135 | Program 3 Prevention Program | Hot Work Permit | Hot work permit documents the requirements of 8 CCR 5189, date of work, & object being worked on | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure the hot work permit documents the following: 1. The fire prevention and protection requirements in 8 CCR 5189 (Process Safety Management of Acutely Hazardous Materials) have been implemented prior to beginning the hot work operations. 2. The date(s) authorized for hot work. 3. The object on which hot work is to be performed identified. |  |  | OBSERVATION: The owner/operator failed to ensure the hot work permit documents the following: fire prevention and protection requirements in 8 CCR 5189 (Process Safety Management of Acutely Hazardous Materials) have been implemented prior to beginning the hot work operations; date(s) authorized for hot work; object on which hot work is to be performed identified. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating future hot work permits document the following: fire prevention and protection requirements in 8 CCR 5189 (Process Safety Management of Acutely Hazardous Materials) have been implemented prior to beginning the hot work operations; date(s) authorized for hot work; object on which hot work is to be performed identified. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010112 |  |  | Program Level 3: Hot Work Permit - Retention | Failure to keep the hot work permit on file until completion of the hot work operations. | 19 CCR 4.5 2760.11(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 136 | Program 3 Prevention Program | Hot Work Permit | Hot work permit kept on file until completion of the hot work operations | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to keep the hot work permit on file until completion of the hot work operations. |  |  | OBSERVATION: The owner/operator failed to keep the hot work permit on file until completion of the hot work operations. CORRECTIVE ACTION: Submit a statement to the CUPA demonstrating the hot work permit will be kept on file until completion of the hot work operations. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010113 |  |  | Program Level 3: Contractors | Failure to perform the following: 1. Obtain and evaluate information regarding the contract owner or operator’s safety performance and programs when selecting a contractor. 2. Inform the contract owner or operator of the known potential fire, explosion, or toxic release hazards related to the contractor’s work and the process. 3. Explain to the contract owner or operator the applicable provisions of Article 7 (Emergency Response Program). 4. Develop and implement safe work practices consistent with the Section 2760.3(d) (operating procedures), to control the entrance, presence, and exit of the contract owner or operator and contract employees in covered process areas. | 19 CCR 4.5 2760.12(b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 137 | Program 3 Prevention Program | Contractors | Complied with all contractor requirements | 41 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to perform the following: 1. Obtain and evaluate information regarding the contract owner or operator’s safety performance and programs when selecting a contractor. 2. Inform the contract owner or operator of the known potential fire, explosion, or toxic release hazards related to the contractor’s work and the process. 3. Explain to the contract owner or operator the applicable provisions of Article 7 (Emergency Response Program). 4. Develop and implement safe work practices consistent with the Section 2760.3(d) (operating procedures), to control the entrance, presence, and exit of the contract owner or operator and contract employees in covered process areas. |  |  | OBSERVATION: The owner/operator failed to do one or more of the following: Obtain and evaluate information regarding the contract owner or operator’s safety performance and programs when selecting a contractor; Inform the contract owner or operator of the known potential fire, explosion, or toxic release hazards related to the contractor’s work and the process; Explain to the contract owner or operator the applicable provisions of Article 7 (Emergency Response Program); Develop and implement safe work practices consistent with the Section 2760.3(d) (operating procedures), to control the entrance, presence, and exit of the contract owner or operator and contract employees in covered process areas. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the owner/operator has corrected the deficiencies noted. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010114 |  |  | Program Level 3: Contractors - Performance Evaluation | Failure to periodically evaluate and document the evaluation of the performance of the contract owner or operator in fulfilling the following: 1. Each contract employee is trained in the work practices necessary to safely perform his or her job. 2. Each contract employee is instructed in the known potential fire, explosion, or toxic release hazards related to his or her job and the process, and the applicable provisions of the emergency action plan. 3. Document that each contract employee has received and understood the training required by this section. 4. Prepare a training record which contains Training record contains the identity of the contract employee, date of training, and the means used to verify that the employee understood the training. 5. Each contract employee follows the safety rules of the stationary source including the safe work practices required by Section 2760.3(d) (operating procedures). 6. Advise the owner or operator of any unique hazards presented by the contract owner or operator’s work, or of any hazards found by the contract owner or operator’s work. | 19 CCR 4.5 2760.12(b)(5) | 2022-07-01 | 2099-12-31 | 2022-07-01 | Revised | 138 | Program 3 Prevention Program | Contractors | Periodically evaluated the performance of the contract owner or operator and documented evaluation | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to periodically evaluate and document the evaluation of the performance of the contract owner or operator in fulfilling the following: 1. Each contract employee is trained in the work practices necessary to safely perform his or her job. 2. Each contract employee is instructed in the known potential fire, explosion, or toxic release hazards related to his or her job and the process, and the applicable provisions of the emergency action plan. 3. Document that each contract employee has received and understood the training required by this section. 4. Prepare a training record which contains Training record contains the identity of the contract employee, date of training, and the means used to verify that the employee understood the training. 5. Each contract employee follows the safety rules of the stationary source including the safe work practices required by Section 2760.3(d) (operating procedures). 6. Advise the owner or operator of any unique hazards presented by the contract owner or operator’s work, or of any hazards found by the contract owner or operator’s work. |  |  | OBSERVATION: Owner/operator failed to periodically evaluate and document the evaluation of the contractor's performance for the following: contract employees are trained in the work practices to safely perform his or her job; each contract employee is instructed in the known potential fire, explosion, or toxic release hazards related to the job and process, and the applicable provisions of the emergency action plan; documentation that each employee received and understood the training; records with the identity of the contract employee, date of training, and the means used to verify employee understood the training; contract employees follow the safety rules and safe work practices required by §2760.3(d); advise the owner/operator of any hazards presented by the contractor’s work, or of any hazards found by the contract owner or operator’s work. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has evaluated the performance of the contract owner or operator as described above. | [6 empty] | No | No | Yes | No
CalARP Program | Administration/Documentation | 5010127 |  |  | Program level 4: Process Safety Information - Compilation | Failure to develop and maintain a compilation of written process safety information before conducting any PHA, Hierarchy of Hazard Control Analysis, Safeguard Protection Analysis, or Damage Mechanism Review, as required. | 19 CCR 4.5 2762.1(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 139 | Program 4 Prevention Program | Process Safety Information | Compiled written process safety information before a PHA, HCA, SPA, as required | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and maintain a compilation of written process safety information before conducting any PHA, Hierarchy of Hazard Control Analysis, Safeguard Protection Analysis, or Damage Mechanism Review, as required. |  |  | OBSERVATION: Owner/Operator failed to develop and maintain a compilation of written process safety information before conducting any PHA, Hierarchy of Hazard Control Analysis, Safeguard Protection Analysis, or Damage Mechanism Review. CORRECTIVE ACTION: Owner/operator will establish revise written procedures to ensure the compilation of written process safety information before conducting any PHA, Hierarchy of Hazard Control Analysis, Safeguard Protection Analysis, or Damage Mechanism Review; compile the process safety information as required in 2762.1; submit documentation to UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010128 |  |  | Program level 4: Process Safety Information - Hazards | Failure to ensure information pertaining to hazards of substances used in, present in or produced by the process includes at least the following: (1) Toxicity information, including acute and chronic health hazards; (2) California Permissible exposure limits (PELs); (3) For regulated substances: American Conference of Governmental Industrial Hygienists (ACGIH) Emergency Response Planning Guideline values, U.S. EPA Acute Exposure Guideline Levels (AEGLs), and the California Office of Environmental Health Hazard Assessment (OEHHA) acute and eight-hour Reference Exposure Levels (RELs); (4) Physical data; (5) Corrosion data; (6) Thermal and chemical stability data; (7) Reactivity data; and (8) Hazardous effects of incompatible mixtures that could foreseeably occur. | 19 CCR 4.5 2762.1(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 140 | Program 4 Prevention Program | Process Safety Information | Compiled info on hazards of substances used in, present in, or produced as required | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure information pertaining to hazards of substances used in, present in or produced by the process includes at least the following: (1) Toxicity information, including acute and chronic health hazards; (2) California Permissible exposure limits (PELs); (3) For regulated substances: American Conference of Governmental Industrial Hygienists (ACGIH) Emergency Response Planning Guideline values, U.S. EPA Acute Exposure Guideline Levels (AEGLs), and the California Office of Environmental Health Hazard Assessment (OEHHA) acute and eight-hour Reference Exposure Levels (RELs); (4) Physical data; (5) Corrosion data; (6) Thermal and chemical stability data; (7) Reactivity data; and (8) Hazardous effects of incompatible mixtures that could foreseeably occur. |  |  | OBSERVATION: Owner/operator failed to compile and maintain up-to-date written process safety information pertaining to the hazards of the regulated substances in the process that includes: toxicity information; for regulated substances, ACGIH Emergency Response Planning Guideline values, US EPA Acute Exposure Guideline Levels, California OEHHA acute and eight - hour Reference Exposure Levels, California Permissible exposure limits; physical data; reactivity data; corrosivity data; thermal and chemical stability data; hazardous effects of inadvertent mixing of different materials that could foreseeably occur. CORRECTIVE ACTION: Compile up-to-date written process safety information for the hazards of hazardous substances that includes: toxicity information; permissible exposure limits; physical data; reactivity data; corrosivity data; thermal and chemical stability data; hazardous effects of inadvertent mixing of different materials; submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010129 |  |  | Program level 4: Process Safety Information - Technology | Failure to ensure information pertaining to the technology of the process includes at least the following items: (1) A block flow diagram or simplified process flow diagram; (2) Process chemistry; (3) Maximum intended inventory; (4) Safe upper and lower limits for process variables such as temperatures, pressures, flows, levels, and compositions; and, (5) The consequences of deviations, including chemical mixing or reactions that may affect the safety and health of employees or the public. | 19 CCR 4.5 2762.1(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 141 | Program 4 Prevention Program | Process Safety Information | Compiled Information on the technology of the process as required | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure information pertaining to the technology of the process includes at least the following items: (1) A block flow diagram or simplified process flow diagram; (2) Process chemistry; (3) Maximum intended inventory; (4) Safe upper and lower limits for process variables such as temperatures, pressures, flows, levels, and compositions; and, (5) The consequences of deviations, including chemical mixing or reactions that may affect the safety and health of employees or the public. |  |  | OBSERVATION: Owner/operator failed to compile written process safety information concerning the technology of the process that includes: a block flow diagram or simplified process flow diagram; process chemistry; maximum intended inventory; safe upper and lower limits for such items as temperatures, pressures, flows or compositions; an evaluation of the consequences of deviations that may affect the safety and health of employees or the public. CORRECTIVE ACTION: Compile written process safety information concerning the technology of the process that includes: a block flow diagram or simplified process flow diagram; process chemistry; maximum intended inventory; safe upper and lower limits for such items as temperatures, pressures, flows or compositions; an evaluation of the consequences of deviations that may affect the safety and health of employees and the public and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010130 |  |  | Program level 4: Process Safety Information - Process Equipment | Failure to ensure information pertaining to the process equipment at least includes the following information : (1) Materials of construction; (2) Piping and instrument diagrams (P&IDs); (3) Electrical classification; (4) Relief system design and design basis; (5) Ventilation system design; (6) Design codes and standards employed, including design conditions and operating limits; (7) Material and energy balances for processes built after June 21, 1999 and previously covered under Program 3, and material and energy balances for all other processes as of the effective date of Article 6.5; (8) Safety systems, such as interlocks, detection and suppression systems; and (9) Electrical supply and distribution systems. | 19 CCR 4.5 2762.1(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 142 | Program 4 Prevention Program | Process Safety Information | Compiled Information on process equipment as required | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure information pertaining to the process equipment at least includes the following information : (1) Materials of construction; (2) Piping and instrument diagrams (P&IDs); (3) Electrical classification; (4) Relief system design and design basis; (5) Ventilation system design; (6) Design codes and standards employed, including design conditions and operating limits; (7) Material and energy balances for processes built after June 21, 1999 and previously covered under Program 3, and material and energy balances for all other processes as of the effective date of Article 6.5; (8) Safety systems, such as interlocks, detection and suppression systems; and (9) Electrical supply and distribution systems. |  |  | OBSERVATION: Owner/operator failed to compile written information on process equipment including: materials of construction; P&IDs; electrical classification; relief system design/design basis; ventilation system design; design codes & standards - design conditions & operating limits; material & energy balances for processes built after June 21, 1999 & under Program 3, material & energy balances of all other processes; safety systems (e.g., interlocks, detection, or suppression systems); electrical supply/distribution systems. CORRECTIVE ACTION: Owner/operator will compile process safety info for equipment including: construction materials; P&IDs; electrical classification; relief system design/design basis; ventilation system design; design codes & standards; material & energy balances for processes after June 21, 1999 & Program 3; safety systems (e.g., interlocks, detection, or suppression systems), electrical supply/distribution systems. & submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010131 |  |  | Program level 4: Process Safety Information - Equipment Compliance Documentation | Failure to document that process equipment complies with recognized and generally accepted good engineering practices (RAGAGEP), where RAGAGEP has been established for that process equipment, or with other more protective internal practices that ensure safe operation. Failure to document that the equipment is designed, constructed, installed, maintained, inspected, tested and operated in a safe manner for installation of new process equipment for which no RAGAGEP exists. | 19 CCR 4.5 2762.1(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 143 | Program 4 Prevention Program | Process Safety Information | Compiled Info on equipment with RAGAGEP - protective internal practice | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document that process equipment complies with recognized and generally accepted good engineering practices (RAGAGEP), where RAGAGEP has been established for that process equipment, or with other more protective internal practices that ensure safe operation. Failure to document that the equipment is designed, constructed, installed, maintained, inspected, tested and operated in a safe manner for installation of new process equipment for which no RAGAGEP exists. |  |  | OBSERVATION: Owner/operator failed to document the following: (1) that equipment complies with recognized and generally accepted good engineering practices (RAGAGEP); (2) more protective internal practice that ensures safe operation; (3) failure to document that new process equipment for which no RAGAGEP exists is designed, constructed, installed, maintained, inspected, tested and operated in a safe manner. CORRECTIVE ACTION: Owner/operator will demonstrate that equipment complies with recognized and generally accepted good engineering practices or a protective internal practice that ensures safe operation and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010132 |  |  | Program level 4: Process Safety Information - Existing Equipment Compliance Documentation | Failure to document that the equipment is designed, constructed, installed, maintained, inspected, tested and operated in a safe manner for existing process equipment that was designed and constructed in accordance with codes, standards, or practices that are no longer in general use. | 19 CCR 4.5 2762.1(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 144 | Program 4 Prevention Program | Process Safety Information | Compiled information on compliance of existing equipment | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document that the equipment is designed, constructed, installed, maintained, inspected, tested and operated in a safe manner for existing process equipment that was designed and constructed in accordance with codes, standards, or practices that are no longer in general use. |  |  | OBSERVATION: Owner/operator failed to determine and document that existing equipment designed and constructed in accordance with codes, standards, or practices that are no longer in general use are designed, maintained, inspected, tested, and operating in a safe manner. CORRECTIVE ACTION: Owner/operator will determine and document that existing equipment are designed, maintained, inspected, tested, operated in a safe manner, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010133 |  |  | Program level 4: Process Hazard Analysis (PHA) - General | Failure to perform and document an effective PHA appropriate to the complexity of each process in order to identify, evaluate, and control hazards associated with each process. Failed to cover all modes of operation, as set forth in subsection 2762.3 (a)(1), in the PHA. Failed to determine and document the priority order for conducting PHAs based on the extent of process hazards, the number of potentially affected people, the age of the process and the process operating history. | 19 CCR 4.5 2762.2(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 145 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Performed and documented effective PHA appropriate to the complexity of each process | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform and document an effective PHA appropriate to the complexity of each process in order to identify, evaluate, and control hazards associated with each process. Failed to cover all modes of operation, as set forth in subsection 2762.3 (a)(1), in the PHA. Failed to determine and document the priority order for conducting PHAs based on the extent of process hazards, the number of potentially affected people, the age of the process and the process operating history. |  |  | OBSERVATION: Owner/operator failed to perform an effective PHA including: a PHA appropriate to the complexity of each process including each process not previously addressed under Program 3 within three years and address all modes of operation as set forth in subsection 2762.3 (a)(1); failed to determine and document a priority order for conducting PHA's based on the process hazards, number of potentially affected people, the age of the process, and the process operating history. CORRECTIVE ACTION: Owner/operator shall develop a written process for prioritizing PHAs based on the process hazards, the number of affected people, the age of the process, and operating history. Owner/Operator shall perform an effective PHA and document the PHA findings and recommendations and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010134 |  |  | Program level 4: Process Hazard Analysis (PHA) - Methodology | Failure to work with the UPA in selecting and using at least one of the following methods: (1) What-If; (2) Checklist; (3) What-If / Checklist; (4) Hazard and Operability Study (HAZOP); (5) Failure Mode and Effects Analysis (FMEA); (6) Fault Tree Analysis; (7) Other PHA methods recognized by engineering organizations or governmental agencies. | 19 CCR 4.5 2762.2(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 146 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Worked with the UPA in selecting and using at least one of the approved PHA methods | 83 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to work with the UPA in selecting and using at least one of the following methods: (1) What-If; (2) Checklist; (3) What-If / Checklist; (4) Hazard and Operability Study (HAZOP); (5) Failure Mode and Effects Analysis (FMEA); (6) Fault Tree Analysis; (7) Other PHA methods recognized by engineering organizations or governmental agencies. |  |  | OBSERVATION: Owner/operator failed to work with the UPA in selecting and using one of the following methods for performing the PHA: (1) What-if; (2) Checklist; (3) What if/Checklist; (4) Hazard and Operability Study (HAZOP); (5) Failure Mode Effects Analysis (FMEA); (6) Fault Tree Analysis; (7) Other PHA methods recognized by engineering organizations or governmental agencies. CORRECTIVE ACTION: Owner/Operator shall contact and coordinate with the UPA before selecting and using a PHA methodology. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010135 |  |  | Program level 4: Process Hazard Analysis (PHA) - Elements | Failure to ensure the PHA addresses: (1) The hazards of the process; (2) Previous publicly documented incidents in the petroleum refinery and petrochemical industry sector that are relevant to the PHA; (3) Damage Mechanism Review reports pursuant to subsection 2762.5(e) that are applicable to the process units; (4) Hierarchy of Hazard Control Analysis reports pursuant to section 2762.13 that are applicable to the process units; (5) A review of Management of Change documents completed since the last PHA that apply to the process unit. (6) Potential consequences of failures of process equipment; (7) Facility siting, including the placement of processes, equipment, buildings, employee occupancies and work stations in order to effectively protect employees and the public from process safety hazards; (8) Human factors as required under section 2762.15; (9) A qualitative evaluation of the types, severity, and likelihood of possible incidents that could result from a failure of a process or of process equipment; (10) The potential effects of external events, including seismic events, if applicable; and (11) The findings of incident investigations relevant to the process. | 19 CCR 4.5 2762.2(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 147 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Ensured the PHA addresses hazards, incidents, DMRs, HCAs, MOCs, failure potential, siting, etc | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PHA addresses: (1) The hazards of the process; (2) Previous publicly documented incidents in the petroleum refinery and petrochemical industry sector that are relevant to the PHA; (3) Damage Mechanism Review reports pursuant to subsection 2762.5(e) that are applicable to the process units; (4) Hierarchy of Hazard Control Analysis reports pursuant to section 2762.13 that are applicable to the process units; (5) A review of Management of Change documents completed since the last PHA that apply to the process unit. (6) Potential consequences of failures of process equipment; (7) Facility siting, including the placement of processes, equipment, buildings, employee occupancies and work stations in order to effectively protect employees and the public from process safety hazards; (8) Human factors as required under section 2762.15; (9) A qualitative evaluation of the types, severity, and likelihood of possible incidents that could result from a failure of a process or of process equipment; (10) The potential effects of external events, including seismic events, if applicable; and (11) The findings of incident investigations relevant to the process. |  |  | OBSERVATION: Owner/operator failed to ensure the PHA addresses: (1) The hazards of the process; (2) Incidents in the petroleum industry or petrochemical industry relevant to the PHA; (3) DMR reports applicable to the process units; (4) HCA reports applicable to the process units; (5) A review of MOC documents that have been completed since the last PHA applicable to the process units; (6) Consequences of failures of process equipment; (7) Facility siting, including the placement of processes, equipment, buildings, employee occupancies and work stations to effectively protect employees and the public: (8) Human factors; (9) A qualitative evaluation of the types, severity, and likelihood of possible incidents that could result from a failure of a process or of process equipment; (10) The potential effects of external events; & (11) Applicable incident investigation findings. CORRECTIVE ACTION: Owner/operator shall perform an effective PHA and submit documentations to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010136 |  |  | Program level 4: Process Hazard Analysis (PHA) - Team Qualifications | Failure to ensure the PHA is performed by a team with expertise in engineering and process operations and to include at least one operating employee who currently works or provides training in the unit, and has experience and knowledge specific to the process being evaluated. Failure to have the team also include one member with expertise in the specific PHA method being used. Failure to have the team consult with individuals with expertise in damage mechanisms, process chemistry, and control systems, as necessary. Failure to provide for employee participation in this process, pursuant to section 2762.10. | 19 CCR 4.5 2762.2(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 148 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | PHA is performed by a team with expertise and complies with requirements | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PHA is performed by a team with expertise in engineering and process operations and to include at least one operating employee who currently works or provides training in the unit, and has experience and knowledge specific to the process being evaluated. Failure to have the team also include one member with expertise in the specific PHA method being used. Failure to have the team consult with individuals with expertise in damage mechanisms, process chemistry, and control systems, as necessary. Failure to provide for employee participation in this process, pursuant to section 2762.10. |  |  | OBSERVATION: Owner/operator failed to perform the Process Hazard Analysis using a team with expertise in engineering and process operations, including at least one employee who has experience and knowledge specific to the process being evaluated, and one member who is knowledgeable in the specific Process Hazard Analysis methodology being used. CORRECTIVE ACTION: Conduct a Process Hazard Analysis using a team with expertise in engineering and process operations, including at least one employee selected pursuant to the employee participation process specified in 2762.10 who has experience and knowledge specific to the process being evaluated, one member who is knowledgeable in the specific Process Hazard Analysis methodology being used, consult with individuals knowledgeable in damage mechanisms, process chemistry, and control systems and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010137 |  |  | Program level 4: Process Hazard Analysis (PHA) - SPA | Failure to perform a Safeguard Protection Analysis (SPA) pursuant to section 2762.2.1 for each scenario in the PHA that identifies the potential for a major incident. Failure to append SPA recommendations to the PHA report, upon completion of the SPA. | 19 CCR 4.5 2762.2(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 149 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Ensured SPA is performed for scenarios in PHA identifying major incidents | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform a Safeguard Protection Analysis (SPA) pursuant to section 2762.2.1 for each scenario in the PHA that identifies the potential for a major incident. Failure to append SPA recommendations to the PHA report, upon completion of the SPA. |  |  | OBSERVATION: Owner/operator failed to perform a Safeguard Protection Analysis pursuant to section 2762.2.1 for each major incident that identified the potential for a major incident. Failure to append the Safeguard Protection Analysis to the PHA report upon completion. CORRECTIVE ACTION: Owner/Operator will conduct Safeguard Protection Analysis for each scenario identified in the PHA with the potential of a major incident as an appendix and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010138 |  |  | Program level 4: Process Hazard Analysis (PHA) - HCA | Failure to conduct in a timely manner a Hierarchy of Hazard Control Analysis pursuant to section 2762.13 for all recommendations made by the PHA team for each scenario that identifies the potential for a major incident. | 19 CCR 4.5 2762.2(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 150 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Used HCA for recommendations for scenarios identifying major incidents | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to conduct in a timely manner a Hierarchy of Hazard Control Analysis pursuant to section 2762.13 for all recommendations made by the PHA team for each scenario that identifies the potential for a major incident. |  |  | OBSERVATION: Owner/operator failed to perform a Hierarchy of Hazard Control Analysis pursuant to 2762.13 for all recommendations made by the PHA team for recommendations made for scenario that identifies the potential for a major incident. CORRECTIVE ACTION: Owner/operator will conduct a Hierarchy of Hazard Control Analysis for recommendations for each scenario identified in the PHA with the potential of a major incident and provide documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010139 |  |  | Program level 4: Process Hazard Analysis (PHA) -Recommendation Documentation | Failure to ensure the team documents its findings and recommendations in a report, made available in the respective work area for review by any person working in that area. | 19 CCR 4.5 2762.2(g) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 151 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Written recommendations & report available in work area for review | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the team documents its findings and recommendations in a report, made available in the respective work area for review by any person working in that area. |  |  | OBSERVATION: Owner/operator failed to ensure the PHA team documents its findings and recommendations in a report made available in the respective work area for review by any person working in that area. CORRECTIVE ACTION: Owner/operator will establish or revise their written procedures to ensure PHA report available for review in the respective work area. Owner/operator will ensure that all PHA findings and recommendations are in a report made available in the respective work area for review by and person working in that area and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010140 |  |  | Program level 4: Process Hazard Analysis (PHA) - Report Contents | Failure to ensure the PHA report include: (1) the method, analyses and factors considered by the PHA team; (2) the findings of the PHA team; and (3) the PHA team's recommendations. | 19 CCR 4.5 2762.2(h) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 152 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Ensured PHA includes methods, analyses, findings, and recommendations | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PHA report include: (1) the method, analyses and factors considered by the PHA team; (2) the findings of the PHA team; and (3) the PHA team's recommendations. |  |  | OBSERVATION: Owner/operator failed to ensure the PHA report include the method, analyses, factors considered by the PHA team, findings of the team and the team's recommendations. CORRECTIVE ACTION: Owner/operator will establish or revise their written procedures and also revise the deficient PHA report to include the method, analyses, factors considered by the team, the findings of the team, and the team's recommendations and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010141 |  |  | Program level 4: Process Hazard Analysis (PHA) -Corrective Action Work Process | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the PHA team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. | 19 CCR 4.5 2762.2(i) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 153 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Followed corrective action work process on findings and recommendations | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the PHA team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. |  |  | OBSERVATION: Owner/operator failed to follow the corrective action work process documented in subsections 2762.16(d) and (e) when resolving the PHA team's findings and recommendations, determining action items for implementation, tracking completion, and documentation of closeout. CORRECTIVE ACTION: Owner/operator will establish or revise written procedures to ensure they follow the corrective action work process documented specified subsections 2762.16(d) and (e) when resolving PHA team's finding and recommendations, determining action items for implementation, tracking completion dates, and documentation of closeout and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010142 |  |  | Program level 4: Process Hazard Analysis (PHA) - Revalidation | Failure to update and revalidate a written PHA at least once every five (5) years in accordance with the requirements of section 2762.2, to ensure that the PHA is consistent with the current process. | 19 CCR 4.5 2762.2(j) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 154 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Ensured written PHA is updated or reevaluated every five years | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update and revalidate a written PHA at least once every five (5) years in accordance with the requirements of section 2762.2, to ensure that the PHA is consistent with the current process. |  |  | OBSERVATION: Owner/operator failed to update and reevaluate a written PHA at least one every five years according to the requirements of 2762.2 to ensure that the PHA is consistent with the current process. CORRECTIVE ACTION: Owner/operator will update and reevaluate the PHA reports which have not been reevaluated in the past five years, establish or modify written procedures to ensure that PHA reports are reviewed every five years, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010143 |  |  | Program level 4: Process Hazard Analysis (PHA) - Retention | Failure to retain for the life of the process all PHAs and PHA updates and revalidations for each process covered by section 2762.2. Failure to have information contain the documented resolution of recommendations as appendices described in subsections 2762.16 (d) and (e). | 19 CCR 4.5 2762.2(k) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 155 | Program 4 Prevention Program | Process Hazard Analysis (PHA) | Retained PHA and all PHA updates for process life | 50 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain for the life of the process all PHAs and PHA updates and revalidations for each process covered by section 2762.2. Failure to have information contain the documented resolution of recommendations as appendices described in subsections 2762.16 (d) and (e). |  |  | OBSERVATION: Owner/operator failed to retain for the life of the process of all PHA reports and PHA update and reevaluation reports for each process covered by section 2762.2. CORRECTIVE ACTION: Owner/operator will retain for the life of the process all PHA reports, PHA update and reevaluation reports, establish or modify written procedures to ensure that PHA reports are retained for the life of each process, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010144 |  |  | Program level 4: Safeguard Protection Analysis - Safeguards | Failure to ensure a SPA team performs a written SPA, for each scenario where a PHA identifies the potential for a major incident, to determine: (1) the effectiveness of existing individual safeguards; (2) the combined effectiveness of all existing safeguards for each failure scenario in the PHA; (3) the individual and combined effectiveness of safeguards recommended in the PHA; and (4) the individual and combined effectiveness of additional or alternative safeguards that may be needed. | 19 CCR 4.5 2762.2.1(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 156 | Program 4 Prevention Program | Safeguard Protection Analysis | Ensured a SPA team performs a SPA for each major incident scenario | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure a SPA team performs a written SPA, for each scenario where a PHA identifies the potential for a major incident, to determine: (1) the effectiveness of existing individual safeguards; (2) the combined effectiveness of all existing safeguards for each failure scenario in the PHA; (3) the individual and combined effectiveness of safeguards recommended in the PHA; and (4) the individual and combined effectiveness of additional or alternative safeguards that may be needed. |  |  | OBSERVATION: Owner/operator failed to ensure a SPA team performs a written SPA for each scenario where a PHA identifies the potential for a major incident, to determine: the effectiveness of existing individual safeguards; the combined effectiveness of all safeguard of each failure scenario; individual and combined effectiveness of safeguards recommended in PHA; the individual and combined effectiveness of additional or alternative safeguards. CORRECTIVE ACTION: Owner/operator will ensure that SPA team performs written SPA for each scenario where a PHA identifies the potential for a incident, to determine: the effectiveness individual safeguards; the combined effectiveness of all existing safeguards, individual and combined effectiveness of safeguards recommended in PHA, individual and combined effectiveness of additional or alternative safeguards that may be needed, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010145 |  |  | Program level 4: Safeguard Protection Analysis - IPLs | Failure to ensure all independent protection layers (IPLs) for each failure scenario shall be independent of each other and independent of initiating causes. | 19 CCR 4.5 2762.2.1(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 157 | Program 4 Prevention Program | Safeguard Protection Analysis | IPL have failure scenario independent of each other & initiating causes as required | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure all independent protection layers (IPLs) for each failure scenario shall be independent of each other and independent of initiating causes. |  |  | OBSERVATION: Owner/operator failed to ensure that when performing SPA that independent protection layers for each failure scenario were independent of each other and of initiating causes. CORRECTIVE ACTION: Owner/operator will prepare or revise the SPA so it includes independent protection layers that are independent of each other and of the initiating causes and establish or revise written procedures to ensure that independent protection layers are independent of initiating causes, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010146 |  |  | Program level 4: Safeguard Protection Analysis - Methodology | Failure to ensure the SPA use a quantitative or semi-quantitative method, such as Layer of Protection Analysis (LOPA) or an equally effective method. Failure to ensure the risk reduction obtainable by each IPL is based on site-specific failure rate data, or in the absence of such data, industry failure rate data for each device, system, or human factor. | 19 CCR 4.5 2762.2.1(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 158 | Program 4 Prevention Program | Safeguard Protection Analysis | Used quantitative, semi-quantitative SPA method, site-specific/industry standard failure rate used | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the SPA use a quantitative or semi-quantitative method, such as Layer of Protection Analysis (LOPA) or an equally effective method. Failure to ensure the risk reduction obtainable by each IPL is based on site-specific failure rate data, or in the absence of such data, industry failure rate data for each device, system, or human factor. |  |  | OBSERVATION: Owner/operator failed to ensure that the SPA used a quantitative method such as Layer of Protection Analysis or an equally effective method. Owner/Operator failed to ensure the risk reduction obtainable by each IPL is based on site-specific failure rate date, or in absence of such date, industry failure rate date for each device, system, or human factor. CORRECTIVE ACTION: Owner/operator will ensure that a quantitative or semiquantitative method such as Layer of Protection Analysis or an equally effective method is used to ensure risk reduction obtainable by each IPL is based on site specific failure rate data or in absence of this data, industry failure rate date for each device, system, human factor, and provide documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010147 |  |  | Program level 4: Safeguard Protection Analysis - Completion Timeline | Failure to complete all SPAs for the PHA within six (6) months of completion of the PHA. | 19 CCR 4.5 2762.2.1(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 159 | Program 4 Prevention Program | Safeguard Protection Analysis | SPAs completed for the PHA within six-months of completion of the PHA | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete all SPAs for the PHA within six (6) months of completion of the PHA. |  |  | OBSERVATION: Owner/operator failed to ensure that SPAs for the PHA were completed within six (6) months of completion of the PHA. CORRECTIVE ACTION: Owner/operator will ensure that SPAs for the PHA are completed within six (6) months of completion of the PHA, establish or revise a written procedure to ensure that the SPA are completed within the six month time period of PHA completion, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010148 |  |  | Program level 4: Safeguard Protection Analysis - Team Qualifications | Failure to ensure SPA is performed by a team with expertise in engineering and process operations and the team include at least one operating employee who has experience and knowledge specific to the process being evaluated. Failure to ensure the team also include one member knowledgeable in the specific SPA methodology being used. Failure to ensure the team consult with individuals with expertise in damage mechanisms, process chemistry, or an engineer specializing in controls systems and instrumentation, as necessary. Failure to provide for employee participation in this process, pursuant to section 2762.10. | 19 CCR 4.5 2762.2.1(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 160 | Program 4 Prevention Program | Safeguard Protection Analysis | SPA team has expertise in engineering, process operations, & employee as required | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure SPA is performed by a team with expertise in engineering and process operations and the team include at least one operating employee who has experience and knowledge specific to the process being evaluated. Failure to ensure the team also include one member knowledgeable in the specific SPA methodology being used. Failure to ensure the team consult with individuals with expertise in damage mechanisms, process chemistry, or an engineer specializing in controls systems and instrumentation, as necessary. Failure to provide for employee participation in this process, pursuant to section 2762.10. |  |  | OBSERVATION: Owner/operator failed to ensure that SPA is performed by a team with expertise in engineering and process operations that includes at least one operating employee who has experience and knowledge specific to the process being evaluated, one member knowledgeable in specific SPA methodology being used, consult with individuals in damage mechanisms, process chemistry, controls, instrumentation, and have employee participation. CORRECTIVE ACTION: Owner/operator will ensure that SPA is performed by a team with expertise in engineering, process operation including one operating employee who has experience and knowledge specific to the process being evaluated, one member knowledgeable in specific SPA methodology being used, consult with individuals with expertise in damage mechanisms, process chemistry, control systems, instrumentation, include employee participation, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010149 |  |  | Program level 4: Safeguard Protection Analysis - Team Documentation Requirements | Failure to ensure the SPA team documents the following: (1) potential initiating events and their likelihood and possible consequences, including equipment failures, human errors, loss of flow control, loss of pressure control, loss of temperature control, loss of level control, excess reaction or other conditions that may lead to a loss of containment; (2) the risk reduction achieved by each IPL for each initiating event; (3) necessary maintenance and testing to ensure that all IPLs function as designed; and (4) recommendations to address any deficiencies identified by the SPA. | 19 CCR 4.5 2762.2.1(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 161 | Program 4 Prevention Program | Safeguard Protection Analysis | SPA team documented initiating events, risk reduction of IPLs, maintenance needed, recommendations | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the SPA team documents the following: (1) potential initiating events and their likelihood and possible consequences, including equipment failures, human errors, loss of flow control, loss of pressure control, loss of temperature control, loss of level control, excess reaction or other conditions that may lead to a loss of containment; (2) the risk reduction achieved by each IPL for each initiating event; (3) necessary maintenance and testing to ensure that all IPLs function as designed; and (4) recommendations to address any deficiencies identified by the SPA. |  |  | OBSERVATION: Owner/operator failed to ensure the SPA team documents initiating events, likelihood, consequences including equipment failures, human errors, loss of flow control, loss of pressure control, loss of temperature control, loss of level control, excess reaction, loss of containment, risk reduction of IPL for each initiating event, maintenance & testing of each IPL so all IPLs function as designed, & recommendations for deficiencies identified by the SPA. CORRECTIVE ACTION: Owner/operator will ensure that SPA team documents potential initiating events: the likelihood, possible consequences as specified in 2762.2.1(f); the risk reduction achieved by each IPL for each initiating event; necessary maintenance and testing that the IPLs function as designed; recommendations to address any deficiencies identified by Safeguard Protection Analysis by revising deficient SPA documents, establishing or revising written procedures, and providing documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010150 |  |  | Program level 4: Safeguard Protection Analysis - Recommendations Annex | Failure to append the SPA findings and recommendations to the PHA report. | 19 CCR 4.5 2762.2.1(g) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 162 | Program 4 Prevention Program | Safeguard Protection Analysis | Ensured SPA findings and recommendations are appended to PHA report | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to append the SPA findings and recommendations to the PHA report. |  |  | OBSERVATION: Owner/operator failed to append the SPA findings and recommendations to the PHA report. CORRECTIVE ACTION: Owner/operator will ensure that SPA findings and recommendations are appended to the PHA report by revising the PHA report to include the SPA findings and recommendations, establishing or revising written procedures on SPA preparation, and submit documentation to UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010151 |  |  | Program level 4: Safeguard Protection Analysis - Corrective Action Work Process | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the SPA team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. | 19 CCR 4.5 2762.2.1(h) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 163 | Program 4 Prevention Program | Safeguard Protection Analysis | Used corrective action process for SPA teams findings & recommendations | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the SPA team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. |  |  | OBSERVATION: Owner/operator failed to follow the corrective action work process documented in subsections 2762.16(d) and (e) when resolving the PHA team's findings and recommendations, determining action items for implementation, tracking completion, and documentation of closeout. CORRECTIVE ACTION: Owner/operator will establish or revise written procedures to ensure they follow the corrective action work process documented specified subsections 2762.16(d) and (e) when resolving PHA team's finding and recommendations, determining action items for implementation, tracking completion dates, and documentation of closeout, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010152 |  |  | Program level 4: Safeguard Protection Analysis - Retention | Failure to retain all SPA documentation for the life of the process. | 19 CCR 4.5 2762.2.1(i) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 164 | Program 4 Prevention Program | Safeguard Protection Analysis | Retained SPA documentation for the life of the process | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain all SPA documentation for the life of the process. |  |  | OBSERVATION: Owner/operator failed to retain all SPA documentation for the life of the process. CORRECTIVE ACTION: Owner/operator will establish or revise written procedures to ensure SPA documentation is retained for the life of the process, will prepare a revised SPA for the process, and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010153 |  |  | Program level 4: Operating Procedures - General | Failure to develop and implement effective written operating procedures with clear instructions for safely conducting activities involved in each process with the process safety information. | 19 CCR 4.5 2762.3(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 165 | Program 4 Prevention Program | Operating Procedures | Developed and implemented clear and effective SOPS for safe operations of the process based on PSI | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement effective written operating procedures with clear instructions for safely conducting activities involved in each process with the process safety information. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information. CORRECTIVE ACTION: Develop and implement written operating procedures that provide clear instructions for safely conducting activities involved in each covered process consistent with the process safety information and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010154 |  |  | Program level 4: Operating Procedures -Steps for each Operating Phase | Failure to develop and implement written operating procedures that address the steps for each operating phase or mode of operation: (A) Startup; (B) Normal operations; (C) Temporary operations as the need arises; (D) Emergency shutdown, including the conditions under which emergency shutdown is required, provisions granting the authority of the qualified operator to shut down the operation or process, and the assignment of responsibilities to qualified operators in order to ensure that emergency shutdown is executed in a safe and timely manner; (E) Normal shutdown; and, (F) Startup following a turnaround, a planned or unplanned shutdown, or after an emergency shutdown. | 19 CCR 4.5 2762.3(a)(1) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 166 | Program 4 Prevention Program | Operating Procedures | Developed and implemented written SOPs that address the steps of each phase or mode of operation | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement written operating procedures that address the steps for each operating phase or mode of operation: (A) Startup; (B) Normal operations; (C) Temporary operations as the need arises; (D) Emergency shutdown, including the conditions under which emergency shutdown is required, provisions granting the authority of the qualified operator to shut down the operation or process, and the assignment of responsibilities to qualified operators in order to ensure that emergency shutdown is executed in a safe and timely manner; (E) Normal shutdown; and, (F) Startup following a turnaround, a planned or unplanned shutdown, or after an emergency shutdown. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address: initial startup; normal operations; temporary operations; emergency shutdown including the conditions under which emergency shutdown is required, and the assignment of shutdown responsibility to qualified operators to ensure that emergency shutdown is executed in a safe and timely manner; emergency operations; normal shutdown; startup following a turnaround, or after an emergency shutdown. CORRECTIVE ACTION: Develop, implement and submit copies of written operating procedures that address the deficiencies noted above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010155 |  |  | Program level 4: Operating Procedures - Operating Limits | Failure to develop and implement written operating procedures that address the operating limits: (A) Consequences of deviation(s); and, (B) Steps required to correct or avoid deviation(s). | 19 CCR 4.5 2762.3(a)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 167 | Program 4 Prevention Program | Operating Procedures | Developed & implemented SOPS that address consequences of deviation & corrective actions/avoidance | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement written operating procedures that address the operating limits: (A) Consequences of deviation(s); and, (B) Steps required to correct or avoid deviation(s). |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address the consequences of deviation and the steps required to correct or avoid the deviation. CORRECTIVE ACTION: Develop and implement written operating procedures that address the consequences of deviation and the steps required to correct or avoid the deviation/ and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010156 |  |  | Program level 4: Operating Procedures - Safety and Health Considerations | Failure to develop and implement written operating procedures that address safety and health considerations: (A) Properties of, and hazards presented by, the chemicals used in the process; (B) Precautions necessary to prevent exposure, including passive, active and procedural safeguards; and personal protective equipment; (C) Protective measures to be taken if physical contact or inhalation exposure occurs; (D) Safety procedures for opening process equipment; (E) Verification of the composition and properties of raw materials and control of hazardous chemical inventory levels; and, (F) Any special or unique hazards. | 19 CCR 4.5 2762.3(a)(3) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 168 | Program 4 Prevention Program | Operating Procedures | Developed & implemented SOPS that address safety & health considerations | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement written operating procedures that address safety and health considerations: (A) Properties of, and hazards presented by, the chemicals used in the process; (B) Precautions necessary to prevent exposure, including passive, active and procedural safeguards; and personal protective equipment; (C) Protective measures to be taken if physical contact or inhalation exposure occurs; (D) Safety procedures for opening process equipment; (E) Verification of the composition and properties of raw materials and control of hazardous chemical inventory levels; and, (F) Any special or unique hazards. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address: properties of, and hazards presented by, the chemicals used in the process; precautions necessary to prevent exposure, including engineering controls, administrative controls, and personal protective equipment; control measures to be taken if physical contact or airborne exposure occurs; quality control for raw materials and control of hazardous chemical inventory levels; any special or unique hazards. CORRECTIVE ACTION: Develop, implement, and submit copy of written operating procedures that address the deficiencies noted above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010157 |  |  | Program level 4: Operating Procedures - Safety Systems and their Functions | Failure to develop and implement written operating procedures that address safety systems and their functions. | 19 CCR 4.5 2762.3(a)(4) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 169 | Program 4 Prevention Program | Operating Procedures | Developed and implemented SOPS that address safety systems and their functions | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement written operating procedures that address safety systems and their functions. |  |  | OBSERVATION: The owner/operator failed to develop and implement written operating procedures that address safety systems and their functions. CORRECTIVE ACTION: Develop and implement written operating procedures that address safety systems and their functions and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010158 |  |  | Program level 4: Operating Procedures - Emergency Operations | Failure to ensure operating procedures include emergency operations for each process, including any response to the over-pressurizing or overheating of equipment or piping, and the handling of leaks, spills, releases and discharges. Failure to ensure operating procedures are consistent with the procedures developed as required by subsection 2762.3 (a)(1)(D) and to provide that only qualified operators may initiate these operations and that prior to allowing employees in the vicinity of a leak, release or discharge, at a minimum do one of the following: (1) Shutdown and depressurize all process operations where a leak, release or discharge is occurring; or(2) Isolate any vessel, piping, and equipment where a leak, spill or discharge is occurring; or (3) Follow established criteria for handling leaks, spills, or discharges that are designed to provide a level of protection that is functionally equivalent to, or safer than, shutting down or isolating the process. | 19 CCR 4.5 2762.3(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 170 | Program 4 Prevention Program | Operating Procedures | Ensured that SOPS include emergency operations for each process | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure operating procedures include emergency operations for each process, including any response to the over-pressurizing or overheating of equipment or piping, and the handling of leaks, spills, releases and discharges. Failure to ensure operating procedures are consistent with the procedures developed as required by subsection 2762.3 (a)(1)(D) and to provide that only qualified operators may initiate these operations and that prior to allowing employees in the vicinity of a leak, release or discharge, at a minimum do one of the following: (1) Shutdown and depressurize all process operations where a leak, release or discharge is occurring; or(2) Isolate any vessel, piping, and equipment where a leak, spill or discharge is occurring; or (3) Follow established criteria for handling leaks, spills, or discharges that are designed to provide a level of protection that is functionally equivalent to, or safer than, shutting down or isolating the process. |  |  | OBSERVATION: The owner/operator failed to ensure that SOPS include emergency operations for each process to include any response to the over pressurizing or overheating of equipment or piping, and the handling of leaks, spills, releases and discharges performed by a qualified operator to initiate at a minimum of the following operations: (1) Shutdown and depressurize all process operations where a leak, release or discharge is occurring; or (2) Isolate any vessel, piping, and equipment where a leak, spill or discharge is occurring; or (3) Follow established criteria for handling leaks, spills, or discharges that are designed to provide a level of protection that is functionally equivalent to, or safer than, shutting down or isolating the process. CORRECTIVE ACTION: Develop and implement written SOPS to include emergency operations for each process meeting the requirements of this section 2762.3(b) and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010159 |  |  | Program level 4: Operating Procedures - Accessibility | Failure to ensure a copy of the operating procedures is readily accessible to employees who work in or near the process area and to any other person who works in or near the process area or who maintains a process. | 19 CCR 4.5 2762.3(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 171 | Program 4 Prevention Program | Operating Procedures | Ensured SOPS are readily accessible to employees who work near or maintains process area | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure a copy of the operating procedures is readily accessible to employees who work in or near the process area and to any other person who works in or near the process area or who maintains a process. |  |  | OBSERVATION: The owner/operator failed to make operating procedures readily accessible to employees who work in or maintain a process. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating operating procedures are readily accessible to employees who work in or maintain a process. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010160 |  |  | Program level 4: Operating Procedures - Review, MOC, Certification | Failure to review and update the operating procedures as often as necessary to ensure that they reflect current safe operating practices. Failure to ensure operating procedures include any changes that result from alterations in process chemicals, technology, personnel, process equipment, or other changes to the stationary source. Failure to ensure changes to operating procedures are managed in accordance with the MOC requirements in section 2762.6. Failure to certify annually that operating procedures are current and accurate. | 19 CCR 4.5 2762.3(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 172 | Program 4 Prevention Program | Operating Procedures | Reviewed and certified SOPS at least annually to reflect all current operations are correct | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to review and update the operating procedures as often as necessary to ensure that they reflect current safe operating practices. Failure to ensure operating procedures include any changes that result from alterations in process chemicals, technology, personnel, process equipment, or other changes to the stationary source. Failure to ensure changes to operating procedures are managed in accordance with the MOC requirements in section 2762.6. Failure to certify annually that operating procedures are current and accurate. |  |  | OBSERVATION: The owner/operator failed to review and update the operating procedures as often as necessary to ensure that they reflect current safe operating practices. Failed to ensure operating procedures include any changes that result from alterations in process chemicals, technology, personnel, process equipment, or other changes to the stationary source. Failed to ensure changes to operating procedures are managed in accordance with the MOC requirements in section 2762.6. Failed to certify annually that operating procedures are current and accurate. CORRECTIVE ACTION: Review and update the operating procedures to assure that they reflect current operating practice. Certify that the operating procedures are current and accurate and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010161 |  |  | Program level 4: Operating Procedures - Safe Work Practices | Failure to develop, implement, and maintain safe work practices to prevent or control hazards during specific activities, such as: 1. Opening process equipment or piping; 2. Tasks requiring lock-out/tag-out procedures; 3. Confined space entry; 4. Handling, controlling, and stopping leaks, spills, releases and discharges; and 5. Control over entry into hazardous work areas by maintenance, contractor, laboratory, or other support personnel. | 19 CCR 4.5 2762.3(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 173 | Program 4 Prevention Program | Operating Procedures | Developed and implemented safe work practices to provide control of hazards during operations | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement, and maintain safe work practices to prevent or control hazards during specific activities, such as: 1. Opening process equipment or piping; 2. Tasks requiring lock-out/tag-out procedures; 3. Confined space entry; 4. Handling, controlling, and stopping leaks, spills, releases and discharges; and 5. Control over entry into hazardous work areas by maintenance, contractor, laboratory, or other support personnel. |  |  | OBSERVATION: The owner/operator failed to develop and implement safe work practices to provide for the control of hazards during operations including: logout/tagout; confined space entry; opening process equipment or piping; and control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel. CORRECTIVE ACTION: Develop and implement safe work practices to provide for the control of hazards during operations including: logout/tagout; confined space entry; opening process equipment or piping; and control over entrance into the stationary source by maintenance, contractor, laboratory, or other support personnel and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020012 |  |  | Program level 4: Training - Initial | (1) Failure to train each employee involved in operating a process, and each operating employee prior to working in a newly assigned process, in an overview of the process and in the operating procedures as specified in section 2762.3. Failure to include material on the specific safety and health hazards applicable to the employee's job tasks, procedures, including emergency operations and shutdown, and safe work practices applicable to the employee's job tasks. (2) Failure to train each employee involved in maintaining the on-going integrity of process equipment in an overview of that process and its hazards and in the procedures applicable to the employee's job tasks to assure that the employee can perform the job tasks in a safe manner. | 19 CCR 4.5 2762.4(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 174 | Program 4 Prevention Program | Training | Trained employees involved in operating a process on requirements in Section 2762.4 | 83 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | (1) Failure to train each employee involved in operating a process, and each operating employee prior to working in a newly assigned process, in an overview of the process and in the operating procedures as specified in section 2762.3. Failure to include material on the specific safety and health hazards applicable to the employee's job tasks, procedures, including emergency operations and shutdown, and safe work practices applicable to the employee's job tasks. (2) Failure to train each employee involved in maintaining the on-going integrity of process equipment in an overview of that process and its hazards and in the procedures applicable to the employee's job tasks to assure that the employee can perform the job tasks in a safe manner. |  |  | OBSERVATION: The owner/operator failed to train each employee presently involved in operating a process, and each employee before being involved in operating a newly assigned process on the following: overview of the process; operating procedures; safety & health hazards; emergency operations including shutdown; safe work practices applicable to the employee's job tasks. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating each employee presently involved in operating a process has been trained on the following: overview of the process; operating procedures; safety & health hazards; emergency operations including shutdown; safe work practices applicable to the employee's job tasks. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020013 |  |  | Program level 4: Training - Refresher and Supplemental | (1) Failure to ensure at least once every three years, and more often if necessary, refresher and supplemental training is provided to each employee involved in operating a process in order to ensure the employee understands and adheres to the current operating procedures of the process. Failure to determine the appropriate frequency and content of refresher training, in consultation with the employees involved in operating the process. (2) Failure to provide effective refresher and supplemental training at least once every three years, and more often if necessary, to each maintenance employee to ensure that each employee understands and adheres to current maintenance procedures. | 19 CCR 4.5 2762.4(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 175 | Program 4 Prevention Program | Training | Performed effective refresher training at least every 3 years or more often if necessary | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | (1) Failure to ensure at least once every three years, and more often if necessary, refresher and supplemental training is provided to each employee involved in operating a process in order to ensure the employee understands and adheres to the current operating procedures of the process. Failure to determine the appropriate frequency and content of refresher training, in consultation with the employees involved in operating the process. (2) Failure to provide effective refresher and supplemental training at least once every three years, and more often if necessary, to each maintenance employee to ensure that each employee understands and adheres to current maintenance procedures. |  |  | OBSERVATION: The owner/operator failed to effectively train employees in operating a process in order to ensure employee understands and adheres to the current operating/maintenance procedures of the process at least once every 3 years or as often as necessary. CORRECTIVE ACTION: Conduct training and provide documentation to CUPA that employees understand and adheres to current operating/maintenance procedures of the process and establishes consistent training frequency at least every 3 years or as often as necessary. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020014 |  |  | Program level 4: Training - Certification Record | Failure to ensure that each employee involved in operating a process has received, understood and successfully completed training as specified by section 2762.4. Failure to prepare, after the initial or refresher training, a certification record containing the identity of the employee, the date(s) of training, the means used to verify that the employee understood the training, and the signature(s) of the person administering the training. | 19 CCR 4.5 2762.4(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 176 | Program 4 Prevention Program | Training | Documented training records identifying employee, training date, & verification of competency | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that each employee involved in operating a process has received, understood and successfully completed training as specified by section 2762.4. Failure to prepare, after the initial or refresher training, a certification record containing the identity of the employee, the date(s) of training, the means used to verify that the employee understood the training, and the signature(s) of the person administering the training. |  |  | OBSERVATION: The owner/operator failed to prepare a certification record containing the identity of the employee, the date(s) of training, the means used to verify that the employee understood the training, and the signature(s) of the person administering the training. CORRECTIVE ACTION: Establish record keeping forms to meet the requirements of this section, perform training, and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020015 |  |  | Program level 4: Training - Requirements and Testing | Failure to develop and implement an effective written program that includes (1) the requirements that an employee must meet in order to be designated as qualified, and (2) employee testing procedures to verify understanding and to ensure competency in job skill levels and work practices that protect employee and public safety and health. | 19 CCR 4.5 2762.4(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 177 | Program 4 Prevention Program | Training | Developed and implemented qualifications/competency program for designated employees | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement an effective written program that includes (1) the requirements that an employee must meet in order to be designated as qualified, and (2) employee testing procedures to verify understanding and to ensure competency in job skill levels and work practices that protect employee and public safety and health. |  |  | OBSERVATION: The owner/operator failed to develop and implement an effective written program that includes (1) the requirements that an employee must meet in order to be designated as qualified, and (2) employee testing procedures to verify understanding and to ensure competency in job skill levels and work practices that protect employee and public safety and health. CORRECTIVE ACTION: Develop and implement and effective written program that meet the requirements of this section and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020016 |  |  | Program level 4: Training - Program 4 Elements | Failure to develop and implement an effective training program to ensure that all affected employees are aware of and understand all Program 4 elements described in Article 6.5. Failure to complete the initial training required in section 2762.4 within twenty-four (24) months following the effective date of section 2762.4. Employees and employee representatives participating in a specialized team pursuant to 2762.13 shall be trained in the Program elements relevant to that team. | 19 CCR 4.5 2762.4(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 178 | Program 4 Prevention Program | Training | Developed, implemented, and completed initial/refresher training for program 4 elements | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement an effective training program to ensure that all affected employees are aware of and understand all Program 4 elements described in Article 6.5. Failure to complete the initial training required in section 2762.4 within twenty-four (24) months following the effective date of section 2762.4. Employees and employee representatives participating in a specialized team pursuant to 2762.13 shall be trained in the Program elements relevant to that team. |  |  | OBSERVATION: The owner/operator failed to develop and implement an effective training program to ensure that all affected employees are aware of and understand all Program 4 elements described in Article 6.5 within 24 months of the effective date of section 2762.4. CORRECTIVE ACTION: Develop and implement training program and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Training | 5020017 |  |  | Program level 4: Training - Employee Participation | Failure to provide for employee participation in developing and implementing the training program, pursuant to section 2762.10. | 19 CCR 4.5 2762.4(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 179 | Program 4 Prevention Program | Training | Provided employee participation to develop and implement training program | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide for employee participation in developing and implementing the training program, pursuant to section 2762.10. |  |  | OBSERVATION: The owner/operator failed to provide employee participation in developing and implementing the training program per section 2762.10. CORRECTIVE ACTION: Establish employee participation program in developing and implementing training programs and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010162 |  |  | Program level 4: Mechanical Integrity - Written Procedures | Failure to develop, implement, and maintain effective written procedures to ensure the ongoing integrity of process equipment. (1) Failure to ensure the procedures provide clear instructions for safely conducting maintenance activities on process equipment, consistent with the Process Safety Information. (2) Failure to ensure the procedures and inspection documents developed under subsection 2762.5 are readily accessible to employees and employee representatives pursuant to section 2762.10. | 19 CCR 4.5 2762.5(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 180 | Program 4 Prevention Program | Mechanical Integrity | Developed, implemented, & maintained accessible SOPS on mechanical integrity/maintenance | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement, and maintain effective written procedures to ensure the ongoing integrity of process equipment. (1) Failure to ensure the procedures provide clear instructions for safely conducting maintenance activities on process equipment, consistent with the Process Safety Information. (2) Failure to ensure the procedures and inspection documents developed under subsection 2762.5 are readily accessible to employees and employee representatives pursuant to section 2762.10. |  |  | OBSERVATION: The owner/operator failed to develop, implement, and maintain effective written procedures to ensure the ongoing integrity of process equipment that provide clear instructions for safely conducting maintenance activities on process equipment, consistent with the Process Safety Information and are readily accessible to employees and employee representatives pursuant to section 2762.10. CORRECTIVE ACTION: Develop, implement, and maintain effective written procedures to ensure the ongoing integrity of process equipment that provide clear instructions for safely conducting maintenance activities on process equipment, consistent with the Process Safety Information and are readily accessible to employees and employee representatives pursuant to section 2762.10 and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Operations/Maintenance | 5030006 |  |  | Program level 4: Mechanical Integrity - Inspection and Testing | (1) Failure to ensure inspections and tests are performed on process equipment, using procedures that meet or exceed recognized and generally accepted good engineering practices (RAGAGEP). (2) Failure to ensure the frequency of inspections and tests of process equipment are consistent with (1) the applicable manufacturers' recommendations, (2) RAGAGEP, or (3) internal practices that are more protective than (1) or (2). Failure to ensure inspections and tests are conducted more frequently if necessary, based on the operating experience with the process equipment. (3) Failure to retain a certification record to document that each inspection and test has been performed in accordance with subsection 2762.5. Failure to ensure the certification record identifies the date of the inspection; the name of the person who performed the inspection or test; a description of the inspection or test performed; the results of the inspection or test; and the serial number or other identifier of the equipment on which the inspection or test was performed. | 19 CCR 4.5 2762.5(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 181 | Program 4 Prevention Program | Mechanical Integrity | Performed & documented inspections/tests per RAGAGEP/manufacturers/internal practices | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | (1) Failure to ensure inspections and tests are performed on process equipment, using procedures that meet or exceed recognized and generally accepted good engineering practices (RAGAGEP). (2) Failure to ensure the frequency of inspections and tests of process equipment are consistent with (1) the applicable manufacturers' recommendations, (2) RAGAGEP, or (3) internal practices that are more protective than (1) or (2). Failure to ensure inspections and tests are conducted more frequently if necessary, based on the operating experience with the process equipment. (3) Failure to retain a certification record to document that each inspection and test has been performed in accordance with subsection 2762.5. Failure to ensure the certification record identifies the date of the inspection; the name of the person who performed the inspection or test; a description of the inspection or test performed; the results of the inspection or test; and the serial number or other identifier of the equipment on which the inspection or test was performed. |  |  | OBSERVATION: The owner/operator failed to ensure frequency of inspections and tests are performed on process equipment per RAGAGP, manufacturer's recommendations, internal practices that are more protective, or are based on operating experience that is more frequent if necessary with retained certification of record to document that each inspection and test has been performed in accordance with subsection 2762.5. CORRECTIVE ACTION: Establish and implement program for inspections and tests performed on process equipment per RAGAGP, manufacturer's recommendations, internal practices that are more protective, or are based on operating experience that is more frequent if necessary with retained certification of record to document that each inspection and test has been performed in accordance with subsection 2762.5 and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Operations/Maintenance | 5030007 |  |  | Program level 4: Mechanical Integrity - Equipment Deficiencies | Failure to correct equipment deficiencies to ensure safe operation of process equipment. Failure to ensure repair methodologies are consistent with RAGAGEP or more protective internal practices. | 19 CCR 4.5 2762.5(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 182 | Program 4 Prevention Program | Mechanical Integrity | Corrected equipment deficiencies for safe operation of process equipment per RAGAGEP/higher | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to correct equipment deficiencies to ensure safe operation of process equipment. Failure to ensure repair methodologies are consistent with RAGAGEP or more protective internal practices. |  |  | OBSERVATION: The owner/operator failed to correct equipment deficiencies to ensure safe operation of process equipment consistent with repair methodologies that are consistent with RAGAGEP or more protective internal practices. CORRECTIVE ACTION: Correct equipment deficiencies to ensure safe operation of process equipment consistent with repair methodologies that are consistent with RAGAGEP or more protective internal practices and submit documentation to CUPA | [6 empty] | No | No | No | Yes
CalARP Program | Operations/Maintenance | 5030008 |  |  | Program level 4: Mechanical Integrity - Quality Assurance | (1) Failure to ensure that all process equipment at a minimum complies with the criteria established in subsection 2762.1(d). Failure to ensure that all process equipment is: (1) suitable for the process application for which it is or will be used; (2) fabricated from the proper materials of construction; (3) designed, constructed, installed, maintained, inspected, tested, operated and replaced in compliance with the manufacturer's and any other design specifications and all applicable codes and standards. (2) Failure to ensure and document newly installed process equipment or existing process equipment for which no RAGAGEP exists, are designed, built, installed, maintained, inspected, tested and operated in a safe manner. (3) Failure to conduct regularly scheduled checks and inspections as necessary to ensure that the requirements of paragraph (1) are met. (4) Failure to ensure that maintenance materials, spare parts and equipment meet design specifications and applicable codes. (5) Failure to establish a process for evaluating new or updated equipment codes and standards and implementing changes as appropriate to ensure safe operation. | 19 CCR 4.5 2762.5(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 183 | Program 4 Prevention Program | Mechanical Integrity | Complied with design specifications of codes/standards, RAGAGEP, or higher protective practices | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | (1) Failure to ensure that all process equipment at a minimum complies with the criteria established in subsection 2762.1(d). Failure to ensure that all process equipment is: (1) suitable for the process application for which it is or will be used; (2) fabricated from the proper materials of construction; (3) designed, constructed, installed, maintained, inspected, tested, operated and replaced in compliance with the manufacturer's and any other design specifications and all applicable codes and standards. (2) Failure to ensure and document newly installed process equipment or existing process equipment for which no RAGAGEP exists, are designed, built, installed, maintained, inspected, tested and operated in a safe manner. (3) Failure to conduct regularly scheduled checks and inspections as necessary to ensure that the requirements of paragraph (1) are met. (4) Failure to ensure that maintenance materials, spare parts and equipment meet design specifications and applicable codes. (5) Failure to establish a process for evaluating new or updated equipment codes and standards and implementing changes as appropriate to ensure safe operation. |  |  | OBSERVATION: The owner/operator failed to comply with one of more of the following: (1) Ensure that all process equipment, at a minimum, complies with the criteria established in subsection 2762.1(d), including, but not limited to, ensuring that all process equipment is: (a) suitable for the process application for which it is or will be used, (b) fabricated from the proper materials of construction, (c) designed, constructed, installed, maintained, inspected, tested, operated and replaced in compliance with the manufacturer's and any other design specifications and all applicable codes and standards; (2) Ensure and document that newly installed process equipment or existing process equipment for which no RAGAGEP exists, are designed, built, installed, maintained, inspected, tested and operated in a safe manner. (3) Conduct regularly scheduled checks and inspections as necessary to ensure that the requirements of paragraph (1) are met. (4) Ensure that maintenance materials, spare parts and equipment meet design specifications and applicable codes. (5) Establish a process for evaluating new or updated equipment codes and standards and implementing changes as appropriate to ensure safe operation. CORRECTIVE ACTION: Ensure that facility is in compliance with all requirements described above and provide documentation to CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010163 |  |  | Program level 4: Mechanical Integrity - Damage Mechanism Review | Failure to complete a Damage Mechanism Review (DMR) for each process for which a damage mechanism exists. Failure to document the rationale for the determination that no damage mechanism exists, where no DMR is performed. Failure to determine and document the priority order for conducting the DMR based on process operating history, PHA schedule and inspection records. Failure to complete no less than 50 percent of the initial DMRs within three (3) years of the effective date of Article 6.5, and the remainder within five (5) years of the effective date of Article 6.5. | 19 CCR 4.5 2762.5(e)(1) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 184 | Program 4 Prevention Program | Mechanical Integrity | Completed and documented DMR for each process within required time frames. | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete a Damage Mechanism Review (DMR) for each process for which a damage mechanism exists. Failure to document the rationale for the determination that no damage mechanism exists, where no DMR is performed. Failure to determine and document the priority order for conducting the DMR based on process operating history, PHA schedule and inspection records. Failure to complete no less than 50 percent of the initial DMRs within three (3) years of the effective date of Article 6.5, and the remainder within five (5) years of the effective date of Article 6.5. |  |  | OBSERVATION: The owner/operator failed to complete a DMR for each process for which a damage mechanism exists; document rationale for the determination that no damage mechanism exists, where no DMR is performed; or document the priority order for conducting the DMR based on operating history/PHA schedule/inspection records within the time frame specified within this section. CORRECTIVE ACTION: Complete DMR with appropriate documentation specified within this section for each process and provide to CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010164 |  |  | Program level 4: Mechanical Integrity - DMR Update | Failure to update a DMR at least once every five (5) years consistent with the requirements of Section 2762.5. | 19 CCR 4.5 2762.5(e)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 185 | Program 4 Prevention Program | Mechanical Integrity | Updated DMR at least once every 5 years | 39 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update a DMR at least once every five (5) years consistent with the requirements of Section 2762.5. |  |  | OBSERVATION: The owner/operator failed to update a DMR at least once every five (5) years consistent with the requirements of section 2762.5. CORRECTIVE ACTION: Update DMR and establish procedures to consistently update DMR at least once every five (5) years and submit to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010165 |  |  | Program level 4: Mechanical Integrity - DMR Review | Failure to review a DMR as part of a major change on a process for which a damage mechanism exists, prior to approval of the change. Failure to conduct a DMR for a major change that may introduce a damage mechanism, prior to approval of the change. Failure to review the most recent DMR(s) that are relevant to the investigation, as part of an incident investigation pursuant to section 2762.9, where a damage mechanism is identified as a contributing factor. Failure to conduct and complete a DMR prior to implementation of corrective actions pursuant to section 2762.16(d) and (e), where a DMR has not been performed on the processes that are relevant to the investigation. | 19 CCR 4.5 2762.5(e)(3) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 186 | Program 4 Prevention Program | Mechanical Integrity | Reviewed or conducted DMR for major change, if relevant to incident invest., or corrective action | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to review a DMR as part of a major change on a process for which a damage mechanism exists, prior to approval of the change. Failure to conduct a DMR for a major change that may introduce a damage mechanism, prior to approval of the change. Failure to review the most recent DMR(s) that are relevant to the investigation, as part of an incident investigation pursuant to section 2762.9, where a damage mechanism is identified as a contributing factor. Failure to conduct and complete a DMR prior to implementation of corrective actions pursuant to section 2762.16(d) and (e), where a DMR has not been performed on the processes that are relevant to the investigation. |  |  | OBSERVATION: Owner/operator failed to review a DMR as part of a major change on a process for which a damage mechanism exists or failed to conduct a DMR for a major change that may introduce a damage mechanism, prior to approval of the change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has reviewed and/or conducted the required DMRs as described above. | OBSERVATION: Owner/operator failed to review the most recent DMR(s) that are relevant to the investigation, as part of an incident investigation pursuant to Section 2762.9, where a damage mechanism is identified as a contributing factor. Owner/operator failed to conduct and complete a DMR prior to implementation of corrective actions pursuant to Section 2762.16(d) and (e), where a DMR has not been performed on the processes that are relevant to the investigation. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has conducted the required DMRs as described above. | [5 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010166 |  |  | Program level 4: Mechanical Integrity - DMR Availability | Failure to ensure the DMR for a process unit is available to the team performing a PHA for that process unit. | 19 CCR 4.5 2762.5(e)(4) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 187 | Program 4 Prevention Program | Mechanical Integrity | Ensured that DMR for a process unit was available to the team performing PHA for that unit | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the DMR for a process unit is available to the team performing a PHA for that process unit. |  |  | OBSERVATION: Owner/operator failed to make the DMR for a process unit available to the team performing a PHA for that process unit. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the owner/operator will ensure that DMRs will be available when performing a PHA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010167 |  |  | Program level 4: Mechanical Integrity - Team Qualifications | Failure to ensure the DMR is performed by a team with expertise in engineering, operation of the processes under review, equipment and pipe inspection, and damage and failure mechanisms. Failure to ensure the team also includes one member knowledgeable in the specific DMR method being used. Failure to provide for employee participation in this process, pursuant to section 2762.10. | 19 CCR 4.5 2762.5(e)(5) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 188 | Program 4 Prevention Program | Mechanical Integrity | DMR(s) were conducted by a team with appropriate expertise and employee participation was addressed | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the DMR is performed by a team with expertise in engineering, operation of the processes under review, equipment and pipe inspection, and damage and failure mechanisms. Failure to ensure the team also includes one member knowledgeable in the specific DMR method being used. Failure to provide for employee participation in this process, pursuant to section 2762.10. |  |  | OBSERVATION: Owner/operator failed to ensure the following: the DMR was performed by a team with expertise in engineering, process operation (specific to the process under review), equipment and pipe inspection, damage and failure mechanisms; the team performing the DMR included one member knowledgeable in the specific DMR method being used; provided for employee participation in the DMR process, pursuant to section 2762.10. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has corrected the deficiencies noted above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010168 |  |  | Program level 4: Mechanical Integrity - DMR Elements | Failure to ensure the DMR for each process unit includes: (A) Assessment of Process Flow Diagrams (PFDs); (B) Identification of all potential damage mechanisms pursuant to subsection 2762.5 (e)(7) ; (C) Determination that the materials of construction are appropriate for their application and are resistant to potential damage mechanisms; (D) A discussion of the conditions that cause the damage mechanism and how rapidly the damage may progress; (E) Methods to prevent or mitigate damage; (F) Review of operating parameters to identify operating conditions that could accelerate damage or that could minimize or eliminate damage | 19 CCR 4.5 2762.5(e)(6) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 189 | Program 4 Prevention Program | Mechanical Integrity | DMRs include PFD assess, pot. damage mech's, mat's of construction, causal conditions, prevention | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the DMR for each process unit includes: (A) Assessment of Process Flow Diagrams (PFDs); (B) Identification of all potential damage mechanisms pursuant to subsection 2762.5 (e)(7) ; (C) Determination that the materials of construction are appropriate for their application and are resistant to potential damage mechanisms; (D) A discussion of the conditions that cause the damage mechanism and how rapidly the damage may progress; (E) Methods to prevent or mitigate damage; (F) Review of operating parameters to identify operating conditions that could accelerate damage or that could minimize or eliminate damage |  |  | OBSERVATION: Owner/operator failed to ensure that DMRs for each process unit includes: an assessment of Process Flow Diagrams (PFDs); identification of all potential damage mechanisms pursuant to subsection 2762.5(e)(7); determination that the materials of construction are appropriate for their application and are resistant to potential damage mechanisms; a discussion of the conditions that cause the damage mechanism and how rapidly the damage may progress; methods to prevent or mitigate damage; a review of operating parameters to identify operating conditions that could accelerate damage or that could minimize or eliminate damage. CORRECTION ACTION: Submit documentation to the UPA demonstrating the owner/operator has included the items listed above in each DMR. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010169 |  |  | Program level 4: Mechanical Integrity - Damage Mechanism Types | Failure to ensure damage mechanisms, for the purposes of section 2762.5, include, but are not limited to; (A) Mechanical loading failures, such as ductile fracture, brittle fracture, mechanical fatigue, and buckling; (B) Erosion, such as abrasive wear, adhesive wear, and fretting; (C) Corrosion, such as uniform corrosion, localized corrosion, and pitting; (D) Thermal-related failures, such as creep, metallurgical transformation, and thermal fatigue; (E) Cracking, such as stress-corrosion cracking; and (F) Embrittlement, such as high-temperature hydrogen attack. | 19 CCR 4.5 2762.5(e)(7) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 190 | Program 4 Prevention Program | Mechanical Integrity | DMRs include mech. load failure, erosion, corrosion, thermal issues, cracking, and embrittlement | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure damage mechanisms, for the purposes of section 2762.5, include, but are not limited to; (A) Mechanical loading failures, such as ductile fracture, brittle fracture, mechanical fatigue, and buckling; (B) Erosion, such as abrasive wear, adhesive wear, and fretting; (C) Corrosion, such as uniform corrosion, localized corrosion, and pitting; (D) Thermal-related failures, such as creep, metallurgical transformation, and thermal fatigue; (E) Cracking, such as stress-corrosion cracking; and (F) Embrittlement, such as high-temperature hydrogen attack. |  |  | OBSERVATION: Owner/operator failed to ensure that the following damage mechanisms, for the purposes of Section 2762.5, include at a minimum: mechanical loading failures,; erosion; corrosion; pitting; thermal-related failures; cracking; and embrittlement. CORRECTIVE ACTION Submit documentation to the UPA demonstrating the owner/operator has addressed the damage mechanisms above in each DMR. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010170 |  |  | Program level 4: Mechanical Integrity - DMR Assessment | Failure to ensure DMRs include: 1. An assessment of previous experience with the process including the inspection history and all damage mechanism data; 2. A review of industry-wide experience with the process; and 3. Applicable standards, codes and practices. | 19 CCR 4.5 2762.5(e)(8) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 191 | Program 4 Prevention Program | Mechanical Integrity | DMRs included previous inspection data, industry data, and applicable standards, codes and practices | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure DMRs include: 1. An assessment of previous experience with the process including the inspection history and all damage mechanism data; 2. A review of industry-wide experience with the process; and 3. Applicable standards, codes and practices. |  |  | OBSERVATION: Owner/operator failed to ensure DMRs include an assessment of previous experience with the process including inspection history and all damage mechanism data; a review of industry-wide experience with the process; and applicable standards, codes and practices. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has included the items listed above in each DMR. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010171 |  |  | Program level 4: Mechanical Integrity - DMR Report | Failure to ensure the team prepare a written DMR, at the conclusion of the analysis, that includes; (A) The process unit(s) reviewed; (B) Damage mechanisms analyzed; (C) Results of the analyses conducted according to subsection 2762.5 (e)(7); (D) Recommendations for temporary mitigation; (E) Recommendations for prevention. | 19 CCR 4.5 2762.5(e)(9) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 192 | Program 4 Prevention Program | Mechanical Integrity | Developed a complete written DMR report | 39 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the team prepare a written DMR, at the conclusion of the analysis, that includes; (A) The process unit(s) reviewed; (B) Damage mechanisms analyzed; (C) Results of the analyses conducted according to subsection 2762.5 (e)(7); (D) Recommendations for temporary mitigation; (E) Recommendations for prevention. |  |  | OBSERVATION: Owner/operator failed to prepare a written DMR that includes: the process unit(s) reviewed; damage mechanisms analyzed; results of the analyses conducted according to subsection 2762.5(e)(7); recommendations for temporary mitigation; recommendations for prevention. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has included the items listed above in each DMR. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010172 |  |  | Program level 4: Mechanical Integrity - DMR Report Review | Failure to provide and, upon request, review the report with all operating, maintenance, and other personnel, whose work assignments are within the process unit covered in the DMR. | 19 CCR 4.5 2762.5(e)(10) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 193 | Program 4 Prevention Program | Mechanical Integrity | DMRs provided to and/or reviewed with personnel working in the process covered by the DMRs | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide and, upon request, review the report with all operating, maintenance, and other personnel, whose work assignments are within the process unit covered in the DMR. |  |  | OBSERVATION: Owner/operator failed to provide and, upon request, review the DMR reports with all operating, maintenance, and other personnel whose work assignments are within the process unit. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has shared the DMR reports with personnel whose work assignments are within the applicable process units. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010173 |  |  | Program level 4: Mechanical Integrity - Corrective Action Work Process | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the DMR team's findings and recommendations, determining corrective action for implementation, tracking to completion, and documentation of closeout. | 19 CCR 4.5 2762.5(e)(11) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 194 | Program 4 Prevention Program | Mechanical Integrity | Followed corrective action work process for resolving DMR team recommendations, tracking, & closeout | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the DMR team's findings and recommendations, determining corrective action for implementation, tracking to completion, and documentation of closeout. |  |  | OBSERVATION: Owner/operator failed to follow the corrective action work process documented in subsections 2762.16(d-e) when resolving the DMR team's findings and recommendations, determining corrective action for implementation, tracking to completion, and documentation of closeout. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating the owner/operator has complied with the items listed above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010174 |  |  | Program level 4: Mechanical Integrity - DMR Retention | Failure to retain DMR reports for the life of the process unit. | 19 CCR 4.5 2762.5(e)(12) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 195 | Program 4 Prevention Program | Mechanical Integrity | Retained DMR reports for the life of the process unit | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain DMR reports for the life of the process unit. |  |  | OBSERVATION: Owner/operator failed to retain DMR reports for the life of the process unit. CORRECTIVE ACTION: Obtain the missing DMRs for each covered process as well as the documented resolution of recommendations for the life of the process and submit a copy to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010175 |  |  | Program level 4: Management of Change - Written Procedures | Failure to develop, implement and maintain effective written Management of Change (MOC) procedures to manage changes in process chemicals, technology, procedures, process equipment, and facilities. Failure to also develop, implement and maintain written Management of Organizational Change (MOOC) procedures to manage changes in personnel or organizational issues. The MOC procedure shall include provisions for temporary repairs, including temporary piping or equipment repairs. | 19 CCR 4.5 2762.6(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 196 | Program 4 Prevention Program | Management of Change | Developed, implemented and maintained effective written MOC and MOOC procedures | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement and maintain effective written Management of Change (MOC) procedures to manage changes in process chemicals, technology, procedures, process equipment, and facilities. Failure to also develop, implement and maintain written Management of Organizational Change (MOOC) procedures to manage changes in personnel or organizational issues. The MOC procedure shall include provisions for temporary repairs, including temporary piping or equipment repairs. |  |  | OBSERVATION: Owner/operator failed to develop, implement and maintain effective written MOC procedures to manage changes in process chemicals, technology, procedures, process equipment, facilities, and temporary repairs including temporary piping or equipment repairs. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating effective written MOC procedures which address the items listed above. | OBSERVATION: Owner/operator failed to develop, implement and maintain effective written MOOC procedure to manage changes in personnel or organizational issues. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating an effective written MOOC procedure. | [5 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010176 |  |  | Program level 4: Management of Change - Criteria | Failure to ensure the MOC procedures address and document the following items prior to any change: (1) The technical basis for the proposed change;(2) Potential process safety impacts of the change; (3) Modifications to operating and maintenance procedures or development of new operating and maintenance procedures; (4) The time period required for the change; and (5) Authorization requirements for the proposed change. | 19 CCR 4.5 2762.6(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 197 | Program 4 Prevention Program | Management of Change | MOC procedures addressed and documented the required items prior to any change | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the MOC procedures address and document the following items prior to any change: (1) The technical basis for the proposed change;(2) Potential process safety impacts of the change; (3) Modifications to operating and maintenance procedures or development of new operating and maintenance procedures; (4) The time period required for the change; and (5) Authorization requirements for the proposed change. |  |  | OBSERVATION: Owner/operator failed to ensure the MOC procedures address and document the following items prior to any change: technical basis for the proposed change, potential process safety impacts of the change, modifications to operating and maintenance procedures or development of new operating and maintenance procedures, the time period required for the change, and authorization requirements for the proposed change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the MOC procedure has been revised to require the items listed above to be addressed and documented. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010177 |  |  | Program level 4: Management of Change - DMR and HCA | Failure to review or conduct a DMR pursuant to subsection 2762.5(e), and perform a Hierarchy of Hazard Control Analysis (HCA) pursuant to section 2762.13, prior to implementation of a major change. Failure to include the findings of the DMR and recommendations of the HCA in the MOC documentation. | 19 CCR 4.5 2762.6(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 198 | Program 4 Prevention Program | Management of Change | DMR reviewed and HCA conducted before a major change implementation with documented recommendations | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to review or conduct a DMR pursuant to subsection 2762.5(e), and perform a Hierarchy of Hazard Control Analysis (HCA) pursuant to section 2762.13, prior to implementation of a major change. Failure to include the findings of the DMR and recommendations of the HCA in the MOC documentation. |  |  | OBSERVATION: Owner/operator failed to review or conduct a DMR and/or HCA prior to implementation of a major change and include the findings of the DMR and recommendations of the HCA in the MOC documentation. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the appropriate DMRs and HCAs were conducted for each major change and that the findings of the DMRs and recommendations of the HCAs were included in the MOC documentation. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010178 |  |  | Program level 4: Management of Change - Qualified Personnel and Appropriate Methods | Failure to use qualified personnel and appropriate methods for MOCs based upon hazard, complexity and type of change. | 19 CCR 4.5 2762.6(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 199 | Program 4 Prevention Program | Management of Change | Qualified personnel and appropriate methods used in MOCs | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to use qualified personnel and appropriate methods for MOCs based upon hazard, complexity and type of change. |  |  | OBSERVATION: Owner/operator failed to use qualified personnel and appropriate methods for MOCs based on hazard, complexity and type of change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that deficient MOCs were reevaluated by qualified personnel and used the appropriate methods based on the hazard, complexity and type of change. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010179 |  |  | Program level 4: Management of Change - Employee Participation | Failure to provide for employee participation, pursuant to section 2762.10. | 19 CCR 4.5 2762.6(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 200 | Program 4 Prevention Program | Management of Change | Provided for employee participation in the MOC process | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide for employee participation, pursuant to section 2762.10. |  |  | OBSERVATION: Owner/operator failed to provide for employee participation in the MOC process. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that deficient MOCs were reevaluated with employee participation. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010180 |  |  | Program level 4: Management of Change - Training | Failure to ensure employees involved in the process as well as maintenance workers whose job tasks will be affected by a change, are informed of, and effectively trained in the change in a timely manner, prior to implementation of the change. Failure to make the MOC documentation available to and require effective training in the change prior to implementation of the change, pursuant to section 2762.12, for contractors and employees of contractors who are operating the process and whose job tasks are affected by a change. | 19 CCR 4.5 2762.6(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 201 | Program 4 Prevention Program | Management of Change | Affected employees/contractors informed of and trained on process changes prior to implementation | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure employees involved in the process as well as maintenance workers whose job tasks will be affected by a change, are informed of, and effectively trained in the change in a timely manner, prior to implementation of the change. Failure to make the MOC documentation available to and require effective training in the change prior to implementation of the change, pursuant to section 2762.12, for contractors and employees of contractors who are operating the process and whose job tasks are affected by a change. |  |  | OBSERVATION: Owner/operator failed to ensure employees involved in the process as well as maintenance workers whose job tasks will be affected by a change, are informed of, and effectively trained in the change in a timely manner, prior to implementation of the change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that, for MOCs not meeting the training requirements, employees and maintenance workers have been informed of and effectively trained in the change. | OBSERVATION: Owner/operator failed to ensure contractors and employees of contractors operating the process whose job tasks will be affected by a change, are provided the MOC documentation and are effectively trained in the change in a timely manner, prior to implementation of the change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that, for MOCs not meeting the training requirements, contractors and employees of contractors have been provided the necessary MOC documentation and effectively trained in the change. | [5 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010181 |  |  | Program level 4: Management of Change - Process Safety Information | Failure to update information as soon as possible for a change covered by section 2762.6 that results in a change to the Process Safety Information required by section 2762.1. | 19 CCR 4.5 2762.6(g) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 202 | Program 4 Prevention Program | Management of Change | Process safety information updated as soon as possible when affected by a process change | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update information as soon as possible for a change covered by section 2762.6 that results in a change to the Process Safety Information required by section 2762.1. |  |  | OBSERVATION: Owner/operator failed to update information as soon as possible for a change that resulted in a change to the Process Safety Information. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that Process Safety Information has been updated as necessary for each deficient MOC. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010182 |  |  | Program level 4: Management of Change - Operating Procedures | Failure to update procedures prior to the start-up of the process for a change covered by section 2762.6 that results in a change to the Operating Procedures required by section 2762.3, or results in a change in the written procedures to maintain the ongoing integrity of process equipment required by section 2762.5. | 19 CCR 4.5 2762.6(h) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 203 | Program 4 Prevention Program | Management of Change | Operating and maintenance procedures updated prior to start-up when affected by a process change | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update procedures prior to the start-up of the process for a change covered by section 2762.6 that results in a change to the Operating Procedures required by section 2762.3, or results in a change in the written procedures to maintain the ongoing integrity of process equipment required by section 2762.5. |  |  | OBSERVATION: Owner/operator failed to update procedures prior to the start-up of the process for a change that resulted in a change to operating or maintenance procedures. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that operating and maintenance procedures have been updated as necessary for each deficient MOC. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010183 |  |  | Program level 4: Management of Change - Organizational Change | Failure to develop, implement, and maintain effective written procedures to manage organizational change. | 19 CCR 4.5 2762.6(i) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 204 | Program 4 Prevention Program | Management of Change | Developed, implemented, and maintained effective written organizational change procedures | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement, and maintain effective written procedures to manage organizational change. |  |  | OBSERVATION: Owner/operator failed to develop, implement, and maintain effective written procedures to manage organizational changes. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that effective written procedures to manage organizational changes have been developed, implemented, and will be maintained. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010184 |  |  | Program level 4: Management of Change - MOOC Assessment | Failure to designate a team to conduct a Management of Organizational Change (MOOC) assessment prior to reducing staffing levels, reducing classification levels of employees, changing shift duration, or substantively increasing employee responsibilities at or above 15%. Failure to ensure this requirement also applies to using contractors in permanent positions. | 19 CCR 4.5 2762.6(j) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 205 | Program 4 Prevention Program | Management of Change | Designated MOOC team to assess organizational changes | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to designate a team to conduct a Management of Organizational Change (MOOC) assessment prior to reducing staffing levels, reducing classification levels of employees, changing shift duration, or substantively increasing employee responsibilities at or above 15%. Failure to ensure this requirement also applies to using contractors in permanent positions. |  |  | OBSERVATION: Owner/operator failed to designate a team to conduct a Management of Organizational Change (MOOC) assessment prior to reducing staffing levels, reducing classification levels of employees or contractors in permanent positions, changing shift duration, or substantively increasing employee or permanent contractor responsibilities at or above 15%. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that a team conducted a MOOC assessment prior to implementing any of the items listed above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010185 |  |  | Program level 4: Management of Change - MOOC Assessment Requirements | Failure to ensure the MOOC is in writing and includes a description of the change being proposed; the makeup of the team responsible for assessing the proposed change; the factors evaluated by the team; the rationale for the team’s decision to implement or not implement the change; and the team’s findings and recommendations. (1) Failure to ensure that the job function descriptions are current and accurate for all positions potentially affected by the change prior to conducting the MOOC. (2) Failure to provide for employee participation pursuant to section 2762.10. (3) Failure to include an assessment of human factors, pursuant to section 2762.15, for All MOOC analyses. (4) Failure to ensure the stationary source manager, or his or her designee, certify based on information and belief formed after reasonable inquiry that the MOOC assessment is accurate and that the proposed organizational change(s) meets the requirements of section 2762.6. | 19 CCR 4.5 2762.6(k) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 206 | Program 4 Prevention Program | Management of Change | MOOC documentation included assessment requirements | 52 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the MOOC is in writing and includes a description of the change being proposed; the makeup of the team responsible for assessing the proposed change; the factors evaluated by the team; the rationale for the team’s decision to implement or not implement the change; and the team’s findings and recommendations. (1) Failure to ensure that the job function descriptions are current and accurate for all positions potentially affected by the change prior to conducting the MOOC. (2) Failure to provide for employee participation pursuant to section 2762.10. (3) Failure to include an assessment of human factors, pursuant to section 2762.15, for All MOOC analyses. (4) Failure to ensure the stationary source manager, or his or her designee, certify based on information and belief formed after reasonable inquiry that the MOOC assessment is accurate and that the proposed organizational change(s) meets the requirements of section 2762.6. |  |  | OBSERVATION: Owner/operator failed to ensure the MOOC is in writing and includes a description of the change being proposed; the makeup of the team responsible for assessing the proposed change; the factors evaluated by the team; the rationale for the team's decision to implement or not implement the change; and the team's findings and recommendations. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that MOOC documentation has been developed and includes the items listed above. | OBSERVATION: Owner/operator failed to ensure that job function descriptions are current and accurate for all positions potentially affected by the change prior to conducting the MOOC. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that job function descriptions for positions potentially affected by the MOOC are complete and accurate. | OBSERVATION: Owner/operator failed to provide for employee participation in the MOOC process. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that MOOCs were reevaluated with employee participation. | OBSERVATION: Owner/operator failed to include an assessment of human factors for all MOOC analyses. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that a human factors assessment was conducted for all deficient MOOC analyses. | OBSERVATION: Owner/operator failed to ensure the stationary source manager, or his or her designee, certify based on information and belief formed after reasonable inquiry that the MOOC assessment is accurate and that the proposed organizational change(s) meets the MOOC requirements. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the stationary source manager, or his or her designee, certified the MOOC assessment as accurate and that the proposed organizational change(s) meet the MOOC requirements. |  |  | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010186 |  |  | Program level 4: Management of Change - Informing Affected Employees | Failure to inform all employees potentially affected by the change prior to implementing a change. | 19 CCR 4.5 2762.6(l) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 207 | Program 4 Prevention Program | Management of Change | Informed affected employees of changes prior to implementation | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to inform all employees potentially affected by the change prior to implementing a change. |  |  | OBSERVATION: Owner/operator failed to inform all employees potentially affected by the organizational change prior to implementing the change. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that all potentially affected employees are informed of the organizational change. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010187 |  |  | Program level 4: Pre-Startup Safety Review - General Requirements | Failure to perform a pre-startup safety review (PSSR) for new processes, for modified processes if the modification necessitates a change in the Process Safety Information, and for partial and unplanned shutdowns. Failure to also conduct a PSSR for all turnaround work performed on a process. | 19 CCR 4.5 2762.7(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 208 | Program 4 Prevention Program | Pre-Startup Safety Review | PSSRs performed for new and modified processes with changes to PSI, partial and unplanned shutdowns | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform a pre-startup safety review (PSSR) for new processes, for modified processes if the modification necessitates a change in the Process Safety Information, and for partial and unplanned shutdowns. Failure to also conduct a PSSR for all turnaround work performed on a process. |  |  | OBSERVATION: Owner/operator failed to perform a PSSR for new processes, for modified processes if the modification necessitates a change in the PSI, for partial and unplanned shutdowns, and for all turnaround work performed on a process. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that PSSRs have been completed for the items listed above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010188 |  |  | Program level 4: Pre-Startup Safety Review - Verification Check | Failure to confirm, as a verification check, independent of the management of change process, that prior to the introduction of highly hazardous materials to a process: (1) Construction, maintenance, and repair work has been performed in accordance with design specifications; (2) Process equipment has been maintained and is operable in accordance with design specifications; (3) Effective safety, operating, maintenance, and emergency procedures are in place; (4) For new process units, a PHA, HCA, DMR, and SPA have each been performed as applicable pursuant to Article 6.5, and recommendations have been implemented or resolved before start-up. For new or modified processes, all changes have been implemented in accordance with the requirements contained in the MOC, section 2762.6; and, (5) Training of each operating employee and maintenance employee affected by the change has been completed. | 19 CCR 4.5 2762.7(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 209 | Program 4 Prevention Program | Pre-Startup Safety Review | Independently verified the required items prior to change implementation | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to confirm, as a verification check, independent of the management of change process, that prior to the introduction of highly hazardous materials to a process: (1) Construction, maintenance, and repair work has been performed in accordance with design specifications; (2) Process equipment has been maintained and is operable in accordance with design specifications; (3) Effective safety, operating, maintenance, and emergency procedures are in place; (4) For new process units, a PHA, HCA, DMR, and SPA have each been performed as applicable pursuant to Article 6.5, and recommendations have been implemented or resolved before start-up. For new or modified processes, all changes have been implemented in accordance with the requirements contained in the MOC, section 2762.6; and, (5) Training of each operating employee and maintenance employee affected by the change has been completed. |  |  | OBSERVATION: Owner/operator failed to confirm, as a verification check, independent of the management of change process, that prior to the introduction of highly hazardous materials to a process: construction, maintenance, and repair work has been performed in accordance with design specifications; process equipment has been maintained and is operable in accordance with design specifications; effective safety, operating, maintenance, and emergency procedures are in place; for new process units, a PHA, HCA, DMR, and SPA have each been performed as applicable pursuant to Article 6.5, and recommendations have been implemented or resolved before start-up; for new or modified processes, all changes have been implemented per the MOC; training of operating maintenance employees affected by the change has been completed. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that a verification check independent of the MOC has been completed for the items listed above. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010189 |  |  | Program level 4: Pre-Startup Safety Review - Employee Representative | Failure to designate as the employee representative, pursuant to section 2762.10, an operating employee who currently works in the unit and has expertise and experience in the process being started. | 19 CCR 4.5 2762.7(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 210 | Program 4 Prevention Program | Pre-Startup Safety Review | Designated an operating employee as employee representative for PSSRs | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to designate as the employee representative, pursuant to section 2762.10, an operating employee who currently works in the unit and has expertise and experience in the process being started. |  |  | OBSERVATION: Owner/operator failed to designate as the employee representative an operating employee who currently works in the unit and has expertise and experience in the process being started. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that an appropriate operating employee was designated as the employee representative for the PSSR process. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010190 |  |  | Program level 4: Compliance Audits - Certification | Failure to conduct an effective compliance audit and certify every three (3) years that the procedures and practices developed under Article 6.5 have been evaluated to verify they are in compliance with the provisions of Article 6.5, and are being followed. | 19 CCR 4.5 2762.8(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 211 | Program 4 Prevention Program | Compliance Audits | Conducted effective compliance audit and certified every three years in compliance with Article 6.5 | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to conduct an effective compliance audit and certify every three (3) years that the procedures and practices developed under Article 6.5 have been evaluated to verify they are in compliance with the provisions of Article 6.5, and are being followed. |  |  | OBSERVATION: Owner/operator failed to certify that they have evaluated compliance with the provisions of Article 6.5 at least every three years to verify that the procedures and practices developed under Article 6.5 are adequate and are being followed. CORRECTIVE ACTION: Submit a certification to the CUPA that the owner/operator has evaluated compliance with the provisions of Article 6.5 at least every three years to verify that the procedures and practices developed under Article 6.5 are adequate and are followed. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010191 |  |  | Program level 4: Compliance Audits - Knowledgeable Person | Failure to ensure the compliance audit is conducted by at least one person knowledgeable in the requirements of the Article 6.5 section under review. | 19 CCR 4.5 2762.8(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 212 | Program 4 Prevention Program | Compliance Audits | Conducted compliance audit by a person knowledgeable in the requirements of Article 6.5 | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the compliance audit is conducted by at least one person knowledgeable in the requirements of the Article 6.5 section under review. |  |  | OBSERVATION: Owner/operator failed to ensure that the compliance audit is conducted by at least one person knowledgeable of the requirements of Article 6.5 under review. CORRECTIVE ACTION: Conduct the compliance audit with at least one person knowledgeable of the requirements of Article 6.5 under review. Develop a report of the compliance audit findings, including appropriate responses to each of the findings and submit a copy to the CUPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010192 |  |  | Program level 4: Compliance Audits - Report | Failure to prepare a written report of the compliance audit that includes the scope, methods used, questions asked to assess each program element along with findings and recommendations of the compliance audit. Failure to ensure the written report also documents the qualifications of those persons performing the compliance audit. Failure to make the report available to employees and employee representatives, in accordance with section 2762.10. Failure to respond in writing within 60 calendar days to any written employee or employee representative comments on the written audit report. | 19 CCR 4.5 2762.8(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 213 | Program 4 Prevention Program | Compliance Audits | Prepared a compliance audit written report, documented team qualif's, made available to employees | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a written report of the compliance audit that includes the scope, methods used, questions asked to assess each program element along with findings and recommendations of the compliance audit. Failure to ensure the written report also documents the qualifications of those persons performing the compliance audit. Failure to make the report available to employees and employee representatives, in accordance with section 2762.10. Failure to respond in writing within 60 calendar days to any written employee or employee representative comments on the written audit report. |  |  | OBSERVATION: Owner/operator failed to: Prepare a written report of the compliance audit assessing each program element along with findings of the audit; ensure the report documents the qualifications of those persons performing the audit; make the report available to employees and employee representatives, in accordance with section 2762.10; and/or respond in writing within 60 calendar days to any written employee or employee representative comments on the written audit report. CORRECTIVE ACTION: Prepare a written report of the compliance audit that includes the scope, methods used, questions asked to assess each program element along with findings and recommendations of the compliance audit. Ensure the written report also documents the qualifications of those persons performing the compliance audit. Make the report available to employees and employee representatives. Respond in writing to any written employee or employee representative comments on the written audit report. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010193 |  |  | Program level 4: Compliance Audits - Corrective Action Work Process | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when developing the resolution and implementation of the compliance audit recommendations. | 19 CCR 4.5 2762.8(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 214 | Program 4 Prevention Program | Compliance Audits | Followed corrective work action process for resolution and implementation of the compliance audit | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when developing the resolution and implementation of the compliance audit recommendations. |  |  | OBSERVATION: Owner/operator failed to: Follow the corrective action work process documented in subsections 2762.16 (d) and (e) when developing the resolution and implementation of the compliance audit recommendations. CORRECTIVE ACTION: Submit documentation to the UPA of compliance with the corrective action work process of the compliance audit recommendations. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010194 |  |  | Program level 4: Compliance Audits - Retention | Failure to retain the three (3) most recent compliance audit reports. | 19 CCR 4.5 2762.8(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 215 | Program 4 Prevention Program | Compliance Audits | Retained three most recent compliance audit reports | 51 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain the three (3) most recent compliance audit reports. |  |  | OBSERVATION: Owner/operator failed to retain the three (3) most recent compliance audit reports. CORRECTIVE ACTION: Obtain, retain and submit to the UPA copies of the three (3) most recent compliance audit reports | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010195 |  |  | Program level 4: Compliance Audits - Consultations | Failure to consult with operators with expertise and experience in each process audited and document the findings and recommendations from these consultations in the audit report, as part of the compliance audit. | 19 CCR 4.5 2762.8(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 216 | Program 4 Prevention Program | Compliance Audits | Consulted with operators and documented findings in the compliance audit report | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to consult with operators with expertise and experience in each process audited and document the findings and recommendations from these consultations in the audit report, as part of the compliance audit. |  |  | OBSERVATION: Owner/operator failed to consult with operators with expertise and experience in each process audited and document the findings and recommendations from these consultations in the audit report, as part of the compliance audit. CORRECTIVE ACTION: Submit documentation of proper consultation with the appropriate operators and of the documentation of findings and recommendations from these consultations. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010196 |  |  | Program level 4: Incident Investigation - Written Procedures | Failure to develop, implement, and maintain effective written procedures for promptly investigating and reporting any incident that results in or could reasonably have resulted in a major incident. | 19 CCR 4.5 2762.9(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 217 | Program 4 Prevention Program | Incident Investigation | Effective incident investigation procedures are written and implemented | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement, and maintain effective written procedures for promptly investigating and reporting any incident that results in or could reasonably have resulted in a major incident. |  |  | OBSERVATION: Owner/operator failed to develop, implement, and maintain effective written procedures for promptly investigating and reporting any incident that results in or could reasonably have resulted in a major incident. CORRECTIVE ACTION: Submit documentation of proper written procedures stemming from a major incident report | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010197 |  |  | Program level 4: Incident Investigation - Root Cause Analysis | Failure to ensure written procedures include an effective method for conducting a thorough root cause analysis. | 19 CCR 4.5 2762.9(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 218 | Program 4 Prevention Program | Incident Investigation | Effective method to conduct a thorough Root Cause Analysis procedure is written | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure written procedures include an effective method for conducting a thorough root cause analysis. |  |  | OBSERVATION: Owner/operator failed to ensure written procedures include an effective method for conducting a thorough root cause analysis. CORRECTIVE ACTION: Submit documentation of an effective method for conducting a thorough Root Cause Analysis. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010198 |  |  | Program level 4: Incident Investigation - Promptness | Failure to initiate the incident investigation as promptly as possible, but no later than 48 hours following an incident. | 19 CCR 4.5 2762.9(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 219 | Program 4 Prevention Program | Incident Investigation | Incident investigation initiated within 48 hours following an incident | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to initiate the incident investigation as promptly as possible, but no later than 48 hours following an incident. |  |  | OBSERVATION: Owner/operator failed to initiate the incident investigation as promptly as possible, but no later than 48 hours following an incident. CORRECTIVE ACTION: Immediately initiate an incident investigation/ Submit procedure to ensure incident investigations begin as promptly as possible, but no later than 48 hours following an incident. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010199 |  |  | Program level 4: Incident Investigation - Team Qualifications | Failure to ensure an incident investigation team is established and, at a minimum, consist of a person with expertise and experience in the process involved, a person with expertise in the owner or operator's root cause analysis method, and a person with expertise in overseeing the investigation and analysis. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure an employee and employee representative of that contractor, if applicable, is also included on the investigation team if the incident involved the work of a contractor. | 19 CCR 4.5 2762.9(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 220 | Program 4 Prevention Program | Incident Investigation | Investigation team consists of personnel with appropriate expertise | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure an incident investigation team is established and, at a minimum, consist of a person with expertise and experience in the process involved, a person with expertise in the owner or operator's root cause analysis method, and a person with expertise in overseeing the investigation and analysis. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure an employee and employee representative of that contractor, if applicable, is also included on the investigation team if the incident involved the work of a contractor. |  |  | OBSERVATION: Owner/operator failed to ensure an incident investigation team is established and, at a minimum, consist of a person with expertise and experience in the process involved, a person with expertise in the owner or operator's root cause analysis method, and a person with expertise in overseeing the investigation and analysis. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure an employee and employee representative of that contractor, if applicable, is also included on the investigation team if the incident involved the work of a contractor. CORRECTIVE ACTION: Submit documentation of proper incident investigation team qualifications. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010200 |  |  | Program level 4: Incident Investigation - RCA Method | Failure to ensure the incident investigation team implement the owner or operator's root cause analysis method to determine the underlying causes of the incident. Failure to ensure the analysis include identification of management system causes, including organizational and safety culture causes. | 19 CCR 4.5 2762.9(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 221 | Program 4 Prevention Program | Incident Investigation | Root Cause Analysis includes management system, organizational and safety culture causes | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the incident investigation team implement the owner or operator's root cause analysis method to determine the underlying causes of the incident. Failure to ensure the analysis include identification of management system causes, including organizational and safety culture causes. |  |  | OBSERVATION: Owner/operator failed to ensure the incident investigation team implement the owner or operator's root cause analysis method to determine the underlying causes of the incident. Failure to ensure the analysis include identification of management system causes, including organizational and safety culture causes. CORRECTIVE ACTION: Submit documentation of proper root cause analysis methods including management system, organizational and safety culture causes. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010201 |  |  | Program level 4: Incident Investigation - DMR | Failure to ensure the team review the related DMRs that were performed pursuant to section 2762.5(e) and incorporate the applicable findings from these DMRs into the incident investigation. | 19 CCR 4.5 2762.9(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 222 | Program 4 Prevention Program | Incident Investigation | Incident Investigation team reviewed related DMR and incorporated findings into its report | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the team review the related DMRs that were performed pursuant to section 2762.5(e) and incorporate the applicable findings from these DMRs into the incident investigation. |  |  | OBSERVATION: Owner/operator failed to ensure the team review the related DMRs that were performed pursuant to section 2762.5(e) and incorporate the applicable findings from these DMRs into the incident investigation. CORRECTIVE ACTION: Submit documentation of proper review of related DMRs and their incorporation into the incident investigation. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010202 |  |  | Program level 4: Incident Investigation - Recommendations | Failure to ensure the incident investigation team develop recommendations to address the findings of the investigation. Failure to ensure recommendations include interim actions that will reduce the risk of a recurrence or similar incident until final actions can be implemented. Failure to perform an HCA pursuant to section 2762.13, for recommendations that result from the investigation of a major incident. Failure to append the HCA report to the final investigation report. | 19 CCR 4.5 2762.9(g) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 223 | Program 4 Prevention Program | Incident Investigation | Incident Investigation team developed recommendations and interim actions to reduce risk | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the incident investigation team develop recommendations to address the findings of the investigation. Failure to ensure recommendations include interim actions that will reduce the risk of a recurrence or similar incident until final actions can be implemented. Failure to perform an HCA pursuant to section 2762.13, for recommendations that result from the investigation of a major incident. Failure to append the HCA report to the final investigation report. |  |  | OBSERVATION: Owner/operator failed to ensure the incident investigation team develop recommendations to address the findings of the investigation. Failure to ensure recommendations include interim actions that will reduce the risk of a recurrence or similar incident until final actions can be implemented. Failure to perform an HCA pursuant to section 2762.13, for recommendations that result from the investigation of a major incident. Failure to append the HCA report to the final investigation report. CORRECTIVE ACTION: Submit documentation of the incident team's recommendations addressing the findings of its investigation and interim actions to reduce risk. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010203 |  |  | Program level 4: Incident Investigation - Report | Failure to submit a written report for major incidents to the UPA within 90 calendar days of the incident. Failure to prepare a status report within 90 calendar days of the incident and every 30 calendar days thereafter until the investigation is complete for cases where the owner or operator has demonstrated that additional time is needed due to the complexity of the investigation. Failure to submit a final report within five (5) months of the incident. | 19 CCR 4.5 2762.9(h) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 224 | Program 4 Prevention Program | Incident Investigation | Investigation report/status updates for major incidents submitted to UPA as required | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to submit a written report for major incidents to the UPA within 90 calendar days of the incident. Failure to prepare a status report within 90 calendar days of the incident and every 30 calendar days thereafter until the investigation is complete for cases where the owner or operator has demonstrated that additional time is needed due to the complexity of the investigation. Failure to submit a final report within five (5) months of the incident. |  |  | OBSERVATION: Owner/operator failed to submit a written report for major incidents to the UPA within 90 calendar days of the incident. Failure to prepare a status report within 90 calendar days of the incident and every 30 calendar days thereafter until the investigation is complete for cases where the owner or operator has demonstrated that additional time is needed due to the complexity of the investigation. Failure to submit a final report within five (5) months of the incident. CORRECTIVE ACTION: Immediately submit a written report of a major incident or a status report to the UPA . | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010204 |  |  | Program level 4: Incident Investigation - Report Contents | Failure to ensure the investigation report includes: (1) Date and time of the incident; (2) Date and time the investigation began; (3) A detailed description of the incident; (4) The factors that caused or contributed to the incident, including direct causes, indirect causes and root causes, determined through the root cause analysis; (5) A list of any DMR(s), PHA(s), HCA(s), and SPA(s) that were reviewed as part of the investigation; (6) Interim recommendations to prevent a recurrence or similar incident; (7) Recommendations for permanent corrective actions. | 19 CCR 4.5 2762.9(i) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 225 | Program 4 Prevention Program | Incident Investigation | Investigation report is thorough and complete | 45 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the investigation report includes: (1) Date and time of the incident; (2) Date and time the investigation began; (3) A detailed description of the incident; (4) The factors that caused or contributed to the incident, including direct causes, indirect causes and root causes, determined through the root cause analysis; (5) A list of any DMR(s), PHA(s), HCA(s), and SPA(s) that were reviewed as part of the investigation; (6) Interim recommendations to prevent a recurrence or similar incident; (7) Recommendations for permanent corrective actions. |  |  | OBSERVATION: Owner/operator failed to ensure the investigation report includes: (1) Date and time of the incident; (2) Date and time the investigation began; (3) A detailed description of the incident; (4) The factors that caused or contributed to the incident, including direct causes, indirect causes and root causes, determined through the root cause analysis; (5) A list of any DMR(s), PHA(s), HCA(s), and SPA(s) that were reviewed as part of the investigation; (6) Interim recommendations to prevent a recurrence or similar incident; (7) Recommendations for permanent corrective actions. CORRECTIVE ACTION: Submit completed investigation report which includes all required contents. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010205 |  |  | Program level 4: Incident Investigation - Report Availability | Failure to ensure the report is provided to and, upon request, reviewed with employees whose job tasks are affected by the incident. Failure to ensure investigation reports are also made available to all operating, maintenance, and other personnel, including employees of contractors where applicable, whose work assignments are within the facility where the incident occurred or whose job tasks are relevant to the incident findings. Failure to ensure investigation reports are provided upon request to employee representatives, and where applicable, contractor employee representatives. | 19 CCR 4.5 2762.9(k) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 226 | Program 4 Prevention Program | Incident Investigation | Investigation report available to personnel whose job tasks are relevant to the incident findings | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the report is provided to and, upon request, reviewed with employees whose job tasks are affected by the incident. Failure to ensure investigation reports are also made available to all operating, maintenance, and other personnel, including employees of contractors where applicable, whose work assignments are within the facility where the incident occurred or whose job tasks are relevant to the incident findings. Failure to ensure investigation reports are provided upon request to employee representatives, and where applicable, contractor employee representatives. |  |  | OBSERVATION: Owner/operator failed to ensure the report is provided to and, upon request, reviewed with employees whose job tasks are affected by the incident. Failure to ensure investigation reports are also made available to all operating, maintenance, and other personnel, including employees of contractors where applicable, whose work assignments are within the facility where the incident occurred or whose job tasks are relevant to the incident findings. Failure to ensure investigation reports are provided upon request to employee representatives, and where applicable, contractor employee representatives. CORRECTIVE ACTION: Submit documentation that the incident investigation report has been made available to all appropriate personnel whose job tasks are relevant to the incident findings. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010206 |  |  | Program level 4: Incident Investigation - Corrective Action | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e), when resolving the investigation team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. Failure to ensure the corrective action plan include review, and revalidation as necessary, of the appropriate portions of all relevant PHAs and DMRs. | 19 CCR 4.5 2762.9(l) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 227 | Program 4 Prevention Program | Incident Investigation | Corrective action work process documented and relevant PHAs and DMRs reviewed | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e), when resolving the investigation team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. Failure to ensure the corrective action plan include review, and revalidation as necessary, of the appropriate portions of all relevant PHAs and DMRs. |  |  | OBSERVATION: Owner/operator failed to follow the corrective action work process documented in subsections 2762.16 (d) and (e), when resolving the investigation team's findings and recommendations, determining action items for implementation, tracking to completion, and documentation of closeout. Failure to ensure the corrective action plan include review, and revalidation as necessary, of the appropriate portions of all relevant PHAs and DMRs. CORRECTIVE ACTION: Submit documentation of compliance with the corrective action findings and recommendations and of review of the relevant PHAs and DMRs. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010207 |  |  | Program level 4: Incident Investigation - Retention | Failure to ensure incident investigation reports are retained for the life of the process unit. | 19 CCR 4.5 2762.9(m) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 228 | Program 4 Prevention Program | Incident Investigation | Incident investigation reports retained for the life of the unit | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure incident investigation reports are retained for the life of the process unit. |  |  | OBSERVATION: Owner/operator failed to ensure incident investigation reports are retained for the life of the process unit. CORRECTIVE ACTION: Obtain, retain and submit documentation of all incident reports for the life of the process unit. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010208 |  |  | Program level 4: Incident Investigation - Independent Analysis | Failure to assist the UPA in conducting an independent analysis, when the UPA chooses to perform an independent Process Safety Culture Assessment (PSCA), Incident Investigation, evaluation of the ARP management system or Human Factors Analysis after a major incident pursuant to section 2775.2.5. | 19 CCR 4.5 2762.9(n) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 229 | Program 4 Prevention Program | Incident Investigation | Assisted UPA to perform an independent analysis after a major incident | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to assist the UPA in conducting an independent analysis, when the UPA chooses to perform an independent Process Safety Culture Assessment (PSCA), Incident Investigation, evaluation of the ARP management system or Human Factors Analysis after a major incident pursuant to section 2775.2.5. |  |  | OBSERVATION: Owner/operator failed to assist the UPA in conducting an independent analysis, when the UPA chooses to perform an independent Process Safety Culture Assessment (PSCA), Incident Investigation, evaluation of the ARP management system or Human Factors Analysis after a major incident pursuant to section 2775.2.5. CORRECTIVE ACTION: Immediately assist the UPA in conducting an independent analysis of PSCA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010209 |  |  | Program level 4: Employee Participation - Plan | Failure to develop, implement and maintain a written plan to effectively provide for employee participation in Accidental Release Prevention elements, as required by Article 6.5. Failure to ensure the plan include provisions that provide for the following: (1) Effective participation by affected operating and maintenance employees and employee representatives, throughout all phases, in performing PHAs, DMRs, HCAs, MOCs, MOOCs, Process Safety Culture Assessments (PSCAs), Incident Investigations, SPAs, and PSSRs; (2) Effective participation by affected operating and maintenance employees and employee representatives, throughout all phases of in the development, training, implementation and maintenance of the Accidental Release Prevention elements required by Article 6.5. (3) Access by employees and employee representatives to all documents or information developed or collected by the owner or operator pursuant to Article 6.5, including information that might be subject to protection as a trade secret | 19 CCR 4.5 2762.10(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 230 | Program 4 Prevention Program | Employee Participation | Written employee participation plan developed, implemented & maintained | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement and maintain a written plan to effectively provide for employee participation in Accidental Release Prevention elements, as required by Article 6.5. Failure to ensure the plan include provisions that provide for the following: (1) Effective participation by affected operating and maintenance employees and employee representatives, throughout all phases, in performing PHAs, DMRs, HCAs, MOCs, MOOCs, Process Safety Culture Assessments (PSCAs), Incident Investigations, SPAs, and PSSRs; (2) Effective participation by affected operating and maintenance employees and employee representatives, throughout all phases of in the development, training, implementation and maintenance of the Accidental Release Prevention elements required by Article 6.5. (3) Access by employees and employee representatives to all documents or information developed or collected by the owner or operator pursuant to Article 6.5, including information that might be subject to protection as a trade secret |  |  | OBSERVATION: Owner/operator failed to: develop, implement and maintain a written plan to effectively provide for employee participation in Accidental Release Prevention elements, as required by Article 6.5, ensure the plan includes provisions that provide for effective participation by affected operating and maintenance employees and employee representatives and access by employees and employee representatives the following: (1) throughout all phases, in performing PHAs, DMRs, HCAs, MOCs, MOOCs, PSCAs, Incident Investigations, SPAs, and PSSRs; (2) throughout all phases of in the development, training, implementation and maintenance of the Accidental Release Prevention elements required by Article 6.5; (3) to all documents or information developed or collected by the owner or operator pursuant to Article 6.5, including information that might be subject to protection as a trade secret. CORRECTIVE ACTION: Submit documentation of compliance with employee participation. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010210 |  |  | Program level 4: Employee Participation - Employee Representative Selection | Failure to establish effective procedures in consultation with employees for the selection of employee representatives, where employees are not represented by an authorized collective bargaining agent. | 19 CCR 4.5 2762.10(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 231 | Program 4 Prevention Program | Employee Participation | Established procedures to select non union employee representatives | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to establish effective procedures in consultation with employees for the selection of employee representatives, where employees are not represented by an authorized collective bargaining agent. |  |  | OBSERVATION: Owner/operator failed to establish effective procedures in consultation with employees for the selection of employee representatives, where employees are not represented by an authorized collective bargaining agent. CORRECTIVE ACTION: Submit documentation of effective procedures to provide proper non union employee representative participation. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010211 |  |  | Program level 4: Hot Work Permit - Hot Work Operations | Failure to issue a hot work permit for hot work operations conducted on or near a covered process. | 19 CCR 4.5 2762.11(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 232 | Program 4 Prevention Program | Hot Work Permit | Hot work permits issued for operations on or near a covered process | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to issue a hot work permit for hot work operations conducted on or near a covered process. |  |  | OBSERVATION: Owner/operator Failed to issue a hot work permit for hot work operations conducted on or near a covered process. CORRECTIVE ACTION: Submit documentation to ensure hot work permits are properly issued. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010212 |  |  | Program level 4: Hot Work Permit - Fire Prevention and Protection | Failure to ensure the permit documents that the fire prevention and protection requirements in section 5189 of Title 8 of CCR have been implemented prior to beginning the hot work operations; failure to indicate the date(s) and time(s) authorized for hot work; and identify the equipment or process on which hot work is to be performed. Failure to ensure the permit is kept on file for one year. | 19 CCR 4.5 2762.11(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 233 | Program 4 Prevention Program | Hot Work Permit | Hot work permits issued fire prevention & protection requirements & retained on file for one year | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the permit documents that the fire prevention and protection requirements in section 5189 of Title 8 of CCR have been implemented prior to beginning the hot work operations; failure to indicate the date(s) and time(s) authorized for hot work; and identify the equipment or process on which hot work is to be performed. Failure to ensure the permit is kept on file for one year. |  |  | OBSERVATION: Owner/operator failed to ensure the permit documents that the fire prevention and protection requirements in section 5189 of Title 8 of CCR have been implemented prior to beginning the hot work operations; failure to indicate the date(s) and time(s) authorized for hot work; and identify the equipment or process on which hot work is to be performed. Failure to ensure the permit is kept on file for one year. CORRECTIVE ACTION: Submit documentation to ensure the hot work permit has proper fire prevention and protection requirements and are retained for one year. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010213 |  |  | Program level 4: Contractors - Owner/Operator Responsibilities | (1) Failure to obtain and evaluate information regarding the contract owner or operator's safety performance and programs, when selecting a contractor, and require that its contractors and any subcontractors use a skilled and trained workforce pursuant to Health and Safety Code Section 25536.7. (2) Failure to inform the contract owner or operator and ensure that the contract owner or operator has informed each of its employees of the work practices necessary to safely perform his or her jobs, including but not limited to: the potential hazards related to their jobs; applicable refinery safety rules; and in the applicable provisions of the stationary source's emergency action plan. (3) Failure to explain to the contract owner or operator the applicable provisions of Article 7. (4) Failure to develop and implement effective written procedures to ensure the safe entry, presence, and exit of the contract owner or operator and contract employees in process areas. (5) Failure to periodically evaluate the performance of the contract owner or operator in fulfilling their obligations as specified in subsection 2762.12 (c). (6) Failure to ensure and document that the requirements of section 2762.12 are performed and completed by the contractor owner or operator. | 19 CCR 4.5 2762.12(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 234 | Program 4 Prevention Program | Contractors | Contractor safety performance and programs reviewed | 51 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | (1) Failure to obtain and evaluate information regarding the contract owner or operator's safety performance and programs, when selecting a contractor, and require that its contractors and any subcontractors use a skilled and trained workforce pursuant to Health and Safety Code Section 25536.7. (2) Failure to inform the contract owner or operator and ensure that the contract owner or operator has informed each of its employees of the work practices necessary to safely perform his or her jobs, including but not limited to: the potential hazards related to their jobs; applicable refinery safety rules; and in the applicable provisions of the stationary source's emergency action plan. (3) Failure to explain to the contract owner or operator the applicable provisions of Article 7. (4) Failure to develop and implement effective written procedures to ensure the safe entry, presence, and exit of the contract owner or operator and contract employees in process areas. (5) Failure to periodically evaluate the performance of the contract owner or operator in fulfilling their obligations as specified in subsection 2762.12 (c). (6) Failure to ensure and document that the requirements of section 2762.12 are performed and completed by the contractor owner or operator. |  |  | OBSERVATION: Owner/operator failed to (1) obtain and evaluate information regarding the contract owner or operator's safety performance and programs and require use of a skilled and trained workforce pursuant to H&SC Sec 25536.7. (2) inform and ensure the contract owner or operator has informed each of its employees of the work practices necessary to safely perform their jobs. (3) explain to the contract owner or operator provisions of Article 7. (4) develop and implement effective written procedures to ensure the safe entry, presence, and exit of the contract owner or operator and contract employees in process areas. (5) periodically evaluate the contract owner or operator in fulfilling their obligations as specified in subsection 2762.12 (c). (6) ensure and document the contractor owner or operator complies with section 2762.12. CORRECTIVE ACTION: Submit documentation of the review of contractor's safety performance and programs. | OBSERVATION: Owner/operator failed to ensure the permit documents that the fire prevention and protection requirements in section 5189 of Title 8 of CCR have been implemented prior to beginning the hot work operations; failure to indicate the date(s) and time(s) authorized for hot work; and identify the equipment or process on which hot work is to be performed. Failure to ensure the permit is kept on file for one year. | [5 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010214 |  |  | Program level 4: Contractors - Contract Owner/Operator Responsibilities | Failure to ensure the contract owner/operator is performing the following responsibilities: (1) Failure to eEnsure that each contract employee is trained in the work practices necessary to safely perform his or her jobs, including but not limited to: the potential hazards related to their jobs; applicable refinery safety rules; and in the applicable provisions of the stationary source's emergency action plan, and shall meet the requirements of Health and Safety Code Section 25536.7. (2) Failure to dDocuments that each contract employee has successfully completed the training required by section 2762.12 by maintaining a record identifying: (A) each employee who has received training; (B) the date(s) and subject(s) of training each employee has received; (C) and the means used to verify that the employee understood the training received. (3) Failure to eEnsure that each contract employee follows the safety and health procedures of the stationary source. (4) Failure to aAdvise the owner or operator of any specific hazards presented by the contract owner or operator's work, or of any hazards found by the contract owner or operator while performing work for the stationary source. | 19 CCR 4.5 2762.12(b)(5); 2762.12(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 235 | Program 4 Prevention Program | Contractors | Complied with contract owner/operator responsibilities | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the contract owner/operator is performing the following responsibilities: (1) Failure to eEnsure that each contract employee is trained in the work practices necessary to safely perform his or her jobs, including but not limited to: the potential hazards related to their jobs; applicable refinery safety rules; and in the applicable provisions of the stationary source's emergency action plan, and shall meet the requirements of Health and Safety Code Section 25536.7. (2) Failure to dDocuments that each contract employee has successfully completed the training required by section 2762.12 by maintaining a record identifying: (A) each employee who has received training; (B) the date(s) and subject(s) of training each employee has received; (C) and the means used to verify that the employee understood the training received. (3) Failure to eEnsure that each contract employee follows the safety and health procedures of the stationary source. (4) Failure to aAdvise the owner or operator of any specific hazards presented by the contract owner or operator's work, or of any hazards found by the contract owner or operator while performing work for the stationary source. |  |  | OBSERVATION: Owner/operator failed to ensure that the contract owner/operator complies with the following: ensure each contract employee is trained in the work practices necessary to safely perform his or her jobs, including: the potential hazards related to their jobs; applicable refinery safety rules; and in the applicable provisions of the emergency action plan, and comply with H&SC 25536.7; document and maintain a training record for each contract employee identifying: each employee who has received training; the date(s) and subject(s) of training; and the means used to verify that the employee understood the training received; ensure each contract employee follows the safety and health procedures of the refinery; advise the owner/operator of any specific hazards presented or of any hazards found by the contract owner or operator's work while performing work. CORRECTIVE ACTION: Ensure that each contract owner/operator properly trains employees is trained in the work practices to safely perform his or her job and submit compliance documentation compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010215 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Schedule | Failure to conduct an HCA for all existing processes. Failure to ensure the HCA for existing processes is performed in accordance with the following schedule, and may be performed in conjunction with the PHA schedule: (1) No less than 50% of existing processes within three (3) years of the effective date of Article 6.5; (2) Remaining processes within five (5) years of the effective date of Article 6.5. | 19 CCR 4.5 2762.13(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 236 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Conducted an HCA for all existing processes in accordance with schedule | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to conduct an HCA for all existing processes. Failure to ensure the HCA for existing processes is performed in accordance with the following schedule, and may be performed in conjunction with the PHA schedule: (1) No less than 50% of existing processes within three (3) years of the effective date of Article 6.5; (2) Remaining processes within five (5) years of the effective date of Article 6.5. |  |  | OBSERVATION: Owner/operator failed to conduct an HCA for all existing processes. Owner/operator failed to ensure the HCA for existing processes is performed in accordance with the following schedule, and may be performed in conjunction with the PHA schedule: (1) No less than 50% of existing processes within three (3) years of the effective date of Article 6.5; (2) Remaining processes within five (5) years of the effective date of Article 6.5. CORRECTIVE ACTION: Conduct an HCA for all existing processes. Ensure the HCA for existing process is performed according to the required schedule and submit documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010216 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Instances | Failure to also conduct an HCA in a timely manner in the following instances: (1) For all PHA recommendations for each scenario that identifies the potential for a major incident; (2) Whenever a major change is proposed at a facility, as part of a Management of Change review required by section 2762.6; (3) When a major incident occurs, on the recommendations of the incident investigation report required by section 2762.9; and (4) During the design and review of new processes, new process units, and new facilities, and their related process equipment. An HCA report prepared for this purpose shall be provided to the UPA. | 19 CCR 4.5 2762.13(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 237 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Conducted a timely HCA in specified instances | 47 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to also conduct an HCA in a timely manner in the following instances: (1) For all PHA recommendations for each scenario that identifies the potential for a major incident; (2) Whenever a major change is proposed at a facility, as part of a Management of Change review required by section 2762.6; (3) When a major incident occurs, on the recommendations of the incident investigation report required by section 2762.9; and (4) During the design and review of new processes, new process units, and new facilities, and their related process equipment. An HCA report prepared for this purpose shall be provided to the UPA. |  |  | OBSERVATION: Owner/operator failed to conduct an HCA in a timely manner in the following instances: (1) For all PHA recommendations for each scenario that identifies the potential for a major incident; (2) Whenever a major change is proposed at a facility, as part of a Management of Change review required by section 2762.6; (3) When a major incident occurs, on the recommendations of the incident investigation report required by section 2762.9; and (4) During the design and review of new processes, new process units, and new facilities, and their related process equipment. An HCA report prepared for this purpose shall be provided to the UPA. CORRECTIVE ACTION: Conduct an HCA in the above required instances and submit an HCA report to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010217 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Update | Failure to update all HCAs consistent with the requirements of section 2762.13 at least once every five years, in conjunction with the PHA schedule. | 19 CCR 4.5 2762.13(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 238 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Updated all HCAs | 17 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update all HCAs consistent with the requirements of section 2762.13 at least once every five years, in conjunction with the PHA schedule. |  |  | OBSERVATION: Owner/operator failed to update all HCAs consistent with the requirements of section 2762.13 at least once every five years, in conjunction with the PHA schedule. CORRECTIVE ACTION: Update all HCAs at least once every five years and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010218 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Team Qualifications | Failure to perform, update, and document an HCA by a team with expertise in engineering and process operations and the team shall include at least one operating employee who currently works on the process and has experience and knowledge specific to the process being evaluated. Failure to ensure the team also include one member knowledgeable in the HCA method being used. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure the team consult with individuals with expertise in damage mechanisms, process chemistry, and control systems, as necessary. | 19 CCR 4.5 2762.13(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 239 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Complied with HCA team qualifications and requirements | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to perform, update, and document an HCA by a team with expertise in engineering and process operations and the team shall include at least one operating employee who currently works on the process and has experience and knowledge specific to the process being evaluated. Failure to ensure the team also include one member knowledgeable in the HCA method being used. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure the team consult with individuals with expertise in damage mechanisms, process chemistry, and control systems, as necessary. |  |  | OBSERVATION: Owner/operator failed to perform, update, and document an HCA by a team with expertise in engineering and process operations and the team shall include at least one operating employee who currently works on the process and has experience and knowledge specific to the process being evaluated. Failure to ensure the team also include one member knowledgeable in the HCA method being used. Failure to provide for employee participation in this process, pursuant to section 2762.10. Failure to ensure the team consult with individuals with expertise in damage mechanisms, process chemistry, and control systems, as necessary. CORRECTIVE ACTION: Submit documentation to the UPA to demonstrate HCA was performed and updated by a qualified team. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010219 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Requirements | Failure to ensure the HCA team: (1) Include all risk-relevant data for each process or recommendation, including incident investigation reports pursuant to section 2762.9; (2) Identify, characterize and prioritize each process safety hazard. (3) Identify, analyze, and document all inherent safety measures and safeguards (or where appropriate, combinations of measures and safeguards) in an iterative manner to reduce each hazard to the greatest extent feasible. Identify, analyze, and document relevant, publicly available information on inherent safety measures and safeguards. This information shall include inherent safety measures and safeguards that have been: (A) achieved in practice by the petroleum refining industry and related industrial sectors; or, (B) required or recommended for the petroleum refining industry, and related industrial sectors, by a federal or state agency, or local California agency, in a regulation or report. | 19 CCR 4.5 2762.13(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 240 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Ensured HCA team complied with Section 2762.13(e) requirements | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the HCA team: (1) Include all risk-relevant data for each process or recommendation, including incident investigation reports pursuant to section 2762.9; (2) Identify, characterize and prioritize each process safety hazard. (3) Identify, analyze, and document all inherent safety measures and safeguards (or where appropriate, combinations of measures and safeguards) in an iterative manner to reduce each hazard to the greatest extent feasible. Identify, analyze, and document relevant, publicly available information on inherent safety measures and safeguards. This information shall include inherent safety measures and safeguards that have been: (A) achieved in practice by the petroleum refining industry and related industrial sectors; or, (B) required or recommended for the petroleum refining industry, and related industrial sectors, by a federal or state agency, or local California agency, in a regulation or report. |  |  | OBSERVATION: Owner/operator failed to ensure the HCA team: include all risk-relevant data for each process or recommendation, including incident investigation reports; identify, characterize and prioritize each process safety hazard; identify, analyze, and document all inherent safety measures and safeguards in an iterative manner to reduce each hazard to the greatest extent feasible; identify, analyze, and document relevant, publicly available information on inherent safety measures and safeguards; include inherent safety measures and safeguards that have been achieved in practice by the petroleum refining industry and related industrial sectors; or, required or recommended for the petroleum refining industry, and related industrial sectors, by a federal or state agency, or local California agency, in a regulation or report. CORRECTIVE ACTION: Ensure HCA team include above requirements above and submit documentation that demonstrates compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010220 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Recommendations | Failure to ensure the team develop written recommendations to eliminate hazards to the greatest extent feasible using first order inherent safety measures for each process safety hazard identified using the analysis required by subsection 2762.13(e). Failure to ensure the team develop written recommendations to reduce any remaining hazards to the greatest extent feasible using second order inherent safety measures. Failure to ensure the team also develop written recommendations to address any remaining risks in the following sequence and priority order, as necessary: (1) Effectively reduce remaining risks using passive safeguards; (2) Effectively reduce remaining risks using active safeguards; (3) Effectively reduce remaining risks using procedural safeguards. | 19 CCR 4.5 2762.13(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 241 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Ensured HCA team develop written recommendations | 49 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the team develop written recommendations to eliminate hazards to the greatest extent feasible using first order inherent safety measures for each process safety hazard identified using the analysis required by subsection 2762.13(e). Failure to ensure the team develop written recommendations to reduce any remaining hazards to the greatest extent feasible using second order inherent safety measures. Failure to ensure the team also develop written recommendations to address any remaining risks in the following sequence and priority order, as necessary: (1) Effectively reduce remaining risks using passive safeguards; (2) Effectively reduce remaining risks using active safeguards; (3) Effectively reduce remaining risks using procedural safeguards. |  |  | OBSERVATION: Owner/operator failed to ensure the team develop written recommendations to eliminate hazards to the greatest extent feasible using first order inherent safety measures for each process safety hazard identified using the analysis required by subsection 2762.13(e). Failure to ensure the team develop written recommendations to reduce any remaining hazards to the greatest extent feasible using second order inherent safety measures. Failure to ensure the team also develop written recommendations to address any remaining risks in the following sequence and priority order, as necessary: (1) Effectively reduce remaining risks using passive safeguards; (2) Effectively reduce remaining risks using active safeguards; (3) Effectively reduce remaining risks using procedural safeguards. CORRECTIVE ACTION: Ensure HCA team develops written recommendations and submit a copy of the recommendations to UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010221 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Report | Failure to ensure the HCA team complete an HCA report within 90 calendar days following development of the recommendations. Failure to ensure the report includes: (1) A description of the composition, experience, and expertise of the members of the team that performed the HCA; (2) A description of the methodology used by the team; (3) A description of each process safety hazard analyzed by the team, pursuant to subsection 2762.13 (e)(2); (4) A description of the inherent safety measure(s) and safeguards analyzed by the team, pursuant to subsection 2762.13 (e)(3); and (5) The rationale for the inherent safety measures and safeguards recommended by the team for each process safety hazard, pursuant to subsection 2762.13 (f). | 19 CCR 4.5 2762.13(g) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 242 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Ensured HCA team complete an HCA report | 40 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the HCA team complete an HCA report within 90 calendar days following development of the recommendations. Failure to ensure the report includes: (1) A description of the composition, experience, and expertise of the members of the team that performed the HCA; (2) A description of the methodology used by the team; (3) A description of each process safety hazard analyzed by the team, pursuant to subsection 2762.13 (e)(2); (4) A description of the inherent safety measure(s) and safeguards analyzed by the team, pursuant to subsection 2762.13 (e)(3); and (5) The rationale for the inherent safety measures and safeguards recommended by the team for each process safety hazard, pursuant to subsection 2762.13 (f). |  |  | OBSERVATION: Owner/operator failed to: ensure the HCA team complete an HCA report within 90 calendar days following development of the recommendations; ensure the report includes: (1) A description of the composition, experience, and expertise of the members of the team that performed the HCA; (2) A description of the methodology used by the team; (3) A description of each process safety hazard analyzed by the team, pursuant to subsection 2762.13 (e)(2); (4) A description of the inherent safety measure(s) and safeguards analyzed by the team, pursuant to subsection 2762.13 (e)(3); and (5) The rationale for the inherent safety measures and safeguards recommended by the team for each process safety hazard, pursuant to subsection 2762.13 (f). CORRECTIVE ACTION: Ensure the HCA team complete an HCA report within 90 calendar days following development of the recommendations and includes the above requirements. Submit a copy of the HCA report to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010222 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Corrective Action Work Process | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the HCA team's finding and recommendations determining corrective action for implementation, tracking to completion, and documentation of closeout. | 19 CCR 4.5 2762.13(h) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 243 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Followed corrective action work process when resolving HCA team's finding(s) | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the HCA team's finding and recommendations determining corrective action for implementation, tracking to completion, and documentation of closeout. |  |  | OBSERVATION: Owner/operator failed to follow the corrective action work process documented in subsections 2762.16 (d) and (e) when resolving the HCA team's finding and recommendations determining corrective action for implementation, tracking to completion, and documentation of closeout. CORRECTIVE ACTION: Follow the corrective action work process for HCA team's resolution of recommendations and submit documentation to demonstrate compliance to the UPA . | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010223 |  |  | Program level 4: Hierarchy of Hazard Control Analysis - Retention | Failure to retain all HCA reports for the life of each process. | 19 CCR 4.5 2762.13(i) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 244 | Program 4 Prevention Program | Hierarchy of Hazard Control Analysis | Retained all HCA reports for the life of each process | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to retain all HCA reports for the life of each process. |  |  | OBSERVATION: Owner/operator failed to retain all HCA reports for the life of each process. CORRECTIVE ACTION: Retain all HCA reports and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010224 |  |  | Program level 4: Process Safety Culture Assessment - Program | Failure to develop, implement and maintain an effective Process Safety Culture Assessment (PSCA) program. | 19 CCR 4.5 2762.14(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 245 | Program 4 Prevention Program | Process Safety Culture Assessment | Developed, implemented, and maintained an effective PSCA program | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement and maintain an effective Process Safety Culture Assessment (PSCA) program. |  |  | OBSERVATION: Owner/operator failed to develop, implement and maintain an effective Process Safety Culture Assessment (PSCA) program. CORRECTIVE ACTION: Develop, implement, and maintain an effective PSCA program. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010225 |  |  | Program level 4: Process Safety Culture Assessment - Report and Action Plan | Failure to conduct an effective PSCA and produce a written report and action plan within eighteen (18) months following the effective date of Article 6.5 and at least once, every five (5) years thereafter. Failure to include an evaluation of the effectiveness of: (1) The owner or operator's hazard reporting program; (2) The owner or operator's response to reports of hazards; (3) The owner or operator's procedures to ensure that incentive programs do not discourage reporting of hazards; (4) The owner or operator's procedures to ensure that process safety is prioritized during upset or emergency conditions; and (5) Management commitment and leadership. | 19 CCR 4.5 2762.14(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 246 | Program 4 Prevention Program | Process Safety Culture Assessment | Conducted an effective PSCA and produced a written report and action plan | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to conduct an effective PSCA and produce a written report and action plan within eighteen (18) months following the effective date of Article 6.5 and at least once, every five (5) years thereafter. Failure to include an evaluation of the effectiveness of: (1) The owner or operator's hazard reporting program; (2) The owner or operator's response to reports of hazards; (3) The owner or operator's procedures to ensure that incentive programs do not discourage reporting of hazards; (4) The owner or operator's procedures to ensure that process safety is prioritized during upset or emergency conditions; and (5) Management commitment and leadership. |  |  | OBSERVATION: Owner/operator failed to: conduct an effective PSCA and produce a written report and action plan within eighteen (18) months following the effective date of Article 6.5 and at least once, every five (5) years thereafter; failed to include an evaluation of the effectiveness of the following elements of process safety leadership: 1) The owner or operator's hazard reporting program; (2) The owner or operator's response to reports of hazards; (3) The owner or operator's procedures to ensure that incentive programs do not discourage reporting of hazards; (4) The owner or operator's procedures to ensure that process safety is prioritized during upset or emergency conditions; and (5) Management commitment and leadership. CORRECTIVE ACTION: Conduct an effective PSCA and submit a written report and action plan to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010226 |  |  | Program level 4: Process Safety Culture Assessment - Team Qualifications | Failure to ensure the PSCA is conducted or overseen by a team that includes at least one person knowledgeable in refinery operations and at least one employee representative. Failure to provide for employee participation in the development and implementation of the PSCA, report, and recommendations, pursuant to section 2762.10. Failure to ensure the team consult with at least one employee or another individual with expertise in assessing process safety culture in the petroleum refining industry. | 19 CCR 4.5 2762.14(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 247 | Program 4 Prevention Program | Process Safety Culture Assessment | Ensured the PSCA team complied with qualifications and requirements | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PSCA is conducted or overseen by a team that includes at least one person knowledgeable in refinery operations and at least one employee representative. Failure to provide for employee participation in the development and implementation of the PSCA, report, and recommendations, pursuant to section 2762.10. Failure to ensure the team consult with at least one employee or another individual with expertise in assessing process safety culture in the petroleum refining industry. |  |  | OBSERVATION: Owner/operator failed to: ensure the PSCA is conducted or overseen by a team that includes at least one person knowledgeable in refinery operations and at least one employee representative; provide for employee participation in the development and implementation of the PSCA, report, and recommendations, pursuant to section 2762.10; ensure the team consult with at least one employee or another individual with expertise in assessing process safety culture in the petroleum refining industry. CORRECTIVE ACTION: Ensure the PSCA team meets the above requirements and provide documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010227 |  |  | Program level 4: Process Safety Culture Assessment - Report Schedule and Content | Failure to ensure the PSCA team develop a written report within 90 calendar days of completion of the assessment. Failure to ensure the report includes: (1) The method(s) used to assess the process safety culture; (2) The conclusions of the process safety culture assessment; (3) The rationale for the conclusions; and (4) The recommendations to address the findings from the PSCA. | 19 CCR 4.5 2762.14(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 248 | Program 4 Prevention Program | Process Safety Culture Assessment | Ensured the PSCA team develop a written report and included requirements | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PSCA team develop a written report within 90 calendar days of completion of the assessment. Failure to ensure the report includes: (1) The method(s) used to assess the process safety culture; (2) The conclusions of the process safety culture assessment; (3) The rationale for the conclusions; and (4) The recommendations to address the findings from the PSCA. |  |  | OBSERVATION: Owner/operator failed to: ensure the PSCA team develop a written report within 90 calendar days of completion of the assessment; ensure the report includes: (1) The method(s) used to assess the process safety culture; (2) The conclusions of the process safety culture assessment; (3) The rationale for the conclusions; and (4) The recommendations to address the findings from the PSCA. CORRECTIVE ACTION: Ensure the PSCA team develop a written report that meets the above requirements and submit a copy of the report to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010228 |  |  | Program level 4: Process Safety Culture Assessment - Corrective Actions | Failure to develop corrective actions based on the PSCA team recommendations and implement the corrective actions within twenty-four (24) months of the completion of the report. | 19 CCR 4.5 2762.14(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 249 | Program 4 Prevention Program | Process Safety Culture Assessment | Developed and implemented PSCA corrective actions | 51 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop corrective actions based on the PSCA team recommendations and implement the corrective actions within twenty-four (24) months of the completion of the report. |  |  | OBSERVATION: Owner/operator failed to develop corrective actions based on the PSCA team recommendations and implement the corrective actions within twenty-four (24) months of the completion of the report. CORRECTIVE ACTION: Develop and implement the corrective actions based on the PSCA team recommendations within (24) months of the completion of the report and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010229 |  |  | Program level 4: Process Safety Culture Assessment - Corrective Action Assessment | Failure to ensure the PSCA team conduct a written interim assessment of the implementation and effectiveness of each PSCA corrective action within three (3) years following the completion of the PSCA report. For a corrective action found to be ineffective, failed to implement changes necessary to ensure effectiveness in a timely manner not to exceed six months. | 19 CCR 4.5 2762.14(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 250 | Program 4 Prevention Program | Process Safety Culture Assessment | Ensured the PSCA team conducted a written corrective action assessment | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PSCA team conduct a written interim assessment of the implementation and effectiveness of each PSCA corrective action within three (3) years following the completion of the PSCA report. For a corrective action found to be ineffective, failed to implement changes necessary to ensure effectiveness in a timely manner not to exceed six months. |  |  | OBSERVATION: Owner/operator failed to ensure the PSCA team conduct a written interim assessment of the implementation and effectiveness of each PSCA corrective action within three (3) years following the completion of the PSCA report. For a corrective action found to be ineffective, failed to implement changes necessary to ensure effectiveness in a timely manner not to exceed six months. CORRECTIVE ACTION: Ensure the PSCA team conduct a written interim assessment of the implementation and effectiveness of each PSCA corrective action within three (3) years following the completion of the PSCA report. For a corrective action found to be ineffective, implement changes necessary to ensure effectiveness in a timely manner not to exceed six months, and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010230 |  |  | Program level 4: Process Safety Culture Assessment - Certification | Failure to ensure the stationary source manager or his or her designee serve as signatory to all process safety culture assessment reports and corrective action plans. | 19 CCR 4.5 2762.14(g) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 251 | Program 4 Prevention Program | Process Safety Culture Assessment | Ensured the refinery manager certifies all PSCA reports and corrective actions | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the stationary source manager or his or her designee serve as signatory to all process safety culture assessment reports and corrective action plans. |  |  | OBSERVATION: Owner/operator failed to ensure the stationary source manager or his or her designee serve as signatory to all process safety culture assessment reports and corrective action plans. CORRECTIVE ACTION: Ensure the stationary source manager or his or her designee serve as signatory to all process safety culture assessment reports and corrective action plans and provide signed copies of the documentation to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010231 |  |  | Program level 4: Process Safety Culture Assessment - Employee Communication | Failure to ensure the PSCA report and action plan and the three year interim assessment are communicated and made available to employees, their representatives and participating contractors within 60 calendar days of the completion of the report. | 19 CCR 4.5 2762.14(h) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 252 | Program 4 Prevention Program | Process Safety Culture Assessment | Ensured the PSCA report, action plan and interim assessment are communicated and made available | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the PSCA report and action plan and the three year interim assessment are communicated and made available to employees, their representatives and participating contractors within 60 calendar days of the completion of the report. |  |  | OBSERVATION: Owner/operator failed to ensure the PSCA report and action plan and the three year interim assessment are communicated and made available to employees, their representatives and participating contractors within 60 calendar days of the completion of the report. CORRECTIVE ACTION: Ensure the PSCA report and action plan and the three year interim assessment are communicated and made available to employees, their representatives and participating contractors within 60 calendar days of the completion of the report. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010232 |  |  | Program level 4: Human Factors Program - Plan | Failure to develop, implement and maintain an effective written Human Factors Program within eighteen (18) months of the effective date of Article 6.5. | 19 CCR 4.5 2762.15(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 253 | Program 4 Prevention Program | Human Factors Program | Developed, implemented, and maintained an effective written Human Factors Program | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop, implement and maintain an effective written Human Factors Program within eighteen (18) months of the effective date of Article 6.5. |  |  | OBSERVATION: Owner/operator failed to develop, implement and maintain an effective written Human Factors Program within eighteen (18) months of the effective date of Article 6.5. CORRECTIVE ACTION: Develop, implement and maintain an effective written Human Factors Program and provide documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010233 |  |  | Program level 4: Human Factors Program - Analysis | Failure to include a written analysis of human factors where relevant in the design phase of a major change, incident investigations, PHAs, MOOCs, and HCAs. Failure to ensure the analysis includes a description of selected methodologies and criteria for their use. | 19 CCR 4.5 2762.15(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 254 | Program 4 Prevention Program | Human Factors Program | Included a written human factors analysis | 42 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to include a written analysis of human factors where relevant in the design phase of a major change, incident investigations, PHAs, MOOCs, and HCAs. Failure to ensure the analysis includes a description of selected methodologies and criteria for their use. |  |  | OBSERVATION: Owner/operator failed to include a written analysis of human factors where relevant in the design phase of a major change, incident investigations, PHAs, MOOCs, and HCAs; failed to ensure the analysis includes a description of selected methodologies and criteria for their use. CORRECTIVE ACTION: Include a written analysis of human factors where relevant in the design phase of a major change, incident investigations, PHAs, MOOCs, and HCAs; Ensure the analysis includes a description of selected methodologies and criteria for their use. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010234 |  |  | Program level 4: Human Factors Program - Evaluation Method and Criteria | Failure to ensure the human factors analysis use an effective method of evaluating the following: staffing levels; the complexity of tasks; the length of time needed to complete tasks; the level of training, experience, and competency of employees; the human-machine and human-system interface; the physical challenges of the work environment in which the task is performed; employee fatigue, including contractor employees and other effects of shiftwork and overtime; communication systems; and the understandability and clarity of operating and maintenance procedures. Failure to ensure the human factors analysis of process controls includes the following areas: (1) Error proof mechanisms; (2) Automatic Alerts; and (3) Automatic System Shutdowns. | 19 CCR 4.5 2762.15(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 255 | Program 4 Prevention Program | Human Factors Program | Ensured the human factors analysis use an effective evaluation method | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the human factors analysis use an effective method of evaluating the following: staffing levels; the complexity of tasks; the length of time needed to complete tasks; the level of training, experience, and competency of employees; the human-machine and human-system interface; the physical challenges of the work environment in which the task is performed; employee fatigue, including contractor employees and other effects of shiftwork and overtime; communication systems; and the understandability and clarity of operating and maintenance procedures. Failure to ensure the human factors analysis of process controls includes the following areas: (1) Error proof mechanisms; (2) Automatic Alerts; and (3) Automatic System Shutdowns. |  |  | OBSERVATION: Owner/operator failed to ensure the human factors analysis use an effective method of evaluating the following: staffing levels; the complexity of tasks; the length of time needed to complete tasks; the level of training, experience, and competency of employees; the human-machine and human-system interface; the physical challenges of the work environment in which the task is performed; employee fatigue, including contractor employees and other effects of shiftwork and overtime; communication systems; and the understandability and clarity of operating and maintenance procedures. Failure to ensure the human factors analysis of process controls includes the following areas: (1) Error proof mechanisms; (2) Automatic Alerts; and (3) Automatic System Shutdowns. CORRECTIVE ACTION: Ensure the human factors analysis complies with the above requirements and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010235 |  |  | Program level 4: Human Factors Program - New and Revised O & M Procedures | Failure to include an analysis of human factors in new and revised operating and maintenance procedures. | 19 CCR 4.5 2762.15(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 256 | Program 4 Prevention Program | Human Factors Program | Included a human factors analysis in new and revised operating and maintenance procedures | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to include an analysis of human factors in new and revised operating and maintenance procedures. |  |  | OBSERVATION: Owner/operator failed to include an analysis of human factors in new and revised operating and maintenance procedures. CORRECTIVE ACTION: Include a human factors analysis in new and revised operating and maintenance procedures and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010236 |  |  | Program level 4: Human Factors Program - Existing O & M Procedures Schedule | Failure to develop a schedule for revising existing operating and maintenance procedures based on a human factors analysis. Failure to complete no less than fifty (50) percent of assessments and revisions within three (3) years following the effective date of Article 6.5 and one hundred (100) percent within five (5) years. | 19 CCR 4.5 2762.15(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 257 | Program 4 Prevention Program | Human Factors Program | Developed a schedule for revising existing operating and maintenance procedures based on a HFA | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop a schedule for revising existing operating and maintenance procedures based on a human factors analysis. Failure to complete no less than fifty (50) percent of assessments and revisions within three (3) years following the effective date of Article 6.5 and one hundred (100) percent within five (5) years. |  |  | OBSERVATION: Owner/operator failed to develop a schedule for revising existing operating and maintenance procedures based on a human factors analysis; failed to complete no less than fifty (50) percent of assessments and revisions within three (3) years following the effective date of Article 6.5 and one hundred (100) percent within five (5) years. CORRECTIVE ACTION: Develop a schedule for revising existing operating and maintenance procedures based on a human factors analysis; complete no less than fifty (50) percent of assessments and revisions within three (3) years following the effective date of Article 6.5 and one hundred (100) percent within five (5) years. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010237 |  |  | Program level 4: Human Factors Program - Training | Failure to train all of their employees that have process and process equipment responsibilities on the Human Factors Program. | 19 CCR 4.5 2762.15(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 258 | Program 4 Prevention Program | Human Factors Program | Trained employees with process and process equipment responsibilities on the Human Factors Program | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to train all of their employees that have process and process equipment responsibilities on the Human Factors Program. |  |  | OBSERVATION: Owner/operator failed to train all of their employees that have process and process equipment responsibilities on the Human Factors Program. CORRECTIVE ACTION: Train all employees that have process and process equipment responsibilities on the Human Factors Program and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010238 |  |  | Program level 4: Human Factors Program - Employee Participation | Failure to provide for employee participation in the development and implementation of the Human Factors Program, pursuant to section 2762.10. | 19 CCR 4.5 2762.15(g) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 259 | Program 4 Prevention Program | Human Factors Program | Provided for employee participation in development and implementation of the Human Factors Program | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide for employee participation in the development and implementation of the Human Factors Program, pursuant to section 2762.10. |  |  | OBSERVATION: Owner/operator failed to provide for employee participation in the development and implementation of the Human Factors Program, pursuant to section 2762.10. CORRECTIVE ACTION: Provide for employee participation in the development and implementation of the Human Factors Program, pursuant to section 2762.10 and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010239 |  |  | Program level 4: Human Factors Program - Availability | Failure to make available and provide on request a copy of the written Human Factors Program to employees and their representatives, and to affected contractors, contractor employees, and contractor representatives. | 19 CCR 4.5 2762.15(h) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 260 | Program 4 Prevention Program | Human Factors Program | Provided a copy of the written Human factors Program to employees and contractors | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to make available and provide on request a copy of the written Human Factors Program to employees and their representatives, and to affected contractors, contractor employees, and contractor representatives. |  |  | OBSERVATION: Owner/operator failed to make available and provide on request a copy of the written Human Factors Program to employees and their representatives, and to affected contractors, contractor employees, and contractor representatives. CORRECTIVE ACTION: Make available and provide on request a copy of the written Human Factors Program to employees and their representatives, and to affected contractors, contractor employees, and contractor representatives. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010240 |  |  | Program level 4: Accidental Release Prevention Program Management System - Plan | Failure to develop and implement an effective written Accidental Release Prevention Program (ARP) Management System. Failure to review and update the ARP Management System every three (3) years. Failure to designate the stationary source manager as the person with authority and responsibility for compliance with section 2762.16, and maintain process safety goals that support continuous improvement. | 19 CCR 4.5 2762.16(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 261 | Program 4 Prevention Program | Management System | Developed and implemented an effective ARP Management System. | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement an effective written Accidental Release Prevention Program (ARP) Management System. Failure to review and update the ARP Management System every three (3) years. Failure to designate the stationary source manager as the person with authority and responsibility for compliance with section 2762.16, and maintain process safety goals that support continuous improvement. |  |  | OBSERVATION: Owner/operator failed to develop and implement an effective written Accidental Release Prevention Program (ARP) Management System. Failure to review and update the ARP Management System every three (3) years; failed to designate the stationary source manager as the person with authority and responsibility for compliance with section 2762.16, and maintain process safety goals that support continuous improvement. CORRECTIVE ACTION: Develop and implement an effective written Accidental Release Prevention Program (ARP) Management System. Review and update the ARP Management System every three (3) years. Designate the stationary source manager as the person with authority and responsibility for compliance with section 2762.16, and maintain process safety goals that support continuous improvement. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010241 |  |  | Program level 4: Accidental Release Prevention Program Management System - Policies and Procedures | Failure to develop and maintain written ARP policies and procedures, as part of the ARP Management System, as described below: (1) Job descriptions of roles and responsibilities under each section of Article 6.5; (2) An organizational chart of management positions with responsibilities for each section of Article 6.5; (3) Written procedures for ensuring the effective communication of safety, operations, and maintenance information among and across process and maintenance personnel, contractors, support personnel, supervisors and senior management; (4) Policies and procedures to ensure that the findings, recommendations and corrective action of all sections in Article 6.5 and the ARP Management System are communicated effectively to employees and employee representatives; and (5) Policies and procedures to effectively provide for employee participation in all applicable sections in Article 6.5 as specified in section 2762.10. | 19 CCR 4.5 2762.16(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 262 | Program 4 Prevention Program | Management System | Developed and maintained written ARP policies and procedures as part of the ARP Management System | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and maintain written ARP policies and procedures, as part of the ARP Management System, as described below: (1) Job descriptions of roles and responsibilities under each section of Article 6.5; (2) An organizational chart of management positions with responsibilities for each section of Article 6.5; (3) Written procedures for ensuring the effective communication of safety, operations, and maintenance information among and across process and maintenance personnel, contractors, support personnel, supervisors and senior management; (4) Policies and procedures to ensure that the findings, recommendations and corrective action of all sections in Article 6.5 and the ARP Management System are communicated effectively to employees and employee representatives; and (5) Policies and procedures to effectively provide for employee participation in all applicable sections in Article 6.5 as specified in section 2762.10. |  |  | OBSERVATION: Owner/operator failed to develop and maintain written ARP policies and procedures, as part of the ARP Management System, as follows: (1) Job descriptions of roles and responsibilities; (2) An organizational chart of management positions with responsibilities; (3) Written procedures for ensuring the effective communication of safety, operations, and maintenance information among and across process and maintenance personnel, contractors, support personnel, supervisors and senior management; (4) Policies and procedures to ensure that the findings, recommendations and corrective action of all sections in Article 6.5 and the ARP Management System are communicated effectively to employees and employee representatives; and (5) Policies and procedures to effectively provide for employee participation. CORRECTIVE ACTION: Develop and maintain written policies and procedures and submit documentation to demonstrate compliance with the above requirements to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010242 |  |  | Program level 4: Accidental Release Prevention Program Management System - Tracking Changes | Failure to track and document all changes to program elements under Article 6.5, as part of the ARP Management System. | 19 CCR 4.5 2762.16(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 263 | Program 4 Prevention Program | Management System | Tracked and documented all changes to program elements as part of the ARP Management System | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to track and document all changes to program elements under Article 6.5, as part of the ARP Management System. |  |  | OBSERVATION: Owner/operator failed to track and document all changes to program elements under Article 6.5, as part of the ARP Management System. CORRECTIVE ACTION: Track and document all changes to program elements and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010243 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Work Process | Failure to develop and document a corrective action work process to address findings and recommendations resulting from program elements. Failure to ensure the corrective action work plan for PSCAs is governed by section 2762.14. Failure to ensure the corrective action work process includes the requirements in subsection 2762.16 (e). | 19 CCR 4.5 2762.16(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 264 | Program 4 Prevention Program | Management System | Developed and documented a corrective action work process to address recommendations | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and document a corrective action work process to address findings and recommendations resulting from program elements. Failure to ensure the corrective action work plan for PSCAs is governed by section 2762.14. Failure to ensure the corrective action work process includes the requirements in subsection 2762.16 (e). |  |  | OBSERVATION: Owner/operator failed to develop and document a corrective action work process to address findings and recommendations resulting from program elements. Failure to ensure the corrective action work plan for PSCAs is governed by section 2762.14. Failure to ensure the corrective action work process includes the requirements in subsection 2762.16 (e). CORRECTIVE ACTION: Submit documentation to demonstrate compliance with the above requirements to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010244 |  |  | Program level 4: Accidental Release Prevention Program Management System - Recommendations Standards | Failure to comply with the following standards for findings and recommendations for the PHA, DMR, HCA, Incident Investigation, Compliance Audit and SPA: (1) All findings and recommendations must be provided by the team to the owner or operator at the earliest opportunity, but no later than 14 calendar days after recommendation and findings are complete. (2) The owner or operator may reject a team recommendation if the owner or operator can demonstrate in writing that one of the following applies: (A) The analysis upon which the recommendation is based contains material factual errors; (B) The recommendation is not relevant to process safety; or (C) The recommendation is infeasible; however, a determination of infeasibility shall not be based solely on cost. (3) The owner or operator may change a team recommendation if the owner or operator can demonstrate in writing that an alternative inherent safety measure would provide an equivalent or higher order of inherent safety, or, for a safeguard recommendation, an alternative safeguard would provide an equally or more effective level of protection. | 19 CCR 4.5 2762.16(e)(1), 2762.16(e)(2), 2762.16(e)(3) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 265 | Program 4 Prevention Program | Management System | Complied with standards for PHA, DMR, HCA, Incident Investigation, Audit, and SPA recommendations | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to comply with the following standards for findings and recommendations for the PHA, DMR, HCA, Incident Investigation, Compliance Audit and SPA: (1) All findings and recommendations must be provided by the team to the owner or operator at the earliest opportunity, but no later than 14 calendar days after recommendation and findings are complete. (2) The owner or operator may reject a team recommendation if the owner or operator can demonstrate in writing that one of the following applies: (A) The analysis upon which the recommendation is based contains material factual errors; (B) The recommendation is not relevant to process safety; or (C) The recommendation is infeasible; however, a determination of infeasibility shall not be based solely on cost. (3) The owner or operator may change a team recommendation if the owner or operator can demonstrate in writing that an alternative inherent safety measure would provide an equivalent or higher order of inherent safety, or, for a safeguard recommendation, an alternative safeguard would provide an equally or more effective level of protection. |  |  | OBSERVATION: Owner/operator (o/o) failed to comply with the following standards for recommendations for the PHA, DMR, HCA, Incident Investigation, Compliance Audit and SPA: All recommendations must be provided by the team to the o/o no later than 14 calendar days after completion; o/o may reject a team recommendation if the o/o can demonstrate in writing one of the following: analysis for the recommendation contains material factual errors; the recommendation is not relevant to process safety; or the recommendation is infeasible; however, infeasibility shall not be based solely on cost. The o/o may change a team recommendation if the o/o can demonstrate in writing that an alternative inherent safety measure would provide an equivalent or higher order of inherent safety, or, for a safeguard recommendation, an alternative safeguard would provide an equally or more effective level of protection. CORRECTIVE ACTION: Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010245 |  |  | Program level 4: Accidental Release Prevention Program Management System - Recommendation Change or Rejection | Failure to document where any of the conditions in subsection 2762.16 (e)(2) or (e)(3) is applied for the purpose of changing or rejecting a team recommendation. Failure to ensure that each recommendation that is changed or rejected by the owner or operator is communicated to onsite team members for comment and made available to offsite team members for comment. | 19 CCR 4.5 2762.16(e)(4) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 266 | Program 4 Prevention Program | Management System | Documented applied conditions for changing or rejecting a team recommendation | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document where any of the conditions in subsection 2762.16 (e)(2) or (e)(3) is applied for the purpose of changing or rejecting a team recommendation. Failure to ensure that each recommendation that is changed or rejected by the owner or operator is communicated to onsite team members for comment and made available to offsite team members for comment. |  |  | OBSERVATION: Owner/operator failed to document where any of the conditions in subsection 2762.16 (e)(2) or (e)(3) is applied for the purpose of changing or rejecting a team recommendation; failed to ensure that each recommendation that is changed or rejected by the owner or operator is communicated to onsite team members for comment and made available to offsite team members for comment. CORRECTIVE ACTION: Document where any of the conditions in subsection 2762.16 (e)(2) or (e)(3) is applied for changing or rejecting a team recommendation; ensure that each recommendation that is changed or rejected is communicated to onsite team members for comment and made available to offsite team members for comment. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010246 |  |  | Program level 4: Accidental Release Prevention Program Management System - Recommendation Comment Documentation | Failure to document any written comments from all team members on any rejected or changed findings and recommendations. | 19 CCR 4.5 2762.16(e)(5) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 267 | Program 4 Prevention Program | Management System | Documented written comments from all team members on rejected or changed recommendations | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document any written comments from all team members on any rejected or changed findings and recommendations. |  |  | OBSERVATION: Owner/operator failed to document any written comments from all team members on any rejected or changed findings and recommendations. CORRECTIVE ACTION: Document any written comments from all team members on any rejected or changed findings and recommendations and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010247 |  |  | Program level 4: Accidental Release Prevention Program Management System - Recommendation Documentation/ Communication | Failure to document a final decision for each recommendation and communicate it to onsite team members and make it available to offsite team members. | 19 CCR 4.5 2762.16(e)(6) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 268 | Program 4 Prevention Program | Management System | Documented decision for each recommendation and communicated it to team members | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document a final decision for each recommendation and communicate it to onsite team members and make it available to offsite team members. |  |  | OBSERVATION: Owner/operator failed to document a final decision for each recommendation and communicate it to onsite team members and make it available to offsite team members. CORRECTIVE ACTION: Document a final decision for each recommendation and communicate it to onsite team members and make it available to offsite team members. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010248 |  |  | Program level 4: Accidental Release Prevention Program Management System - Recommendation Target Dates | Failure to develop and document corrective actions to implement each accepted recommendation, including documentation of a completion date and assignment of responsibility for completion of each corrective action. Failure to ensure all target dates are consistent with the requirements of subsections 2762.16(e)(10) through (13) for completion of corrective actions. | 19 CCR 4.5 2762.16(e)(7) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 269 | Program 4 Prevention Program | Management System | Developed and documented corrective actions to implement each accepted recommendation | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and document corrective actions to implement each accepted recommendation, including documentation of a completion date and assignment of responsibility for completion of each corrective action. Failure to ensure all target dates are consistent with the requirements of subsections 2762.16(e)(10) through (13) for completion of corrective actions. |  |  | OBSERVATION: Owner/operator failed to: develop and document corrective actions to implement each accepted recommendation, including documentation of a completion date and assignment of responsibility for completion of each corrective action; ensure all target dates are consistent with the requirements of subsections 2762.16(e)(10) through (13) for completion of corrective actions. CORRECTIVE ACTION: Develop and document corrective actions to implement each accepted recommendation, including documentation of a completion date and assignment of responsibility for completion of each corrective action; ensure all target dates are consistent with the requirements of subsections 2762.16(e)(10) through (13) for completion of corrective actions. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010249 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Update | Failure to ensure that a corrective action requiring revalidation or update of any applicable PHA, HCA, DMR, or SPA is subject to the corrective action requirements in subsections 2762.16 (9) and (11) through (12). Failure to promptly append any revalidated or updated PHA, DMR, HCA, or SPA, to the applicable report. | 19 CCR 4.5 2762.16(e)(8) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 270 | Program 4 Prevention Program | Management System | Ensured a corrective action requiring revalidation is promptly appended to the applicable report | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that a corrective action requiring revalidation or update of any applicable PHA, HCA, DMR, or SPA is subject to the corrective action requirements in subsections 2762.16 (9) and (11) through (12). Failure to promptly append any revalidated or updated PHA, DMR, HCA, or SPA, to the applicable report. |  |  | OBSERVATION: Owner/operator failed to ensure that a corrective action requiring revalidation or update of any applicable PHA, HCA, DMR, or SPA is subject to the corrective action requirements in subsections 2762.16 (9) and (11) through (12). Failure to promptly append any revalidated or updated PHA, DMR, HCA, or SPA, to the applicable report. CORRECTIVE ACTION: Ensure that a corrective action requiring revalidation or update of any applicable PHA, HCA, DMR, or SPA is subject to the corrective action requirements in subsections 2762.16 (9) and (11) through (12). Promptly append any revalidated or updated PHA, DMR, HCA, or SPA, to the applicable report. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010250 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Completion Dates | Failure to promptly complete all corrective actions and comply with the completion dates required by subsection 2762.16 (e). Failure to conduct a MOC pursuant to section 2762.6 for any proposed change to a completion date. Failure to make all completion dates available, upon request, to all affected operation and maintenance employees and employee representatives. | 19 CCR 4.5 2762.16(e)(9) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 271 | Program 4 Prevention Program | Management System | Completed all corrective actions and completion dates. Conducted MOC for completion date change. | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to promptly complete all corrective actions and comply with the completion dates required by subsection 2762.16 (e). Failure to conduct a MOC pursuant to section 2762.6 for any proposed change to a completion date. Failure to make all completion dates available, upon request, to all affected operation and maintenance employees and employee representatives. |  |  | OBSERVATION: Owner/operator failed to: promptly complete all corrective actions and comply with the completion dates required by subsection 2762.16 (e); conduct a MOC pursuant to section 2762.6 for any proposed change to a completion date; make all completion dates available, upon request, to all affected operation and maintenance employees and employee representatives. CORRECTIVE ACTION: Promptly complete all corrective actions as required above and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010251 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Prioritization | Failure to prioritize and promptly complete corrective actions addressing process safety hazards, either through permanent corrections or interim safeguards sufficient to prevent the potential for a major incident, pending permanent corrections. | 19 CCR 4.5 2762.16(e)(10) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 272 | Program 4 Prevention Program | Management System | Prioritized and promptly completed corrective actions addressing process safety hazards | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prioritize and promptly complete corrective actions addressing process safety hazards, either through permanent corrections or interim safeguards sufficient to prevent the potential for a major incident, pending permanent corrections. |  |  | OBSERVATION: Owner/operator failed to prioritize and promptly complete corrective actions addressing process safety hazards, either through permanent corrections or interim safeguards sufficient to prevent the potential for a major incident, pending permanent corrections. CORRECTIVE ACTION: Prioritize and promptly complete corrective actions as required above and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010252 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Not Requiring Process Shutdown | Failure to ensure each corrective action except as specified under subsection 2762.16 (10) that does not require a process shutdown is completed within two and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. | 19 CCR 4.5 2762.16(e)(11) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 273 | Program 4 Prevention Program | Management System | Completed each corrective action not requiring process shutdown within two and half years | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure each corrective action except as specified under subsection 2762.16 (10) that does not require a process shutdown is completed within two and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. |  |  | OBSERVATION: Owner/operator failed to ensure each corrective action except as specified under subsection 2762.16 (10) that does not require a process shutdown is completed within two and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. CORRECTIVE ACTION: Ensure each corrective action except as specified under subsection 2762.16 (10) that does not require a process shutdown is completed within two and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010253 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action from Compliance Audit | Failure to ensure each corrective action from a compliance audit is completed within one and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. | 19 CCR 4.5 2762.16(e)(12) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 274 | Program 4 Prevention Program | Management System | Completed each compliance audit corrective action within one and half years | 76 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure each corrective action from a compliance audit is completed within one and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. |  |  | OBSERVATION: Owner/operator failed to ensure each corrective action from a compliance audit is completed within one and half years after the completion of the analysis or review unless the owner or operator demonstrates in writing that it is not feasible to do so. Failure to ensure each corrective action from an incident investigation is completed within one and half years after completion of the investigation unless the owner or operator demonstrates in writing that it is infeasible to do so. CORRECTIVE ACTION: Ensure each corrective action from a compliance audit and incident investigation is completed within one and half years unless the owner or operator demonstrates in writing that it is infeasible. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010254 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Requiring Process Shutdown | Failure to ensure each corrective action requiring a process shutdown is completed during the first regularly scheduled turnaround of the applicable process, subsequent to completion of the PHA, SPA, DMR, HCA, MOC, compliance audit or incident investigation, unless the owner or operator demonstrates in writing it is not feasible to do so. | 19 CCR 4.5 2762.16(e)(13) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 275 | Program 4 Prevention Program | Management System | Completed each corrective action requiring process shutdown during the first scheduled turnaround | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure each corrective action requiring a process shutdown is completed during the first regularly scheduled turnaround of the applicable process, subsequent to completion of the PHA, SPA, DMR, HCA, MOC, compliance audit or incident investigation, unless the owner or operator demonstrates in writing it is not feasible to do so. |  |  | OBSERVATION: Owner/operator failed to ensure each corrective action requiring a process shutdown is completed during the first regularly scheduled turnaround of the applicable process, subsequent to completion of the PHA, SPA, DMR, HCA, MOC, compliance audit or incident investigation, unless the owner or operator demonstrates in writing it is not feasible to do so. CORRECTIVE ACTION: Ensure each corrective action requiring a process shutdown is completed during the first regularly scheduled turnaround of the applicable process, subsequent to completion of the PHA, SPA, DMR, HCA, MOC, compliance audit or incident investigation, unless the owner or operator demonstrates in writing it is not feasible to do so. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010255 |  |  | Program level 4: Accidental Release Prevention Program Management System - Interim Safeguards | Failure to ensure that interim safeguards are sufficient to prevent the potential for a major incident, pending permanent corrections, where a corrective action cannot be implemented within the times described in 2762.16(e)(10) through (13). Failure to document all corrective actions delayed beyond the timelines established in subsection 2762.16 (e). The documentation shall include: (A) The rationale for deferring the corrective action(s); (B) The documentation required under the MOC process; (C) A timeline describing when the corrective action(s) will be implemented; and (D) An effective plan to make available the rationale and revised timeline to all affected employees and their representatives. | 19 CCR 4.5 2762.16(e)(14) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 276 | Program 4 Prevention Program | Management System | Ensured interim safeguards are sufficient to prevent a major incident | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that interim safeguards are sufficient to prevent the potential for a major incident, pending permanent corrections, where a corrective action cannot be implemented within the times described in 2762.16(e)(10) through (13). Failure to document all corrective actions delayed beyond the timelines established in subsection 2762.16 (e). The documentation shall include: (A) The rationale for deferring the corrective action(s); (B) The documentation required under the MOC process; (C) A timeline describing when the corrective action(s) will be implemented; and (D) An effective plan to make available the rationale and revised timeline to all affected employees and their representatives. |  |  | OBSERVATION: Owner/operator failed to: ensure that interim safeguards are sufficient to prevent the potential for a major incident, pending permanent corrections, where a corrective action cannot be implemented within the times described in 27622.16(e)(10) through (13); document all corrective actions delayed beyond the timelines established in subsection 2762.16(e); include the following documentation: (A) The rationale for deferring the corrective action(s); (B) The documentation required under the MOC process; (C) A timeline describing when the corrective action(s) will be implemented; and (D) An effective plan to make available the rationale and revised timeline to all affected employees and their representatives. CORRECTIVE ACTION: Ensure interim safeguards are sufficient to prevent the potential for a major incident, and delayed corrective actions meet the above requirements. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010256 |  |  | Program level 4: Accidental Release Prevention Program Management System - Corrective Action Annex | Failure to track each corrective action item to completion and append the documentation of completion to the applicable PHA, DMR, HCA, SPA, compliance audit, or incident investigation report. | 19 CCR 4.5 2762.16(e)(15) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 277 | Program 4 Prevention Program | Management System | Tracked each corrective action item to completion and appended the documentation | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to track each corrective action item to completion and append the documentation of completion to the applicable PHA, DMR, HCA, SPA, compliance audit, or incident investigation report. |  |  | OBSERVATION: Owner/operator failed to track each corrective action item to completion and append the documentation of completion to the applicable PHA, DMR, HCA, SPA, compliance audit, or incident investigation report. CORRECTIVE ACTION: Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010257 |  |  | Program level 4: Accidental Release Prevention Program Management System - Stop Work Procedures and Anonymous Hazard Reporting | Failure to develop and implement the following, within 90 calendar days of the effective date of Article 6.5, in consultation with employees and employees representatives: (1) Effective Stop Work procedures that ensure: (A) The authority of all employees, including employees of contractors, to refuse to perform a task where doing so could reasonably result in death or serious physical harm; (B) The authority of all employees, including employees of contractors, to recommend to the operator in charge of a unit that an operation or process be partially or completely shut-down, based on a process safety hazard; and, (C) The authority of the qualified operator in charge of a unit to partially or completely shut-down an operation or process, based on a process safety hazard. (2) Effective procedures to ensure the right of all employees, including employees of contractors, to anonymously report hazards. The owner or operator shall respond in writing within 30 calendar days to written hazard reports submitted by employees, employee representatives, contractors, employees of contractors and contractor employee representatives. The owner or operator shall prioritize and promptly respond to and correct hazards that present the potential for death or serious physical harm. | 19 CCR 4.5 2762.16(f)(1), 2762.16(f)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 278 | Program 4 Prevention Program | Management System | Developed and implemented effective Stop Work procedures and to anonymously report hazards | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and implement the following, within 90 calendar days of the effective date of Article 6.5, in consultation with employees and employees representatives: (1) Effective Stop Work procedures that ensure: (A) The authority of all employees, including employees of contractors, to refuse to perform a task where doing so could reasonably result in death or serious physical harm; (B) The authority of all employees, including employees of contractors, to recommend to the operator in charge of a unit that an operation or process be partially or completely shut-down, based on a process safety hazard; and, (C) The authority of the qualified operator in charge of a unit to partially or completely shut-down an operation or process, based on a process safety hazard. (2) Effective procedures to ensure the right of all employees, including employees of contractors, to anonymously report hazards. The owner or operator shall respond in writing within 30 calendar days to written hazard reports submitted by employees, employee representatives, contractors, employees of contractors and contractor employee representatives. The owner or operator shall prioritize and promptly respond to and correct hazards that present the potential for death or serious physical harm. |  |  | OBSERVATION: Owner/operator failed to: develop and implement the following, within 90 calendar days of the effective date of Article 6.5, in consultation with employees/employees representatives: (1) Effective Stop Work procedures (2) Effective procedures to ensure the right of all employees/contractor employees, to anonymously report hazards. CORRECTIVE ACTION: Develop and implement effective Stop Work procedures and procedures to ensure the right of all employees/contractor employees to anonymously report hazards. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010258 |  |  | Program level 4: Accidental Release Prevention Program Management System - Reporting System | Failure to develop a system, within 90 calendar days of the effective date of section 2762.16, to document and enable employees to report information pursuant to subsections 2762.16 (f)(1) and (f)(2). | 19 CCR 4.5 2762.16(g) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 279 | Program 4 Prevention Program | Management System | Developed a system to document and enable employees to report information | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop a system, within 90 calendar days of the effective date of section 2762.16, to document and enable employees to report information pursuant to subsections 2762.16 (f)(1) and (f)(2). |  |  | OBSERVATION: Owner/operator failed to develop a system, within 90 calendar days of the effective date of section 2762.16, to document and enable employees to report information pursuant to subsections 2762.16 (f)(1) and (f)(2). CORRECTIVE ACTION: Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010259 |  |  | Program level 4: Accidental Release Prevention Program Management System-Process Safety Performance Indicators | Failure to report process safety performance indicators listed in subsection (A) through (E) below to CalEPA and the UPA every year on June 30 for the period from January 1 to December 31 of the prior year, starting one calendar year after the effective date of Article 6.5. (A) Past due inspections for piping and pressure vessels: i. Overdue inspection for piping and pressure vessels shall be reported. This information will not include relief devices, instrumentation, instrument air receivers, boilers, furnaces, atmospheric tanks, or rotating equipment. ii. Pressure vessels include but are not limited to: heat exchangers, columns, spheres, bullets as defined by CA Safety Order and U-stamped (or treated as such). The scope of the inspections for this reporting include external visual, condition monitoring location (CML) and nondestructive examination (NDE), and internal visual. Pressure vessel is defined by Title 8, Division 1, Chapter 4, Subchapter 1 Unfired Pressure vessel safety orders. iii. Process Piping and piping components excluding utility piping, the scope of the inspections shall include external visual, CML/NDE and internal visual as appropriate. iv. Past due is defined as overdue by the requirements listed in California Code of Regulations, Title 8, section 6857, API 510 and API 570. Deferral/extension when used shall follow the requirements contained within the above code and recommended practices. v. Inspections shall be defined by circuits rather than points. A circuit shall be defined by one of the following: isometrics, by process stream and piping class, or piece of equipment, such as a pressure vessel. When reporting past due inspections to Cal OES and the UPA, the owner or operator shall include the total number of circuits at the stationary source and the total number of annual planned circuit inspections for that year to provide context regarding the number of circuits/equipment defined by the inspection program at the facility. (B) Past due PHA corrective actions and seismic corrective actions shall be reported. If a stationary source receives an extension approved by the UPA, the new approved due date shall apply. (C) Past due Incident Investigation corrective actions shall be reported for major incidents. All major incidents that occur after the effective date of this Article are subject to this requirement. (D) Major incidents: The number of major incidents that have occurred since the effective date of this Article. (E) The number of temporary piping and equipment repairs that are installed on hydrocarbon and high energy utility systems that are past their date of replacement with a permanent repair and the total number of temporary piping and equipment repairs installed on hydrocarbon and high energy utility systems. The owner or operator shall document, but not report, the date the temporary piping repair was installed, and the date for the permanent repair is to be complete. (F) Past due item is an item that is not completed by the end of the month during the month that is due. Each month an item that is past due shall be counted overdue. If the item is continued from the prior month then it is also counted as a repeat item. The repeat row is a subset of the overdue items. The table below shall be used for each of the indicators listed above. | 19 CCR 4.5 2762.16(h)(1) | 2022-07-01 | 2099-12-31 | 2022-07-01 | Existing | 280 | Program 4 Prevention Program | Management System | Reported Process Safety Performance Indicators to CalEPA and the UPA annually on June 30. | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to report process safety performance indicators listed in subsection (A) through (E) below to CalEPA and the UPA every year on June 30 for the period from January 1 to December 31 of the prior year, starting one calendar year after the effective date of Article 6.5. (A) Past due inspections for piping and pressure vessels: i. Overdue inspection for piping and pressure vessels shall be reported. This information will not include relief devices, instrumentation, instrument air receivers, boilers, furnaces, atmospheric tanks, or rotating equipment. ii. Pressure vessels include but are not limited to: heat exchangers, columns, spheres, bullets as defined by CA Safety Order and U-stamped (or treated as such). The scope of the inspections for this reporting include external visual, condition monitoring location (CML) and nondestructive examination (NDE), and internal visual. Pressure vessel is defined by Title 8, Division 1, Chapter 4, Subchapter 1 Unfired Pressure vessel safety orders. iii. Process Piping and piping components excluding utility piping, the scope of the inspections shall include external visual, CML/NDE and internal visual as appropriate. iv. Past due is defined as overdue by the requirements listed in California Code of Regulations, Title 8, section 6857, API 510 and API 570. Deferral/extension when used shall follow the requirements contained within the above code and recommended practices. v. Inspections shall be defined by circuits rather than points. A circuit shall be defined by one of the following: isometrics, by process stream and piping class, or piece of equipment, such as a pressure vessel. When reporting past due inspections to Cal OES and the UPA, the owner or operator shall include the total number of circuits at the stationary source and the total number of annual planned circuit inspections for that year to provide context regarding the number of circuits/equipment defined by the inspection program at the facility. (B) Past due PHA corrective actions and seismic corrective actions shall be reported. If a stationary source receives an extension approved by the UPA, the new approved due date shall apply. (C) Past due Incident Investigation corrective actions shall be reported for major incidents. All major incidents that occur after the effective date of this Article are subject to this requirement. (D) Major incidents: The number of major incidents that have occurred since the effective date of this Article. (E) The number of temporary piping and equipment repairs that are installed on hydrocarbon and high energy utility systems that are past their date of replacement with a permanent repair and the total number of temporary piping and equipment repairs installed on hydrocarbon and high energy utility systems. The owner or operator shall document, but not report, the date the temporary piping repair was installed, and the date for the permanent repair is to be complete. (F) Past due item is an item that is not completed by the end of the month during the month that is due. Each month an item that is past due shall be counted overdue. If the item is continued from the prior month then it is also counted as a repeat item. The repeat row is a subset of the overdue items. The table below shall be used for each of the indicators listed above. |  |  | OBSERVATION: Owner/operator failed to: report process safety performance indicators listed in subsection (A) through (E) below to CalEPA and the UPA every year on June 30 for the period from January 1 to December 31 of the prior year, starting one calendar year after the effective date of Article 6.5; use the required table for each of the indicators listed. CORRECTIVE ACTION: Report process safety performance indicators as required above and submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010260 |  |  | Program level 4: Accidental Release Prevention Program Management System -Individual Program 4 Process Safety Performance Indicators | Failure to develop and measure, no later than six months after the effective date of Article 6.5, a list of site-specific indicators, consisting of activities and other events in order to evaluate the performance of its process safety systems for the purpose of continuous improvement. Failure to prepare an annual written report by June 30 of each year containing a compilation of these site specific indicators for the previous calendar year. Failure to ensure the stationary source manager or designee certify annually that the report is current and accurate. | 19 CCR 4.5 2762.16(h)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 281 | Program 4 Prevention Program | Management System | Developed and measured site-specific indicators to evaluate performance of process safety systems | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to develop and measure, no later than six months after the effective date of Article 6.5, a list of site-specific indicators, consisting of activities and other events in order to evaluate the performance of its process safety systems for the purpose of continuous improvement. Failure to prepare an annual written report by June 30 of each year containing a compilation of these site specific indicators for the previous calendar year. Failure to ensure the stationary source manager or designee certify annually that the report is current and accurate. |  |  | OBSERVATION: Owner/operator failed to: develop and measure, no later than six months after the effective date of Article 6.5, a list of site-specific indicators, consisting of activities and other events in order to evaluate the performance of its process safety systems for the purpose of continuous improvement; prepare an annual written report by June 30 of each year containing a compilation of these site specific indicators for the previous calendar year; ensure the stationary source manager or designee certify annually that the report is current and accurate. CORRECTIVE ACTION: Develop and measure a list of site-specific indicators that meet above requirements; prepare an annual written report and ensure the refinery manager or designee annually certify report. Submit documentation to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Administration/Documentation | 5010261 |  |  | Program level 4: Access to Documents and Information | Failure to provide documents or information developed or collected pursuant to Article 6.5 to the UPA upon request. | 19 CCR 4.5 2762.17 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 282 | Program 4 Prevention Program | Access to Documents and Information | Provided documents or information developed pursuant Article 6.5 to the UPA upon request. | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide documents or information developed or collected pursuant to Article 6.5 to the UPA upon request. |  |  | OBSERVATION: Owner/operator failed to provide documents or information developed or collected pursuant to Article 6.5 to the UPA upon request. CORRECTIVE ACTION: Submit and provide documentation or information developed or collected pursuant to Article 6.5 to demonstrate compliance to the UPA. | [6 empty] | No | No | No | Yes
CalARP Program | Operations/Maintenance | 5030005 |  |  | General Duty Clause | Failure to: 1. Identify hazards that may result from releases using appropriate hazard assessment techniques. 2. Design and maintain a safe facility taking those steps as are necessary to prevent releases. 3. Minimize the consequences of accidental releases that do occur. | HSC 25531.2(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 283 | General Facility Requirements | General Duty Clause | Hazards assessed & ID'd, steps taken to maintain safety & prevent releases/reduce consequences | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to: 1. Identify hazards that may result from releases using appropriate hazard assessment techniques. 2. Design and maintain a safe facility taking those steps as are necessary to prevent releases. 3. Minimize the consequences of accidental releases that do occur. |  |  | OBSERVATION: Owner/Operator violated the General Duty Clause by failing to do one or more of the following: Identify hazards that may result from releases using appropriate hazard assessment techniques; Design and maintain a safe facility taking those steps as are necessary to prevent releases; or Minimize the consequences of accidental releases that do occur.[PROVIDE SPECIFICS] CORRECTIVE ACTION: Take actions necessary to ensure compliance with the General Duty Clause. [PROVIDE SPECIFICS] Submit documentation to UPA describing correction actions taken. | [6 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5010 |  |  | CalARP Program - Administration/Documentation - General | Administration/Documentation - General | 19 CCR 4.5 Multiple Sections | 2011-07-01 | 2099-12-31 | 2011-07-01 | Existing | 284 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Administration/Documentation | 5015 |  |  | CalARP Program - Administration/Documentation - General Local Ordinance | Administration/Documentation - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 285 | General Facility Requirements |  | Administration/Documentation - General Local Ordinance | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Training | 5020 |  |  | CalARP Program - Training - General | Training - General | 19 CCR 4.5 Multiple Sections | 2011-07-01 | 2099-12-31 | 2011-07-01 | Existing | 286 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Training | 5025 |  |  | CalARP Program - Training - General Local Ordinance | Training - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 287 | General Facility Requirements |  | Training - General Local Ordinance | 34 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Operations/Maintenance | 5030 |  |  | CalARP Program - Operations/Maintenance - General | Operations/Maintenance - General | 19 CCR 4.5 Multiple Sections | 2011-07-01 | 2099-12-31 | 2011-07-01 | Existing | 288 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Operations/Maintenance | 5035 |  |  | CalARP Program - Operations/Maintenance - General Local Ordinance | Operations/Maintenance - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 289 | General Facility Requirements |  | Operations/Maintenance - General Local Ordinance | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Release/Leaks/Spills | 5040 |  |  | CalARP Program - Release/Leaks/Spills -General | Release/Leaks/Spills - General | 19 CCR 4.5 Multiple Sections | 2011-07-01 | 2099-12-31 | 2011-07-01 | Existing | 290 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Release/Leaks/Spills | 5045 |  |  | CalARP Program - Release/Leaks/Spills - General Local Ordinance | Release/Leaks/Spills - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 291 | General Facility Requirements |  | Release/Leaks/Spills - General Local Ordinance | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 5050 |  |  | CalARP Program - Abandonment/Illegal Disposal/Unauthorized Treatment -General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 19 CCR 4.5 Multiple Sections | 2011-07-01 | 2099-12-31 | 2011-07-01 | Existing | 292 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes | Yes | Yes | Yes
CalARP Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 5055 |  |  | CalARP Program - Abandonment/Illegal Disposal/Unauthorized Treatment General - Local Ordinance | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 293 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes

## UST
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading (Optional) | Inspection Checklist Sub-Heading (Optional) | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop-Down | Default Degree of Violation | Required Item? | Points (Optional) | Comply By Days (Optional) | Violation Descriptive Text | TCR DESIGNATION | Violation Corrective Text (Optional) | Inspector Comment 1 (Optional) | Inspector Comment 2 (Optional) | Inspector Comment 3 (Optional) | Inspector Comment 4 (Optional) | Inspector Comment 5 (Optional) | UST FULL | UST DW | UST SW
UST Program | Operations/Maintenance | 2030021 |  |  | Failure to Obtain Operating Permit | Failure to obtain a valid permit to operate from the UPA including but not limited to unpaid permit fees. | 23 CCR 16 2711(d); HSC 6.7 25284 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 1 | File Review | Facility/Tank Information | Facility has a valid Permit to Operate from the CUPA | 52 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to obtain a valid permit to operate from the UPA including but not limited to unpaid permit fees. |  |  | OBSERVATION: Owner/Operator did not obtain and/or maintain a valid Operating Permit from the CUPA, and/or failed to pay permit fees. CORRECTIVE ACTION: Obtain and maintain a valid Operating Permit from the CUPA and/or pay all past due permit fees. | OBSERVATION: A permit to operate the UST system has not been issued. No person may own or operate an UST unless a permit for its operation has been issued by the local agency to the owner or operator of the UST system. CORRECTIVE ACTION: Immediately obtain a permit to operate a UST system from the CUPA. An “Operating without a Permit” penalty applies. |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010010 |  |  | UST Facility and/or Tank Information | Failure to submit a complete and accurate application for a permit to operate a UST, or for renewal of the permit. | 23 CCR 16 2711; HSC 6.7 25284, 25286 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 2 | File Review | Facility/Tank Information | Complete and accurate UST Operating Permit Application has been submitted. | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a complete and accurate application for a permit to operate a UST, or for renewal of the permit. |  |  | OBSERVATION: Owner/Operator did not submit and/or maintain a complete and/or accurate UST Operating Permit Application. CORRECTIVE ACTION: Submit and/or maintain a complete and/or accurate UST Operating Permit Application, including for permit renewal. | OBSERVATION: UST facility operating permit information and UST tank information [note which ones] are not current in CERS. Any change of information must be updated in CERS within 30 days of the change. CORRECTIVE ACTION: Immediately update the required information in CERS and submit for review by the CUPA. |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010013 |  |  | Monitoring Plan | Failure to submit a complete and accurate UST Monitoring Plan. | 23 CCR 16 2632(d)(1), 2634(d), 2641(h) | 2016-06-01 | 2099-12-31 | 2016-05-13 14:22 | Existing | 3 | File Review | Facility/Tank Information | Facility has submitted a complete and accurate UST Monitoring Plan. | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a complete and accurate UST Monitoring Plan. |  |  | OBSERVATION: Facility failed to submit a complete and accurate UST Monitoring Plan. CORRECTIVE ACTION: Submit a complete and accurate UST Monitoring Plan. |  |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010014 |  |  | Response Plan | Failure to submit a complete and accurate UST Response Plan. | 23 CCR 16 2632(d)(2), 2634(e), 2641(h) | 2016-06-01 | 2099-12-31 | 2016-05-13 14:25 | Existing | 4 | File Review | Facility/Tank Information | Facility has submitted a complete and accurate UST Response Plan. | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a complete and accurate UST Response Plan. |  |  | OBSERVATION: Facility failed to submit a complete and accurate UST Response Plan. CORRECTIVE ACTION: Submit a complete and accurate UST Response Plan. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030041 |  |  | Plot Plan | Failure to submit or maintain a current facility plot plan. | 23 CCR 16 2632(d)(1)(C), 2641(h) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 5 | File Review | Facility/Tank Information | A current facility plot plan is maintained and has been submitted | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit or maintain a current facility plot plan. |  |  | OBSERVATION: Owner/Operator did not maintain and/or submit a current facility plot plan. CORRECTIVE ACTION: Maintain and/or submit a current facility plot plan. |  |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010006 |  |  | Falsification (USEPA Priority) | Owner/operator made false statements, representation, or certification on an application, record, or other document. | HSC 6.7 25299(a)(8) and/or 25299(b)(7) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 6 | File Review | Facility/Tank Information | Owner/Operator has not made false statements, certifications, or representations on documents | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Owner/operator made false statements, representation, or certification on an application, record, or other document. |  |  | OBSERVATION: Owner/operator made false statements, representations, or certifications on an application, record, or other document. CORRECTIVE ACTION: Owner/operator shall not make false statements, representations, or certifications on an application, record, or other document. Submit accurate document. |  |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010003 | Designated Operator Training (USEPATCR 10) |  | Designated Operator (DO) - Identification Notification (USEPATCR 10) | Failure to submit the “Designated Underground Storage Tank Operator Identification Form” within 30 days of installing a UST system or within 30 days of a change in DO. | 23 CCR 16 2715(a)(1)(B), 2715(a)(3) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 7 | File Review | Facility/Tank Information | Owner/Operator submitted DO form and/or informed the CUPA of any change(s) within 30 days (TCR 10) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit the “Designated Underground Storage Tank Operator Identification Form” within 30 days of installing a UST system or within 30 days of a change in DO. | 10 |  | OBSERVATION: Owner/Operator did not submit the “Designated Underground Storage Tank Operator Identification Form” to the UPA within 30 days of obtaining or changing the DO. CORRECTIVE ACTION: Submit “Designated Underground Storage Tank Operator Identification Form” to the UPA within 30 days of a change. | OBSERVATION:A new designated operator was hired on [date] and notification was not provided to the CUPA within 30 days of the change. Any changes shall be reported to the CUPA with 30 days. CORRECTIVE ACTION: Upload the required information into CERS and submit to the CUPA or submit notification to the CUPA identifying all the designated operators for this facility by [date, 30 days from now]. |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010016 | Designated Operator Training (USEPATCR 10) |  | Owner/Operator Statement of Understanding and Compliance (USEPATCR 10) | Failure to submit the “Underground Storage Tank Statement of Understanding and Compliance Form”. | 23 CCR 16 2715(a)(1)(A), 2715(a)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 8 | File Review | Facility/Tank Information | “Underground Storage Tank Statement of Understanding and Compliance Form” submitted (TCR 10) | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit the “Underground Storage Tank Statement of Understanding and Compliance Form.” | 10 |  | OBSERVATION: Owner/operator failed to submit the “Underground Storage Tank Statement of Understanding and Compliance Form”. CORRECTIVE ACTION: Submit the “Underground Storage Tank Statement of Understanding and Compliance Form”. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030002 | Release Detection (USEPATCR 9d) |  | Leak Detection Equipment Maintenance (USEPATCR 9d) (USEPA Priority) | Failure to have a properly qualified service technician test leak detection equipment as required every 12 months (vacuum, pressure, hydrostatic (VPH) system, sensors, line-leak detectors (LLD), automatic tank gauge (ATG), etc.). | 23 CCR 16 2638(a) & (b), 2641(j), 2715(f) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 9 | File Review | Testing | Leak detection equipment tested by qualified service technician every 12 months (TCR 9d) | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to have a properly qualified service technician test leak detection equipment as required every 12 months (vacuum, pressure, hydrostatic (VPH) system, sensors, line-leak detectors (LLD), automatic tank gauge (ATG), etc.). | 9d |  | OBSERVATION: Owner/Operator did not have a properly qualified service technician test leak detection equipment every 12 months (VPH, sensor, LLD, ATG, etc.). CORRECTIVE ACTION: Have a properly qualified service technician test leak detection equipment every 12 months. | OBSERVATION: Annual monitoring system certification and/or leak detector testing, were last performed on [date] and was completed on [date], [# months late] months past due. These tests are required once every 12 months. CORRECTIVE ACTION: Immediately schedule these tests and provide 48 hours notification to the CUPA. Please be aware that a follow up inspection will be charged at our current hourly rate. |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030074 |  |  | 12 Month Monitoring System Certification Submittal | Failure to submit the “Monitoring System Certification Form” to the UPA within 30 days of completion of the test. | 23 CCR 16 2638(c), 2638(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 10 | File Review | Testing | Annual Monitoring System Certification Form to the CUPA within 30 days of completion of the test | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit the “Monitoring System Certification Form” to the UPA within 30 days of completion of the test. |  |  | OBSERVATION: Owner/Operator did not submit the Monitoring System Certification Form to the CUPA within 30 days of completion of the test. CORRECTIVE ACTION: Submit copy of the Monitoring System Certification to the CUPA. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030048 | Release Detection (USEPATCR 9d) |  | Secondary Containment Testing (USEPATCR 9d) (USEPA Priority) | Failure to conduct secondary containment testing, or meet one or more of the following requirements: 1) Within six months of installation and every 36 months thereafter. 2) Within 30 days of a repair or discontinuing vacuum, pressure or hydrostatic monitoring. 3) Using a procedure that demonstrates the system works as well as it did upon installation. 4) Using applicable manufacturer guidelines, industry codes, engineering standards, or professional engineer approval. 5) Performed by a certified service technician. 6) Maintaining records of secondary containment testing for 36 months. | 23 CCR 16 2637(a), 2637(b), 2637(c), 2637(d), 2712(b)(1)(F) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 11 | File Review | Testing | Sec containment testing conducted per requirements & records kept for 36 mths (TCR 9d) | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to conduct secondary containment testing, or meet one or more of the following requirements: 1) Within six months of installation and every 36 months thereafter. 2) Within 30 days of a repair or discontinuing vacuum, pressure or hydrostatic monitoring. 3) Using a procedure that demonstrates the system works as well as it did upon installation. 4) Using applicable manufacturer guidelines, industry codes, engineering standards, or professional engineer approval. 5) Performed by a certified service technician. 6) Maintaining records of secondary containment testing for 36 months. | 9d |  | OBSERVATION: Owner/Operator did not do one or more of the following: conduct secondary containment testing within six months of installation and every 36 months thereafter; perform secondary containment testing within 30 days of a repair or discontinuing VPH monitoring; use a procedure that demonstrates the system works as well as at installation; use applicable manufacturer guidelines, industry codes, engineering standards, or professional engineer approval; have testing performed by a certified service technician; or maintain records of secondary containment testing for 36 months. CORRECTIVE ACTION: Conduct secondary containment testing in accordance with all applicable requirements and maintain records for 36 months. Submit verification. | OBSERVATION: Secondary containment testing was last performed on [date] and was due by [month/year]. Testing has not been completed and is [# of months] months past due. Secondary containment testing is required once every 36 months. CORRECTIVE ACTION: Immediately schedule this test and provide 48 hours notification to the CUPA. | OBSERVATION: Secondary containment testing was last performed on [date] and was completed on [date], [# of months] months past due. Secondary containment testing is required once every 36 months. CORRECTIVE ACTION: Take all necessary precautions to ensure testing is performed in a timely manner. | OBSERVATION: [note which secondary containment component] was installed on [date] and six month testing was due by [month/year]. Testing has not been completed and is [# of months] months past due. Secondary containment testing is required six months after installation and at least every 36 months after. CORRECTIVE ACTION: Immediately schedule this test and provide 48 hours notification to the CUPA. |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010009 |  |  | Secondary Containment Testing - Reporting | Failure to submit a copy of the secondary containment test results on the “Secondary Containment Testing Report Form” to the UPA within 30 days after the test. | 23 CCR 16 2637(e), (f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 12 | File Review | Testing | Secondary containment test results submitted to the CUPA within 30 days after the test. | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a copy of the secondary containment test results on the “Secondary Containment Testing Report Form” to the UPA within 30 days after the test. |  |  | OBSERVATION: Owner/Operator did not submit secondary containment test results to the CUPA within 30 days after the test. CORRECTIVE ACTION: Submit secondary containment test results to the CUPA within 30 days after the test. | OBSERVATION: Secondary containment testing was scheduled to be performed on [date] and a test report has not been submitted to the CUPA. A copy of the test report must be submitted within 30 days of the test. CORRECTIVE ACTION: Immediately submit a copy of the test report or schedule this test and provide 48 hours notification to the CUPA. |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010017 |  |  | Spill Container Testing - Reporting | Failure to submit a copy of the spill containment test results on the “Spill Container Testing Report Form” to the UPA within 30 days after the test. | 23 CCR 16 2637.1(d), 2637.1(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 13 | File Review | Testing | Spill bucket testing results submitted to the UPA within 30 days of testing | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a copy of the spill containment test results on the “Spill Container Testing Report Form” to the UPA within 30 days after the test. |  |  | OBSERVATION: Owner/Operator failed to submit the spill bucket testing results to UPA within 30 days of testing. CORRECTIVE ACTION: Submit spill bucket testing results. |  |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010018 |  |  | Overfill Prevention Inspection – Records | Failure to submit a copy of the overfill prevention equipment inspection results on the “Overfill Prevention Equipment Inspection Report Form” to the UPA within 30 days after the inspection. | 23 CCR 16 2637.2(d), 2637.2(e), 2665(a), 2665(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 14 | File Review | Testing | Overfill prevention equipment inspection report form submitted to the UPA within 30 days | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a copy of the overfill prevention equipment inspection results on the “Overfill Prevention Equipment Inspection Report Form” to the UPA within 30 days after the inspection. |  |  | OBSERVATION: Owner/operator failed to submit a copy of the overfill prevention equipment inspection results on the “Overfill Prevention Equipment Inspection Report Form” to the UPA within 30 days after the inspection. CORRECTIVE ACTION: Submit a copy of the overfill prevention equipment inspection results on the “Overfill Prevention Equipment Inspection Report Form” to the UPA within 30 days. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030042 | Release Detection (USEPATCR 9d) |  | Pressurized Double-Walled Pipe - Line Integrity Test (USEPATCR 9d) (USEPA Priority) | Failure to perform one of the following line integrity test(s): 1) A 12 month test for pressurized double-walled piping that does not utilize fail safe and positive shut down, or 2) Within 30 days of the date of the completion of a repair to the primary piping. | 23 CCR 16 2636(f)(3), 2643(c)(3); HSC 6.7 25290.2(g), 25291(f), 25292(e); | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 15 | File Review | Testing | Line integrity test completed on DW press piping every 12 mths if no fail safe / + shutdown (TCR 9d) | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform one of the following line integrity test(s): 1) A 12 month test for pressurized double-walled piping that does not utilize fail safe and positive shut down, or 2) Within 30 days of the date of the completion of a repair to the primary piping. | 9d |  | OBSERVATION: Owner/Operator did not perform and pass annual line integrity test for double-walled pressurized piping that does not utilize fail safe or positive shut down, or did not complete test within 30 days of the completion of a repair to the primary piping. CORRECTIVE ACTION: Perform and pass annual line integrity test for pressurized piping that does not utilize fail safe or shut down, and within 30 days of completing any repairs to the primary piping. Submit verification. | OBSERVATION: Annual line tightness testing was last performed on [date] and was due by [month/year]. Testing has not been completed and is [# months late] months past due. This test is required annually. CORRECTIVE ACTION: Immediately schedule this test and provide 48 hours notification to the CUPA. Please be aware that a follow up inspection will be charged at our current hourly rate | OBSERVATION: Annual line tightness testing was last performed on [date] and was completed on [date] , [# months late] months past due. This test is required annually. CORRECTIVE ACTION: Take all necessary precautions to ensure testing is performed in a timely manner. |  |  | Yes | Yes | No
UST Program | Operations/Maintenance | 2030050 | Release Detection (USEPATCR 9d) |  | Single-Walled Conventional Suction Testing (USEPATCR 9d) (USEPA Priority) | For single-walled conventional suction systems, failure to conduct 0.1 gallon per hour piping integrity test at one of the following times: 1. Every 36 months. 2. Within 30 days of the date of the completion of a repair to the piping. | 23 CCR 16 2643(d), 2661(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 16 | File Review | Testing | 0.1 gph piping test conducted on SW suction systems every 36 mths and after piping repair (TCR 9d) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | For single-walled conventional suction systems, failure to conduct 0.1 gallon per hour piping integrity test at one of the following times: 1. Every 36 months. 2. Within 30 days of the date of the completion of a repair to the piping. | 9d |  | OBSERVATION: Owner/Operator did not conduct 0.1 gph integrity test every 36 months, or within 30 days of a piping repair, for single-walled conventional suction systems. CORRECTIVE ACTION: Conduct a 0.1 gallon per hour piping integrity test on single-walled conventional suction systems and retest at least every 36 months. Submit test results to the CUPA. | OBSERVATION: Tightness testing on the [grade] suction piping was last performed on [date] and was due by [month/year]. Testing has not been completed and is [# months late] months past due. Piping that conveys hazardous substances under less than atmospheric pressure shall be monitored at least once every three years at a pressure designated by the test equipment manufacturer and shall be capable of detecting a minimum release equivalent to 0.1gphat 40 psi. CORRECTIVE ACTION: Immediately schedule this test and provide 48 hours notification to the CUPA. Provide copies of the test results by [date, 30 days from now]. |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030051 | Release Detection (USEPATCR 9d) |  | Single-Walled Gravity Testing (USEPATCR 9d) (USEPA Priority) | For single-walled gravity systems, failure to conduct a 0.1 gallon-per-hour line piping integrity test at one of the following times: 1) Every 24 months. 2) Within 30 days of the date of the completion of a repair to the piping. | 23 CCR 16 2643(e), 2661(f) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 17 | File Review | Testing | 0.1 gph piping test conducted on SW gravity systems every 24 mths and after piping repair (TCR 9d) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | For single-walled gravity systems, failure to conduct a 0.1 gallon-per-hour line piping integrity test at one of the following times: 1) Every 24 months. 2) Within 30 days of the date of the completion of a repair to the piping. | 9d |  | OBSERVATION: Owner/Operator did not conduct 0.1 gallon per hour piping integrity test every 24 months, or within 30 days of a piping repair, for single-walled gravity systems. CORRECTIVE ACTION: Conduct 0.1 gallon per hour piping integrity test and retest at least every 24 months for single-walled gravity systems. Submit test results. | OBSERVATION: Tightness testing on the [grade] gravity flow piping was last performed on [date] and was due by [month/year]. Testing has not been completed and is [# months late] months past due. Piping that conveys hazardous substances by the force of gravity (excluding vertical drops) shall be monitored at least once every two years at a pressure designated by the test equipment manufacturer and shall be capable of detecting a minimum release equivalent to 0.1gphat 40 psi. CORRECTIVE ACTION: Immediately schedule this test and provide 48 hours notification to the CUPA. Provide copies of the test results to the CUPA by [date, 30 days from now]. |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030029 | Corrosion Protection (USEPATCR 9c) |  | Lined Tank Requirements (USEPATCR 9c) (USEPA Priority) | Failure to complete one or more of the requirements of tank lining, including but not limited to: 1) Submit proper written tank lining certification to the UPA within 30 days of completion of the inspection. 2) Perform tank integrity test and/or vacuum test following lining, employ proper coatings expert and/or special inspector. 3) Failure to inspect a steel tank which has been lined or repaired using the interior lining method within 120 months of lining and every 60 months thereafter. 4) Maintain records for the life of the tank. | 23 CCR 16 2663, 2712(b)(6) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 18 | File Review | Testing | Tank lining inspected w/in 10 years of lining, every 5 years after, cert submitted to CUPA (TCR 9c) | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to complete one or more of the requirements of tank lining, including but not limited to: 1) Submit proper written tank lining certification to the UPA within 30 days of completion of the inspection. 2) Perform tank integrity test and/or vacuum test following lining, employ proper coatings expert and/or special inspector. 3) Failure to inspect a steel tank which has been lined or repaired using the interior lining method within 120 months of lining and every 60 months thereafter. 4) Maintain records for the life of the tank. | 9c |  | OBSERVATION: Owner/Operator failed to comply with one or more of the following requirements for steel tank lining: submit proper written tank lining certification to the UPA within 30 days of completion of the inspection, perform tank integrity test and/or vacuum test following lining, employ proper coatings expert and/or special inspector, inspect a steel tank which has been lined or repaired using the interior lining method within 120 months of lining and every 60 months thereafter, or maintain records for the life of the tank. CORRECTIVE ACTION: Ensure that tank lining is inspected as required, records are maintained for the life of the tank, and that written tank lining certification is submitted to the UPA within 30 days of completion. |  |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010005 |  |  | Enhanced Leak Detection Testing - Results | Failure to submit enhanced leak detection testing results to the State Water Board and the UPA within 60 days of completion of the test. | 23 CCR 16 2644.1(a)(5) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 19 | File Review | Testing | ELD testing results sent to the board and the CUPA within 60 days of completion of the test | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit enhanced leak detection testing results to the board and the CUPA within 60 days of completion of the test. |  |  | OBSERVATION: Owner/Operator did not submit ELD testing results to the Board and/or CUPA. CORRECTIVE ACTION: Submit ELD testing results to the board and the CUPA within 60 days of completion of the test. |  |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030056 |  |  | Statistical Inventory Reconciliation (SIR) Reporting (USEPA Priority) | Failure to submit the statistical inventory reconciliation (SIR) Report every 12 months to the UPA. | 23 CCR 16 2646.1(j) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 20 | File Review | Testing | SIR Report submitted to the CUPA every 12 months | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit the statistical inventory reconciliation (SIR) Report every 12 months to the UPA. |  |  | OBSERVATION: Owner/Operator did not submit the SIR Report to the UPA every 12 months. CORRECTIVE ACTION: Submit SIR Report to the CUPA every 12 months. Submit verification. |  |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030064 |  |  | Testing Notification | Failure to notify the UPA 48 hours prior to testing. | 23 CCR 16 2637(g), 2637.1(f), 2637.2(f), 2638(e), 2643(g), 2644.1(a)(4) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 21 | File Review | Testing | CUPA was notified within 48 hours prior to testing | 51 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to notify the CUPA 48 hours prior to testing. |  |  | OBSERVATION: Owner/Operator did not notify the CUPA 48 hours prior to testing. CORRECTIVE ACTION: Ensure that the CUPA is notified 48 hours prior to testing. | OBSERVATION: Annual monitoring system certification, leak detector testing, and spill container testing were performed on [date] without providing notification to the CUPA at least 48 hours in advance. Notification shall be provided to the CUPA at least 48 hours in advance of testing. The CUPA will not accept these results and testing must be rescheduled with a 48-hour notification. Testing was last performed on [date] and was [or is] due by [month/year]. CORRECTIVE ACTION: Immediately schedule these tests and provide 48 hours notification to the CUPA. | OBSERVATION: Secondary containment testing was performed on [date] without providing notification to the CUPA at least 48 hours in advance. Notification shall be provided to the CUPA at least 48 hours in advance of testing. The CUPA will not accept these results and testing must be rescheduled with a 48-hour notification. Testing was last performed on [date] and was [or is] due by [month/year]. CORRECTIVE ACTION: Immediately schedule this test and provide 48 hours notification to the CUPA. |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030068 |  |  | Well Proximity Enhanced Leak Detection (ELD) Testing (Initial or One Time) | Failure to conduct the required initial or periodic enhanced leak detection (ELD) test for UST systems located within 1,000 feet of a public drinking water well. | 23 CCR 16 2640(e), 2644.1; HSC 6.7 25292.4(a), 25292.5(a) | 2016-06-01 | 2099-12-31 | 2016-06-13 08:25 | Existing | 22 | File Review | Testing | Initial or triennial ELD testing conducted on UST system 1000’ of public well | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to conduct initial or triennially ELD testing for UST systems located within 1,000 feet of a public drinking water well. |  |  | OBSERVATION: Owner/Operator did not conduct initial or triennial ELD testing for UST systems located within 1,000 feet of a public drinking water well. CORRECTIVE ACTION: Conduct ELD testing on UST systems located within 1,000 feet of a public drinking water well. Submit test results within 60 days. | OBSERVATION: The UST system at this facility has been identified by the State Water Resources Control Board to be located within 1000 feet of a public drinking water well and must test the UST system once using an enhanced leak detection test. This testing has not been completed. CORRECTIVE ACTION: Immediately schedule this test and provide 48 hours notification to the CUPA. Provide copies of the test results within [date, 30 days from now]. |  |  |  | Yes | Yes | Yes
UST Program | Design/Construction | 2060001 |  |  | As-Built Plans | Failure to submit as-built plans for the location and orientation of the tanks and appurtenant piping systems for new installations and/or with the permit application. | 23 CCR 16 2635(e)(8) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 23 | File Review | Install/Repair | As-built plans for new installations and/or with the permit application have been submitted | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit as-built plans for the location and orientation of the tanks and appurtenant piping systems for new installations and/or with the permit application. |  |  | OBSERVATION: Owner/Operator did not submit as-built plans for the location and orientation of the tanks and appurtenant piping systems for new installations and/or with the permit application. CORRECTIVE ACTION: Submit as-built plans for the location and orientation of the tanks and appurtenant piping systems for new installations and/or with the permit application. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030003 |  |  | Audible and Visual Alarm (USEPA Priority) | Failure of the leak detection equipment to have an audible and visual alarm as required. | 23 CCR 16 2632(c)(2)(B), 2634(d)(1)(A), 2636(f)(1) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 24 | UST System Observations | General Monitoring | Leak detection system maintains continuous monitoring that activates an audible and visual alarm | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the leak detection equipment to have an audible and visual alarm as required. |  |  | OBSERVATION: Owner/Operator did not maintain leak detection equipment with an audible and visual alarm. CORRECTIVE ACTION: Maintain leak detection equipment with an audible and visual alarm. | OBSERVATION: The [grade/location] sensor failed to activate an audible and visual alarm when tested to ensure continuous monitoring of the tank system. All monitoring equipment shall be maintained to activate an audible and visual alarm or stop the flow of product at the dispenser when it detects a leak. The [grade/location] sensor failed to activate an audible and visual alarm when tested to ensure continuous monitoring of the tank system. All monitoring equipment shall be maintained to activate an audible and visual alarm or stop the flow of product at the dispenser when it detects a leak. The sensor was replaced and retested during the inspection. The [type/brand of stand-alone sensor ] in the [UDC #] sump failed to stop the flow of product at the dispenser when tested. All monitoring equipment shall be maintained to activate an audible and visual alarm or stop the flow of product at the dispenser when it detects a leak. The sensor was replaced and retested during the inspection. CORRECTIVE ACTION: Correct immediately by having a properly licensed, trained, and certified contractor replace the failed component with a functional component (LG 113-x listed, if applicable) and obtain a permit within 1 business day from the CUPA. If the failed component can’t be replaced immediately, there is a possibility that the [grade] UST system may be red tagged to prevent fuel inputs. |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030016 | Release Detection (USEPATCR 9d) |  | Double-Walled Tank Monitoring - After January 1, 1984 and Before July 1, 2004 (USEPATCR 9d) (USEPA Priority) | Failure to continuously monitor the interstitial space of a double-walled tank with an audible and visual alarm system. | 23 CCR 16 2631(g), 2632(c)(2)(A) & (B) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 25 | UST System Observations | General Monitoring | Annular space of USTs are continuously monitored with an audible and visual alarm system (TCR 9d) | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to continuously monitor the interstitial space of a double-walled tank with an audible and visual alarm system. | 9d |  | OBSERVATION: Owner/Operator did not continuously monitor the interstitial space of the USTs such that the leak detection activates an audible/visual alarm when a leak is detected. CORRECTIVE ACTION: Continuously monitor the interstitial space of the USTs such that the leak detection equipment activates an audible/visual alarm when a leak is detected. Submit verification. | OBSERVATION: The [grade] annular sensor failed to activate an audible and visual alarm when tested and, therefore, the tank is not monitored. The interstitial space shall be monitored with a monitoring system connected to an audible and visual alarm system. CORRECTIVE ACTION: Immediately contact a properly licensed, trained, and certified contractor to replace the failed component with a functional component (LG 113-x listed, if applicable) under permit and inspection of the CUPA within [# of business day's]. | OBSERVATION: The [grade] annular sensor failed to activate an audible and visual alarm when tested and, therefore, the tank is not monitored. The interstitial space shall be monitored with a monitoring system connected to an audible and visual alarm system. The sensor was replaced and retested during the inspection. CORRECTIVE ACTION: Immediately contact a properly licensed, trained, and certified contractor to replace the failed component with a functional component (LG 113-x listed, if applicable) under permit and inspection of the CUPA within one business day. |  |  | Yes | Yes | No
UST Program | Operations/Maintenance | 2030017 | Release Detection (USEPATCR 9d) |  | Double-Walled Pressurized Pipe - Monitoring - In Lieu of 12 Month Line Integrity Test (USEPATCR 9d) (USEPA Priority) | Failure to meet one or more of the following monitoring requirements in lieu of the requirement to be tightness tested every 12 months: 1) The monitoring system maintains all product piping outside the dispenser to be fail-safe and shut down the pump when a leak is detected. 2) The monitoring system shuts down the pump or stops flow when a leak is detected in the under dispenser containment (UDC). | 23 CCR 16 2636(f)(4) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 26 | UST System Observations | General Monitoring | Piping out of UDC is fail-safe/shut down, UDC leak shuts off pump/flow, or tightness test (TCR 9d) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet one or more of the following monitoring requirements in lieu of the requirement to be tightness tested every 12 months: 1) The monitoring system maintains all product piping outside the dispenser to be fail-safe and shut down the pump when a leak is detected. 2) The monitoring system shuts down the pump or stops flow when a leak is detected in the under dispenser containment (UDC). | 9d |  | OBSERVATION: Owner/Operator, in lieu of annual tightness testing, failed to maintain all product piping, outside the dispenser, to be fail-safe and capable of shutting down the pump when a leak is detected and/or failed to maintain a monitoring system capable of shutting down the pump or stops the flow (flow restriction) when a leak is detected in the under dispenser containment. CORRECTIVE ACTION: Maintain all product piping outside the dispenser to be fail-safe and shut down the pump when a leak is detected and a monitoring system that shuts down the pump or stops the flow (flow restriction) when a leak is detected in the under dispenser containment. Submit verification. | OBSERVATION: The [UST component] did not [note what requirement was lacking] and does not meet the requirements for annual line tightness testing exemption. The service technician reprogrammed the monitoring panel to [whatever was fixed], which satisfies the annual line tightness testing requirement. CORRECTIVE ACTION: Immediately schedule this test and provide 48 hours notification to the CUPA. |  |  |  | Yes | Yes | No
UST Program | Operations/Maintenance | 2030018 | Release Detection (USEPATCR 9d) |  | Double-Walled Pressurized Pipe -Interstitial Monitoring (USEPATCR 9d) (USEPA Priority) | Failure of the double-walled pressurized piping to be continuously monitored with a system that activates an audible and visual alarm or stops flow at the dispenser when a leak is detected. | 23 CCR 16 2636(f)(1), 2666(b)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 27 | UST System Observations | General Monitoring | DW press piping is monitored with an audible/visual alarm or stops flow at UDC (TCR 9d) | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the double-walled pressurized piping to be continuously monitored with a system that activates an audible and visual alarm or stops flow at dispenser when a leak is detected. | 9d |  | OBSERVATION: Owner/Operator did not continuously monitor double-walled piping with a system that activates an audible and visual alarm or stops flow at dispenser when a leak is detected. CORRECTIVE ACTION: Continuously monitor double-walled piping with a system that activates an audible and visual alarm or stops flow at dispenser when a leak is detected. Submit verification. | OBSERVATION: The [grade/location] sensor failed to activate an audible and visual alarm when tested to ensure continuous monitoring of the tank system. All monitoring equipment shall be maintained to activate an audible and visual alarm or stop the flow of product at the dispenser when it detects a leak. CORRECTIVE ACTION: Correct immediately by having a properly licensed, trained, and certified contractor replace the failed component with a functional component (LG 113-x listed, if applicable) and obtain a permit within 1 business day from the CUPA. If the failed component can’t be replaced immediately, there is a possibility that the [grade] UST system may be red tagged to prevent fuel inputs. | OBSERVATION: The [grade/location] sensor failed to activate an audible and visual alarm when tested to ensure continuous monitoring of the tank system. All monitoring equipment shall be maintained to activate an audible and visual alarm or stop the flow of product at the dispenser when it detects a leak. The sensor was replaced and retested during the inspection. CORRECTIVE ACTION: Correct immediately by having a properly licensed, trained, and certified contractor replace the failed component with a functional component (LG 113-x listed, if applicable) and obtain a permit within 1 business day from the CUPA. If the failed component can’t be replaced immediately, there is a possibility that the [grade] UST system may be red tagged to prevent fuel inputs. |  |  | Yes | Yes | No
UST Program | Operations/Maintenance | 2030043 | Release Detection (USEPATCR 9d) |  | Monitoring Equipment (USEPATCR 9d) (USEPA Priority) | Failure of the leak detection equipment to be installed, calibrated, operated, and/or maintained in accordance with manufacturer's instructions. | 23 CCR 16 2638(a), 2641(j) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 28 | UST System Observations | General Monitoring | Leak detection equipment properly installed, calibrated, operated, and maintained (TCR 9d) | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the leak detection equipment to be installed, calibrated, operated, and/or maintained in accordance with manufacturer's instructions. | 9d |  | OBSERVATION: Owner/Operator did not properly install, calibrate, operate and/or maintain leak detection equipment. CORRECTIVE ACTION: Properly install, calibrate, operate and/or maintain leak detection equipment. |  |  |  |  | Yes | Yes | Yes
UST Program | Design/Construction | 2060005 |  |  | Double-Walled Construction After January 1, 1984 | Failure of the UST system to be designed and constructed with a monitoring system capable of detecting the entry of the hazardous substance into the secondary containment. | 23 CCR 16 2636(a)(1); HSC 6.7 25291(b) | 2022-07-01 | 2099-12-31 | 2022-07-01 | Revised | 29 | UST System Observations | General Monitoring | UST system constructed with a mon system capable of detecting entry into secondary containment | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the UST system to be designed and constructed with a monitoring system capable of detecting the entry of the hazardous substance into the secondary containment. |  |  | OBSERVATION: Owner/Operator failed to design or construct a UST system with a monitoring system capable of detecting the entry of the hazardous substance into the secondary containment. CORRECTIVE ACTION: UST system must be modified or repaired so that the monitoring system is capable of detecting the entry of the hazardous substance into the secondary containment. Submit verification. | OBSERVATION: The [grade] annular sensor failed to activate an audible and visual alarm when tested and, therefore, the tank is not monitored. The interstitial space shall be monitored with a monitoring system connected to an audible and visual alarm system. CORRECTIVE ACTION: Immediately contact a properly licensed, trained, and certified contractor to replace the failed component with a functional component (LG 113-x listed, if applicable) under permit and inspection of the CUPA within one business day. | OBSERVATION: The [grade/location] sensor failed to activate an audible and visual alarm when tested to ensure continuous monitoring of the tank system. All monitoring equipment shall be maintained to activate an audible and visual alarm or stop the flow of product at the dispenser when it detects a leak. CORRECTIVE ACTION: Correct immediately by having a properly licensed, trained, and certified contractor replace the failed component with a functional component (LG 113-x listed, if applicable) and obtain a permit within 1 business day from the CUPA. If the failed component can’t be replaced immediately, there is a possibility that the [grade] UST system may be red tagged to prevent fuel inputs. |  |  | Yes | Yes | No
UST Program | Design/Construction | 2060015 | Release Detection (USEPATCR 9d) |  | Improper Monitoring (USEPATCR 9d) (USEPA Priority) | Failure of leak detection equipment to be installed, maintained and located such that the equipment is capable of detecting a leak at the earliest possible opportunity. | 23 CCR 16 2630(d), 2641(a) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 30 | UST System Observations | General Monitoring | Leak detection equipment located so leak is detected at the earliest possible opportunity (TCR 9d) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure of leak detection equipment to be installed, maintained and located such that the equipment is capable of detecting a leak at the earliest possible opportunity. | 9d |  | OBSERVATION: Owner/Operator failed to install, maintain, or position leak detection equipment so that it is capable of detecting a leak at the earliest possible opportunity. CORRECTIVE ACTION: Install, maintain and position leak detection equipment so that it is capable of detecting a leak at the earliest possible opportunity. | OBSERVATION: The [grade/location] sump sensor was raised approximately [# of inches] inches off the lowest point of the sump [or located on top of the saddle of the tank sump or wrong side, etc.] and not located to detect a leak at the earliest opportunity. Monitoring equipment shall be maintained to be able to detect a leak at the earliest possible opportunity. CORRECTIVE ACTION: Immediately relocate this sensor to the lowest point of the [grade/location] sump. | OBSERVATION: The [grade] annular sensor was found not located at the bottom of the tank to detect a leak at the earliest opportunity. [Explain here] Monitoring equipment shall be maintained to be able to detect a leak at the earliest possible opportunity. CORRECTIVE ACTION: Immediately relocate this sensor to the lowest point of the [grade] tank. |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030062 | Release Detection (USEPATCR 9d) |  | Tampering with Leak Detection Equipment (USEPATCR 9d) (USEPA Priority) | Leak detection equipment disabled or tampered with in a manner that would prevent the monitoring system from detecting and/or alerting the owner/operator of a leak. | HSC 6.7 25299(a)(9) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 31 | UST System Observations | General Monitoring | Leak detection equipment has not been tampered with or disabled (TCR 9d) | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Leak detection equipment disabled or tampered with in a manner that would prevent the monitoring system from detecting and/or alerting the owner/operator of a leak. | 9d |  | OBSERVATION: Owner/Operator tampered with and/or disabled leak detection equipment in a manner that would prevent the monitoring system from detecting and/or alerting the owner/operator of a leak. CORRECTIVE ACTION: Owner/Operator shall not disable or tamper with monitoring equipment. Repair/replace equipment so that it functions per manufacturer's specifications. Submit verification. | OBSERVATION: The [grade/location] sump sensor was raised [# of inches] approximately inches off the lowest point of the sump [or located on top of the turbine, wrapped up in a plastic bag, etc.] and not located [or maintained] to detect a leak at the earliest opportunity. Monitoring equipment shall be maintained to be able to detect a leak at the earliest possible opportunity. CORRECTIVE ACTION: Immediately relocate this sensor to the lowest point of the [grade/location] sump. |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030075 | Release Detection (USEPATCR 9d) |  | Emergency Generator Tank Systems Line Leak Detector (LLD) (USEPATCR 9d) (USEPA Priority) | Failure of the functional line leak detector (LLD) for emergency generator tank systems to monitor with the capability of detecting a release of 3.0 gallons per hour leak at 10 pounds per square inch within an hour and restrict or shut off the flow of product through the piping or triggers a visual and audible alarm. | 23 CCR 16 2636(f), 2666(c), 2666(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 32 | UST System Observations | General Monitoring | E Gen System LLD detects 3 gph leak & restricts/shuts off flow or activates aud/vis alarm (TCR 9d) | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the functional line leak detector (LLD) for emergency generator tank systems to monitor with the capability of detecting a release of 3.0 gallons per hour leak at 10 pounds per square inch within an hour and restrict or shut off the flow of product through the piping or triggers a visual and audible alarm. | 9d |  | OBSERVATION: Owner/Operator did not install or failed to ensure that a functional LLD was installed on underground piping connected to emergency generator tank system which monitors at least hourly with the capability of detecting a release of 3.0 gph leak at 10 psi and restricts or shuts off the flow of product through the piping, or triggers a visual and audible alarm. CORRECTIVE ACTION: Repair or install LLD on underground piping connected to emergency generator tank system which meets the requirements listed above. |  |  |  |  | Yes | Yes | Yes
UST Program | Design/Construction | 2060022 |  |  | UST Construction - On or After July 1, 2003 and Before July 1, 2004 | Failure of a UST system installed on or after July 1, 2003 and before July 1, 2004 to be designed and constructed with a monitoring system capable of detecting the entry of the hazardous substance stored in the primary containment into the secondary containment and capable of detecting water intrusion into the secondary containment. | HSC 6.7 25290.2(d) | 2016-06-01 | 2099-12-31 | 2016-06-20 08:40 | Existing | 33 | UST System Observations | General Monitoring | System has a mon system capable of detecting entry of haz sub or water into secondary containment | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the UST system installed on or after July 1, 2003 and before July 1, 2004 to comply with one or more of the following: be designed and constructed with a monitoring system capable of detecting the entry of the hazardous substance stored in the primary containment into the secondary containment and/or capable of detecting water intrusion into the secondary containment. |  |  | OBSERVATION: Owner/Operator did not design and/or construct UST system with a continuous monitoring system capable of detecting the entry of the hazardous substance stored in the primary containment into the secondary containment and/or capable of detecting water intrusion into the secondary containment. CORRECTIVE ACTION: Design/Construct UST system installed on or after July 1, 2003 and before July 1, 2004 so that the continuous monitoring system is capable of detecting the entry of the hazardous substance stored in the primary containment into the secondary containment and/or capable of detecting water intrusion into the secondary containment. Submit verification. | OBSERVATION: The [grade/location] sensor failed when tested. The continuous monitoring system shall be maintained to detect the entry of the liquid or vapor phase of the hazardous substance stored in the primary containment into the secondary containment and to detect water intrusion into the secondary containment. CORRECTIVE ACTION: Correct immediately by having a properly licensed, trained, and certified contractor replace the failed component with a functional component (LG 113-x listed, if applicable) and obtain a permit within one business day from the CUPA. If the failed component can’t be replaced immediately, there is a possibility that the [grade] UST system may be red tagged to prevent fuel inputs. |  |  |  | Yes | Yes | No
UST Program | Operations/Maintenance | 2030034 |  |  | Monitoring Equipment Service Tag | Failure to properly affix tag/sticker on each monitoring equipment being certified, repaired, or replaced. | 23 CCR 16 2638(f), 2641(j) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 34 | UST System Observations | General Monitoring | Tag/sticker on affixed monitoring equipment being certified, repaired, or replaced | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly affix tag/sticker on each monitoring equipment being certified, repaired, or replaced. |  |  | OBSERVATION: Tag/sticker was not affixed on monitoring equipment being certified, repaired, or replaced. CORRECTIVE ACTION: Affix tag/sticker on monitoring equipment being certified, repaired, or replaced. Submit verification. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030065 | Release Detection (USEPATCR 9d) |  | Vacuum, Pressure, Hydrostatic (VPH) Monitoring - On or After July 1, 2004 (USEPATCR 9d) (USEPA Priority) | Failure to maintain the interstitial space such that a breach in the primary or secondary containment is detected before the liquid or vapor phase of the hazardous substance stored in the UST tank is released into the environment, i.e. vacuum, pressure, hydrostatic (VPH) monitoring. | HSC 6.7 25290.1(e) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 35 | UST System Observations | VPH Monitoring | Interstitial space of the UST is under constant VPH monitoring (TCR 9d) | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain the interstitial space such that a breach in the primary or secondary containment is detected before the liquid or vapor phase of the hazardous substance stored in the UST tank is released into the environment, i.e. vacuum, pressure, hydrostatic (VPH) monitoring. | 9d |  | OBSERVATION: Owner/Operator did not maintain the interstitial space under constant vacuum, pressure, or hydrostatic monitoring such that a breach in the primary or secondary containment is detected before the liquid or vapor phase of the hazardous substance stored in the UST tank is released into the environment. CORRECTIVE ACTION: Maintain the interstitial space so that constant vacuum, pressure, or hydrostatic monitoring occurs. Submit verification. | OBSERVATION: The [grade/location of annular sensor] sensor failed when tested. The interstitial space of the UST shall be maintained, as designed, under constant vacuum such that a breach in the primary or secondary containment is detected before the hazardous substance is released into the environment. CORRECTIVE ACTION: Correct immediately by having a properly licensed, trained, and certified contractor replace the failed component with a functional component (LG 113-x listed, if applicable) and obtain a permit within [# of business days] from the CUPA. If the failed component can’t be replaced immediately, there is a possibility that the [grade] UST system may be red tagged by to prevent fuel inputs CUPA. | OBSERVATION: The [grade/location of annular sensor] sensor failed when tested. The sensors monitoring the liquid level in the interstitial space shall be maintained so that a breach in the primary or secondary containment is detected before the hazardous substance is released into the environment. CORRECTIVE ACTION: Correct immediately by having a properly licensed, trained, and certified contractor replace the failed component with a functional component (LG 113-x listed, if applicable) and obtain a permit within one business day from the CUPA. If the failed component can’t be replaced immediately, there is a possibility that the [grade] UST system may be red tagged to prevent fuel inputs. |  |  | Yes | Yes | No
UST Program | Design/Construction | 2060023 |  |  | UST Construction - On or After July 1, 2004 | Failure of a UST system installed on or after July 1, 2004 to be designed and constructed with a monitoring system capable of detecting the entry of the liquid or vapor-phase of the hazardous substance stored in the primary containment into the secondary containment and capable of detecting water intrusion into the secondary containment. | HSC 6.7 25290.1(d) | 2016-06-01 | 2099-12-31 | 2016-06-13 09:59 | Existing | 36 | UST System Observations | VPH Monitoring | System has a mon system that can detect entry of haz sub liquid/vapor, or water into sec contain | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a UST system installed on or after July 1, 2004 to be designed and constructed with a monitoring system capable of detecting the entry of the liquid or vapor-phase of the hazardous substance stored in the primary containment into the secondary containment and capable of detecting water intrusion into the secondary containment. |  |  | OBSERVATION: Owner/Operator did not design and/or construct UST system with a monitoring system capable of detecting the entry of the liquid or vapor-phase of the hazardous substance stored in the primary containment into the secondary containment, and/or water intrusion into the secondary containment. CORRECTIVE ACTION: UST system must have a monitoring system capable of detecting the entry of the liquid or vapor-phase of the hazardous substance stored in the primary containment into the secondary containment, and detecting water intrusion into the secondary containment. Submit verification. | OBSERVATION: The [grade/location] sensor failed when tested. The continuous monitoring system shall be maintained to detect the entry of the liquid or vapor phase of the hazardous substance stored in the primary containment into the secondary containment and to detect water intrusion into the secondary containment. CORRECTIVE ACTION: Correct immediately by having a properly licensed, trained, and certified contractor replace the failed component with a functional component (LG 113-x listed, if applicable) and obtain a permit within one business day from the CUPA. If the failed component can’t be replaced immediately, there is a possibility that the [grade] UST system may be red tagged to prevent fuel inputs. |  |  |  | Yes | Yes | No
UST Program | Operations/Maintenance | 2030009 | Corrosion Protection (USEPATCR 9c) |  | Corrosion Protection - Impressed Current/Sacrificial Anode (USEPATCR 9c) (USEPA Priority) | Failure to comply with one or more of the following requirements for the cathodic protection system: 1) Install corrosion protection for USTs and/or the field-installed cathodic protection system to meet the consensus standards. 2) For impressed current: - Have corrosion protection equipment turned on and functioning properly. - Inspect the impressed-current system every 60 days. - Test the impressed-current system within six months of installation or repair and at least every 36 months thereafter. 3) For sacrificial anodes: - Check sacrificial anodes within six months of installation or repair and at least once every 36 months thereafter in accordance with the manufacturer’s instructions. 4) For all corrosion protection systems: - Maintain records for 78 months on-site or off-site at a readily available location if approved by the UPA. | 23 CCR 16 2635(a)(2), 2636(b), 2662(c)(1)(B), 2712(b)(3) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 37 | UST System Observations | Cathodic Protection | Cathodic protection is installed/maintained as required, including required documentation (TCR 9c) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with one or more of the following requirements for the cathodic protection system: 1) Install corrosion protection for USTs and/or the field-installed cathodic protection system to meet the consensus standards. 2) For impressed current: - Have corrosion protection equipment turned on and functioning properly. - Inspect the impressed-current system every 60 days. - Test the impressed-current system within six months of installation or repair and at least every 36 months thereafter. 3) For sacrificial anodes: - Check sacrificial anodes within six months of installation or repair and at least once every 36 months thereafter in accordance with the manufacturer’s instructions. 4) For all corrosion protection systems: - Maintain records for 78 months on-site or off-site at a readily available location if approved by the UPA. | 9c |  | OBSERVATION: Owner/Operator did not install corrosion protection system to meet the consensus standards, did not maintain records for 78 months on-site or off-site at a readily available location if approved by the UPA, or did not do one or more of the following for an impressed current system: inspect system every 60 calendar days; have corrosion protection equipment turned on and functioning properly; test system within six months of installation or repair and at least every 36 months thereafter. For sacrificial anodes failed to check within six months of installation or repair and at least once every 36 months thereafter in accordance with the manufacturer’s instructions. CORRECTIVE ACTION: Correct the deficiencies cited above and submit verification. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030005 | Release Detection (USEPATCR 9d) |  | Continuous In-Tank Leak Detection (CITLD) - Single-Walled Tank (USEPATCR 9d) (USEPA Priority) | Failure of the continuous in-tank leak detection (CITLD) system to perform a 0.2 gallon-per-hour leak test that determines the leak status of the tank at least once every 30 days. | 23 CCR 16 2643(b)(3) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 38 | UST System Observations | Single Walled Tank Monitoring | SW tank continuous in tank leak detection test is functioning properly (TCR 9d) | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the continuous in-tank leak detection (CITLD) system to perform a 0.2 gallon-per-hour leak test that determines the leak status of the tank at least once every 30 days. | 9d |  | OBSERVATION: The continuous in-tank leak detection (CITLD) system does not perform a 0.2 gallon-per-hour leak test that determines the leak status of the tank at least once every 30 days. CORRECTIVE ACTION: Repair continuous in-tank leak detection (CITLD) system so that it functions properly. Submit test results. |  |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030006 | Release Detection (USEPATCR 9d) |  | Automatic Tank Gauging - Single-Walled Tank (USEPATCR 9d) (USEPA Priority) | Failure of the automatic tank gauging (ATG) system to perform valid 0.2 gallon-per-hour leak tests or generate hard-copy test reports at least once every 30 days. | 23 CCR 16 2643(b)(1) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 39 | UST System Observations | Single Walled Tank Monitoring | Monthly 0.2 gph ATG test is being conducted and copies of test results are available (TCR 9d) | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the automatic tank gauging (ATG) system to perform valid 0.2 gallon-per-hour leak tests or generate hard-copy test reports at least once every 30 days. | 9d |  | OBSERVATION: Owner/Operator did not conduct the 0.2 gph automatic tank gauging test on a single wall tank and/or use the automatic tank gauge to generate and print a hard copy of the 0.2 gph test at least once every 30 days. CORRECTIVE ACTION: Conduct the 0.2 gph automatic tank gauging test on a single wall tank and generate a hard copy of the test results at least once every 30 days. Submit test results. |  |  |  |  | Yes | No | Yes
UST Program | Design/Construction | 2060002 | Release Detection (USEPATCR 9d) |  | Automatic Tank Gauge (ATG) / Statistical Inventory Reconciliation / Continuous In-Tank Leak Detection (CITLD) (USEPATCR 9d) (USEPA Priority) | Failure to outfit the single-walled UST system with a monitoring system capable of detecting a leak. | 23 CCR 16 2641(e); HSC 6.7 25292(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 40 | UST System Observations | Single Walled Tank Monitoring | SW UST system has monitoring system capable of detecting releases (TCR 9d) | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to outfit the single-walled UST system with a monitoring system capable of detecting a leak. | 9d |  | OBSERVATION: Owner/Operator failed to install a monitoring system capable of detecting a leak on SW UST system. CORRECTIVE ACTION: Install/ensure proper functioning of monitoring system capable of detecting a leak. Submit verification. |  |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030022 | Release Detection (USEPATCR 9d) |  | Groundwater and Vadose Zone Monitoring (USEPATCR 9d) (USEPA Priority) | Failure to conduct groundwater and/or vadose zone monitoring or maintain site assessment as required. | 23 CCR 16 2647, 2648, 2712(b)(4) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 41 | UST System Observations | Single Walled Tank Monitoring | Groundwater and/or vadose zone monitoring conducted, or site assessment maintained (TCR 9d) | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to conduct groundwater and/or vadose zone monitoring or maintain site assessment as required. | 9d |  | OBSERVATION: Owner/Operator did not conduct groundwater and/or vadose zone monitoring, or maintain site assessment as required. CORRECTIVE ACTION: Conduct groundwater and/or vadose zone monitoring, and maintain site assessment. Submit verification. |  |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030052 | Release Detection (USEPATCR 9d) |  | Single-Walled Pressurized Pipe Monitoring/Testing - (USEPATCR 9d) (USEPA Priority) | Failure to perform one or more of the following on a single-walled pressurized piping system: 1) A 0.1 gallons per hour test at least once every 12 months unless a 0.2 gallons per hour test is performed every 30 days. 2) A 0.1 gallons per hour test within 30 days of the date of the completion of a repair to the piping. | 23 CCR 16 2643(c)(2), 2643(c)(3), 2661(f); HSC 6.7 25292(e)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 42 | UST System Observations | Single Walled Piping Monitoring | .2 gph mthly or .1 gph yrly tests performed on piping, and .1 gph w/in 30 days of repair (TCR 9d) | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform one or more of the following on a single-walled pressurized piping system: 1) A 0.1 gallons per hour test at least once every 12 months unless a 0.2 gallons per hour test is performed every 30 days. 2) A 0.1 gallons per hour test within 30 days of the date of the completion of a repair to the piping. | 9d |  | OBSERVATION: Owner/Operator failed to perform the .2 gph leak test monthly, or 0.1 gph leak test annually, on SW pressurized piping, or failed to complete the .1 gph test within 30 days of a repair. CORRECTIVE ACTION: Perform a 0.2 gph monthly test or 0.1 gph annual test on SW pressurized piping and submit test results. |  |  |  |  | Yes | No | Yes
UST Program | Design/Construction | 2060012 | Release Detection (USEPATCR 9d) |  | Line Leak Detector (LLD) - Installed (USEPATCR 9d) (USEPA Priority) | Failure to install a line leak detector (LLD). | 23 CCR 16 2636(f)(2), 2636(f)(5)(B), 2643(c)(1), 2666(f); HSC 6.7 25290.1(h), 25290.2(g), 25291(f), 25292(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 43 | UST System Observations | Line Leak Detector | LLD installed on pressurized piping system (TCR 9d) | 51 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to install LLD on pressurized piping system. | 9d |  | OBSERVATION: Owner/Operator did not install LLD on pressurized piping system. CORRECTIVE ACTION: Install and test LLD on pressurized piping system. Submit test results. | OBSERVATION: The pressurized piping on the [grade] tank is not equipped with an automatic LLD. CORRECTIVE ACTION: Correct immediately by having a properly licensed, trained, and certified contractor install a leak detector (LG 113-x listed, if applicable)capable of detecting a 3 gph leak. Obtain a permit within 1 business day from the CUPA. |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030027 | Release Detection (USEPATCR 9d) |  | Line Leak Detector (LLD) - Single-Walled Pressurized Pipe (USEPATCR 9d) (USEPA Priority) | Failure of the line leak detector (LLD) monitoring single-walled pressurized piping to meet the following requirements: 1) Monitored at least hourly with the capability of detecting a release of 3.0 gallons per hour leak at 10 pounds per square inch. 2) Shut down the pump when a leak is detected or when the LLD fails or is disconnected. | 23 CCR 16 2666(c), 2643(c)(1) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 44 | UST System Observations | Line Leak Detector | LLD on SW press piping tests hrly, detects 3 gph leak, shuts down pump if leak or LLD fails (TCR 9d) | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the line leak detector (LLD) monitoring single-walled pressurized piping to meet the following requirements: 1) Monitored at least hourly with the capability of detecting a release of 3.0 gallons per hour leak at 10 pounds per square inch. 2) Shut down the pump when a leak is detected or when the LLD fails or is disconnected. | 9d |  | OBSERVATION: Owner/Operator did not repair/maintain LLD to monitor at least hourly, detect releases of 3 gph at 10 psi, and shut down turbine when a leak is detected or when the LLD is disconnected. CORRECTIVE ACTION: Repair/maintain LLD to meet the requirements listed above. |  |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030025 | Release Detection (USEPATCR 9d) |  | Line Leak Detector (LLD)-Double-Walled Pressurized Pipe (USEPATCR 9d) (USEPA Priority) | Failure of the functional line leak detector (LLD) monitoring pressurized piping to meet one or more of the following requirements: 1) Monitored with the capability of detecting a release of 3.0 gallons per hour leak at 10 pounds per square inch within an hour. 2) Restrict or shut off the flow of product through the piping when a leak is detected. | 23 CCR 16 2636(f)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 45 | UST System Observations | Line Leak Detector | LLD on DW press piping monitors hrly, detects a 3.0 gph leak, and restricts/shuts off flow (TCR 9d) | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the functional line leak detector (LLD) monitoring pressurized piping to meet one or more of the following requirements: 1) Monitored with the capability of detecting a release of 3.0 gallons per hour leak at 10 pounds per square inch within an hour. 2) Restrict or shut off the flow of product through the piping when a leak is detected. | 9d |  | OBSERVATION: Line leak detector failed to meet one or more of the following requirements: Monitor at least hourly; Capable of detecting a release of 3.0 gallons per hour at 10 p.s.i.g.; Restricting or shutting off the flow of product through the piping when a leak is detected. CORRECTIVE ACTION: Repair or replace line leak detector (specify tank) so that is it is capable of monitoring at least hourly, detecting a release of 3.0 gallons per hour at 10 p.s.i.g., and restricting or shutting off the flow of product through the piping when a leak is detected. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030053 |  |  | Single-Walled Safe Suction (USEPA Priority) | Safe Suction piping fails to meet one or more of the following requirements: 1) Below grade piping sloped to drain back into storage tank if the suction is released; 2) Only one check valve on the piping located directly below the suction pump; 3) Inspection method is provided which readily demonstrates compliance. | 23 CCR 16 2636(a)(3), 2641(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 46 | UST System Observations | Suction Piping | SW Safe Suction piping drains back into storage tank, one check valve and inspections conducted | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Safe Suction piping fails to meet one or more of the following requirements: 1) Below grade piping sloped to drain back into storage tank if the suction is released; 2) Only one check valve on the piping located directly below the suction pump; 3) Inspection method is provided which readily demonstrates compliance. |  |  | OBSERVATION: Owner/Operator did not construct/inspect single-walled safe-suction piping for compliance with the following: Below grade piping sloped to drain back into storage tank if the suction is released; only one check valve on the piping located directly below the suction pump; and inspection method which readily demonstrates compliance. CORRECTIVE ACTION: Configure/Inspect suction piping to meet all of the following requirements: Below grade piping sloped to drain back into storage tank if the suction is released; only one check valve on the piping located directly below the suction pump; Inspection method which readily demonstrates compliance. Submit verification. |  |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030008 |  |  | Water in Secondary Containment | Failure to keep water out of the secondary containment of UST systems installed on or after July 1, 2003. | HSC 6.7 25290.1(c)(3), 25290.2(c)(3) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 47 | UST System Observations | Secondary Containment | Secondary containment installed after July 1, 2003 is free of water | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to keep water out of the secondary containment of UST systems installed on or after July 1, 2003. |  |  | OBSERVATION: Owner/Operator failed to keep water out of the secondary containment. CORRECTIVE ACTION: Keep all secondary containment free of water. | OBSERVATION: Liquid was observed in the [note which piping, fill, or UDC sump] sump [or tank annular]. If water could enter into the secondary containment by precipitation or infiltration, it must be removed and disposed of properly. CORRECTIVE ACTION: Immediately remove this liquid, make a hazardous waste determination per Title 22 hazardous waste regulations, and manage it accordingly. Ensure that the [note which piping, fill, or UDC sump] sump [or tank annular] is maintained free of liquid. |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030040 | Release Detection (USEPATCR 9d) |  | Piping Obstruction (USEPATCR 9d) (USEPA Priority) | Failure to maintain secondarily contained piping to allow liquid to flow into the sump in the event of a leak (i.e., failure to remove test boot). | 23 CCR 16 2630(d), 2641(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 48 | UST System Observations | Secondary Containment | Secondarily contained piping allows liquid to flow into the sump in the event of a leak (TCR 9d) | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain secondarily contained piping to allow liquid to flow into the sump in the event of a leak (i.e., failure to remove test boot). | 9d |  | OBSERVATION: Owner/Operator did not maintain piping secondary to drain into a sump in the event of a leak. CORRECTIVE ACTION: Piping secondary must be maintained to allow liquid to flow into the sump in the event of a leak. Correct and submit verification. |  |  |  |  | Yes | Yes | No
UST Program | Operations/Maintenance | 2030047 |  |  | Secondary Containment (USEPA Priority) | Failure to maintain secondary containment (e.g. failure of secondary containment testing). | HSC 6.7 25290.1(c), 25290.1(e), 25290.2(c), 25291(a)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 49 | UST System Observations | Secondary Containment | Secondary containment maintained tight and has been confirmed by testing | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain secondary containment (e.g. failure of secondary containment testing). |  |  | OBSERVATION: Secondary containment has not been properly maintained as evidenced by failed secondary containment testing. CORRECTIVE ACTION: Repair secondary containment as needed and retest. Notify CUPA of testing and submit results. | OBSERVATION: The [date] secondary containment test results indicate a failure at the [grade and component]. All secondary containment for the UST system must be tight. CORRECTIVE ACTION: Immediately have a properly licensed, trained, and certified contractor repair or replace the failed component(s) under permit and inspection of the CUPA. | OBSERVATION: [What was found - loss of brine, brine found in sump, liquid in dry annular, etc.] was found in the [grade/location of sump or tank] indicating a leak in the secondary containment. Secondary containment shall be impervious to the liquid and vapor of the substance contained and constructed to prevent structural weakening as a result of contact with any hazardous substances released from the primary containment. CORRECTIVE ACTION: Immediately contact a properly licensed, trained, and certified contractor to make repairs to the UST system under permit and inspection of the CUPA. |  |  | Yes | Yes | Yes
UST Program | Design/Construction | 2060020 | Spill Prevention (USEPATCR 9a) |  | Spill Container (USEPATCR 9a) (USEPA Priority) | Failure to meet one or more of the following requirements: 1) Install or maintain a liquid-tight spill container. 2) Have a minimum capacity of five gallons. 3) Have a functional drain valve or other method for the removal of liquid from the spill container. 4) Be resistant to galvanic corrosion. 5) Perform a tightness test at installation, every 12 months thereafter, or within 30 days after a repair to the spill container. 6) Tested using applicable manufacturer guidelines, industry codes, engineering standards, or a method approved by a professional engineer. 7) Tested by a certified UST service technician. 8) Maintain records of spill containment testing for 36 months. | 23 CCR 16 2635(b), 2637.1(a), 2637.1(b), 2637.1(c), 2665(a), 2665(b), 2712(b)(1)(F); HSC 6.7 25284.2 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 50 | UST System Observations | Secondary Containment | Spill buckets meet requirements, have been tested as required, and records kept for 36 mths (TCR 9a) | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet one or more of the following requirements: 1) Install or maintain a liquid-tight spill container. 2) Have a minimum capacity of five gallons. 3) Have a functional drain valve or other method for the removal of liquid from the spill container. 4) Be resistant to galvanic corrosion. 5) Perform a tightness test at installation, every 12 months thereafter, or within 30 days after a repair to the spill container. 6) Tested using applicable manufacturer guidelines, industry codes, engineering standards, or a method approved by a professional engineer. 7) Tested by a certified UST service technician. 8) Maintain records of spill containment testing for 36 months. | 9a |  | OBSERVATION: Owner/Operator failed to meet one or more of the following spill container requirements: install or maintain spill container which is liquid-tight, has a minimum capacity of five gallons, has a functional drain valve or other method for the removal of liquid from the spill container, and is resistant to galvanic corrosion; did not perform tightness test at installation, every 12 months thereafter, or within 30 days after a repair; did not have tested using manufacturer's guidelines, industry codes, engineering standards, or method approved by PE, or was not tested by a certified UST service technician; or failed to maintain testing records for 36 months. CORRECTIVE ACTION: Install or repair spill buckets to meet all of the listed requirements, have tightness tested using approved method, by certified UST service technician, and submit documentation to verify compliance. Maintain all testing records for 36 months. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030035 |  |  | Unsafe UST Operation (USEPA Priority) | Failure to operate the UST system to prevent unauthorized releases including leaks, spills, and/or overfills. | HSC 6.7 25292.1(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 51 | UST System Observations | Overfill | UST system is operated to prevent unauthorized release, including spills and overfills | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to operate the UST system to prevent spills and/or overfills. |  |  | OBSERVATION: Owner/Operator did not operate UST system to prevent spills and/or overfills. CORRECTIVE ACTION: Operate UST system to prevent spills and/or overfills. Submit verification. | OBSERVATION: [Note what you found - spills and/or stains on ground, failed secondary containment not repaired, spill bucket not repaired, overfill prevention system broken, etc]. The underground storage tank system shall be operated to prevent unauthorized releases. CORRECTIVE ACTION: Immediately [make specific repairs, clean spills, etc.]. |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030036 | Overfill Prevention (USEPATCR 9b) |  | Overfill Prevention (USEPATCR 9b) (USEPA Priority) | Failure to comply with one or more of the following overfill prevention equipment requirements: 1) Alert the transfer operator when the tank is 90 percent full by restricting the flow into the tank or triggering an audible and visual alarm; or 2) Restrict delivery of flow to the tank at least 30 minutes before the tank overfills, provided the restriction occurs when the tank is filled to no more than 95 percent of capacity; and activate an audible alarm at least five minutes before the tank overfills; or 3) Provide positive shut-off of flow to the tank when the tank is filled to no more than 95 percent of capacity; or 4) Provide positive shut-off of flow to the tank so that none of the fittings located on the top of the tank are exposed to product due to overfilling. 5) Install/retrofit overfill prevention equipment that does not use flow restrictors on vent piping to meet overfill prevention equipment requirements when the overfill prevention equipment is installed, repaired, or replaced on and after October 1, 2018. 6) Perform an inspection at least once every 36 months, at installation and every 36 months thereafter. 7) Inspected within 30 days after a repair to the overfill prevention equipment. 8) Inspected using an applicable manufacturer guidelines, industry codes, engineering standards, or a method approved by a professional engineer. 9) Inspected by a certified UST service technician. 10) Maintain records of overfill prevention equipment inspection for 36 months. | 23 CCR 16 2635(c)(1), 2635(d), 2637.2(a) 2637.2(b), 2637.2(c), 2665, 2712(b)(1)(G) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 52 | UST System Observations | Overfill | Overfill prevention system has not been overridden and meets overfill requirements (TCR 9b) | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with one or more of the following overfill prevention equipment requirements: 1) Alert the transfer operator when the tank is 90 percent full by restricting the flow into the tank or triggering an audible and visual alarm; or 2) Restrict delivery of flow to the tank at least 30 minutes before the tank overfills, provided the restriction occurs when the tank is filled to no more than 95 percent of capacity; and activate an audible alarm at least five minutes before the tank overfills; or 3) Provide positive shut-off of flow to the tank when the tank is filled to no more than 95 percent of capacity; or 4) Provide positive shut-off of flow to the tank so that none of the fittings located on the top of the tank are exposed to product due to overfilling. 5) Install/retrofit overfill prevention equipment that does not use flow restrictors on vent piping to meet overfill prevention equipment requirements when the overfill prevention equipment is installed, repaired, or replaced on and after October 1, 2018. 6) Perform an inspection at least once every 36 months, at installation and every 36 months thereafter. 7) Inspected within 30 days after a repair to the overfill prevention equipment. 8) Inspected using an applicable manufacturer guidelines, industry codes, engineering standards, or a method approved by a professional engineer. 9) Inspected by a certified UST service technician. 10) Maintain records of overfill prevention equipment inspection for 36 months. | 9b |  | OBSERVATION: Owner/Operator failed to meet one or more of the requirements applicable to overfill prevention equipment. [Describe] CORRECTIVE ACTION: Maintain overfill prevention system to comply with the deficiencies noted above. Submit verification. | OBSERVATION: The [ATG, mechanical flapper, ball float (note which ones), enunciator, etc.] used as the overfill prevention system is not currently functional [or “is being overridden by a stick placed in the drop tube”] on the [note which ATG, mechanical flapper, ball float, enunciator, etc.] UST. CORRECTIVE ACTION: Immediately discontinue deposition of petroleum into this tank until the component is repaired or replaced by a properly licensed, trained, and certified contractor under permit and inspection of the CUPA. If the failed component can’t be replaced immediately, there is a possibility that the [grade] UST system may be red tagged to prevent fuel inputs. | OBSERVATION: The [ATG, enunciator, light, etc.] used as [part of] the overfill prevention system is not currently functional on the [note which ATG, enunciator, light, etc.] UST. The [ATG, enunciator, light, etc.] was replaced and retested during the inspection. CORRECTIVE ACTION: Immediately discontinue deposition of petroleum into this tank until the component is repaired or replaced by a properly licensed, trained, and certified contractor under permit and inspection of the CUPA. If the failed component can’t be replaced immediately, there is a possibility that the [grade] UST system may be red tagged to prevent fuel inputs. | OBSERVATION: The mechanical overfill prevention device on the [grade] UST is currently overridden by the presence of a measuring stick placed in the drop tube. The stick was removed by the service technician onsite. CORRECTIVE ACTION: Take all necessary precautions to prevent reoccurrences in the future. |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010007 | Financial Responsibility (USEPATCR 11) |  | Financial Responsibility (USEPATCR 11) | Failure to submit and maintain complete and current Certification of Financial Responsibility or other mechanism of financial assurance. | 23 CCR 16 2711(a)(11); 23 CCR 18 2808.1, 2809-2809.2; HSC 6.7 25292.2(a); HSC 6.75 25299.30-25299.34 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 53 | On Site Records | Certifications | Submitted/maintained current Cert of Financial Responsibility/mech of financial assurance (TCR 11) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit and maintain complete and current Certification of Financial Responsibility or other mechanism of financial assurance. | 11 |  | OBSERVATION: Financial responsibility documents have not been submitted to the CUPA. Current financial responsibility documents are required to be submitted annually. CORRECTIVE ACTION: Complete and submit a copy of the financial responsibility by [date, 30 days from now]. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030007 |  |  | Compatibility Records | Failure to submit and/or maintain documentation regarding compatibility for UST system components. | 23 CCR 16 2631(j), 2631(l), 2631.1(b), 2640.1, 2665(b), 2666(b)(2), 2666(e)(2), 2711(c), 2712(b)(5) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 54 | On Site Records | Certifications | Documentation of compatibility for UST system components submitted and/or maintained. | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit and/or maintain documentation regarding compatibility for UST system components. |  |  | OBSERVATION: Owner/Operator did not submit and maintain documentation regarding compatibility for UST system components. CORRECTIVE ACTION: Submit and maintain documentation regarding compatibility for UST system components. |  |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010004 | Designated Operator Inspection Requirements (USEPATCR 12) |  | Designated Operator - Inspection Records (USEPATCR 12) (USEPA Priority) | Failure to maintain on-site, or off-site at a readily available location if approved by the UPA, copies of the "Designated Underground Storage Tank Operator Visual Inspection Report" and all attachments for 36 months. | 23 CCR 16 2716(f) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 55 | On Site Records | Designated Operator | Copies of DO inspections for last 12 months maintained, 36 months for those after 10/1/18 (TCR 12) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain on-site, or off-site at a readily available location if approved by the UPA, copies of the "Designated Underground Storage Tank Operator Visual Inspection Report" and all attachments for 36 months. | 12 |  | OBSERVATION: Facility did not maintain copies on-site, or off-site at a readily available location, of the "Designated Underground Storage Tank Operator Visual Inspection Report" and all attachments for 36 months. CORRECTIVE ACTION: Submit copies of the "Designated Underground Storage Tank Operator Visual Inspection Report" and all attachments, for the last [enter #] months, and maintain copies of these monthly inspections on-site or at a readily available location, for 36 months. | OBSERVATION: The [month/year] designated operator monthly inspection report(s) were not found onsite. Designated operator monthly inspection reports for the previous 36 months shall be retained onsite. CORRECTIVE ACTION: Locate and ensure that copies of the previous 36 months of designated operator monthly inspection reports are maintained onsite. Submit copies to the CUPA by [date, 30 days from now]. |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030013 | Designated Operator Inspection Requirements (USEPATCR 12) |  | Designated Operator (DO) - Inspection (USEPATCR 12) (USEPA Priority) | Failure to comply with one or more of the following Designated Operator (DO) inspection requirements: 1) Conduct the DO visual inspection at least once every 30 days. 2) Be performed by an ICC certified DO. 3) Inspect monthly alarm history report, check that alarms are documented and responded to appropriately, and attach a copy. 4) Inspect for the presence of liquid/debris in spill containers. 5) Inspect for the presence of liquid/debris in under dispenser containment (UDC) and ensure that the monitoring equipment is positioned correctly. 6) Inspect for liquid or debris in containment sumps where an alarm occurred with no service visit. 7) Check that all testing and maintenance has been completed and documented. 8) Verify that all facility employees have been trained in accordance with 23 CCR 2715(c). 9) The owner/operator sign and date the Designated Underground Storage Tank Operator Visual Inspection Report within 72 hours of being provided a signed copy. | 23 CCR 16 2716(a) through (e) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 56 | On Site Records | Designated Operator | DO inspections completed at least every 30 days and meet all requirements (TCR 12) | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with one or more of the following Designated Operator (DO) inspection requirements: 1) Conduct the DO visual inspection at least once every 30 days. 2) Be performed by an ICC certified DO. 3) Inspect monthly alarm history report, check that alarms are documented and responded to appropriately, and attach a copy. 4) Inspect for the presence of liquid/debris in spill containers. 5) Inspect for the presence of liquid/debris in under dispenser containment (UDC) and ensure that the monitoring equipment is positioned correctly. 6) Inspect for liquid or debris in containment sumps where an alarm occurred with no service visit. 7) Check that all testing and maintenance has been completed and documented. 8) Verify that all facility employees have been trained in accordance with 23 CCR 2715(c). 9) The owner/operator sign and date the Designated Underground Storage Tank Operator Visual Inspection Report within 72 hours of being provided a signed copy. | 12 |  | OBSERVATION: Facility did not comply with one or more of the following DO inspection requirements: Conduct the DO visual inspection at least once every 30 days; Performed by an ICC certified DO; Inspect monthly alarm history report, check that alarms are documented and responded to appropriately, and attach a copy; Inspect for the presence of liquid/debris in spill containers; Inspect for the presence of liquid/debris in under dispenser containment (UDC) and ensure that the monitoring equipment is positioned correctly; Inspect for liquid or debris in containment sumps where an alarm occurred with no service visit; Check that all testing and maintenance has been completed and documented; Verify that all facility employees have been trained in accordance with 23 CCR 2715(c); The owner/operator signed and dated the Designated Underground Storage Tank Operator Visual Inspection Report within 72 hours of being provided a signed copy. CORRECTIVE ACTION: Ensure that facility is complying with all DO inspection requirements noted above. Submit copy of compliant DO inspection record. | OBSERVATION: The designated operator failed to visually inspect the [note what was not inspected by the DO] for leaks, water, or debris during the [month/year] monthly inspection(s). During the monthly inspection, the designated operator shall visually inspect all spill containers and UDC sumps, and any tank top sump that had an alarm for which there is no record of a service visit. CORRECTIVE ACTION: Ensure that designated operators performing monthly inspections at this facility are inspecting all of the required areas and noting it on the on the reports. | OBSERVATION: The designated operator failed to check and note the correct test dates for the [note which tests] on the [month/year] designated operator monthly inspection report(s). [You can note the incorrect dates, or missing dates here.] During the monthly inspection, the designated operator shall check that all required testing and maintenance for the UST system have been completed and document the dates they were done. CORRECTIVE ACTION: Ensure that designated operators performing monthly inspections at this facility are including all of the required information on the reports. | OBSERVATION: The designated operator failed to document all the alarms from the attached alarm history on the [month/year] designated operator monthly inspection report(s) and failed to check that they were responded to appropriately. The missing alarms include: [list alarm locations and dates]. During the monthly inspection, the designated operator shall review the alarm history for the previous month, check that each alarm was documented and responded to appropriately, and attach a copy of the alarm history with documentation taken in response to any alarms to the monthly report. CORRECTIVE ACTION: Ensure that designated operators performing monthly inspections at this facility are including all of the required information on the reports. |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030012 |  |  | Facility Employee Training | Failure to comply with one or more of the following: 1) Provide initial training before the individual performs the duties of a facility employee. 2) Train facility employees in the proper operation and maintenance of the underground storage tank system at least once every 12 months. 3) Have at least one facility employee present during operating hours that has been trained in the proper operation and maintenance of the UST system by a designated operator (DO). | 2715(c), 2715(c)(1), 2715(c)(2) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 57 | On Site Records | Designated Operator | Initial and annual training provided to employees and at least one trained employee is present | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with one or more of the following: 1) Provide initial training before the individual performs the duties of a facility employee. 2) Train facility employees in the proper operation and maintenance of the underground storage tank system at least once every 12 months. 3) Have at least one facility employee present during operating hours that has been trained in the proper operation and maintenance of the UST system by a designated operator (DO). |  |  | OBSERVATION: Owner/Operator failed to do one or more of the following: Provide initial training before the individual performs the duties of a facility employee; Train facility employees in the proper operation and maintenance of the underground storage tank system at least once every 12 months; Have at least one employee present during operating hours that has been trained in the proper operation and maintenance of the UST system by a designated operator (DO). CORRECTIVE ACTION: Ensure that employees receive initial and annual training in the proper operation and maintenance of the UST system and that at least one employee is present during operating hours that has been trained in the proper operation and maintenance of the UST system by a designated operator (DO). | OBSERVATION: The designated operator employee training for [name of employee] was not performed [or not current]. The designated operator shall train facility employees for which he or she is responsible in the proper operation and maintenance of the UST system once every 12 months. The training shall include, but is not limited to: 1. Operation of the UST system in a manner consistent with the facility’s best management practices 2. Employee’s role with regard to monitoring equipment as specified in the facility’s monitoring plan 3. Employee’s role with regard to spills and overfills as specified in the facility’s response plan 4. Name of the contact person(s) for emergencies and monitoring equipment alarms. CORRECTIVE ACTION: Ensure that employees have been trained by the designated operator, maintain the list onsite, and submit a copy of the training records to the CUPA by [date, 30 days from now]. |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010015 |  |  | Designated Operator - Records | Failure to maintain a copy of the "Facility Employee Training Certificate" on-site or off-site at a readily available location, if approved by the UPA. | 23 CCR 16 2715(c)(3), 2715(c)(4) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 58 | On Site Records | Designated Operator | Copies of Facility Employee Training Certificates maintained | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain a copy of the "Facility Employee Training Certificate" on-site or off-site at a readily available location, if approved by the UPA. |  |  | OBSERVATION: Owner/Operator did not maintain a copy of the "Facility Employee Training Certificate" on-site or off-site at a readily available location. CORRECTIVE ACTION: Maintain copies of the "Facility Employee Training Certificate" on-site or off-site at a readily available location. |  |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2030001 | Release Detection (USEPATCR 9d) |  | Release Detection Monitoring and Maintenance Records (USEPATCR 9d) (USEPA Priority) | Failure to maintain monitoring records for 36 months and/or failure to maintain maintenance records (including written performance claims and calibration records) for the release detection system for 60 months. | 23 CCR 16 2712(b)(1)and(2) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 59 | On Site Records | Logs | Records of release detection monitoring and maintenance properly maintained (TCR 9d) | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain monitoring records for 36 months and/or failure to maintain maintenance records (including written performance claims and calibration records) for the release detection system for 60 months. | 9d |  | OBSERVATION: Owner/Operator failed to maintain release detection monitoring and maintenance records. CORRECTIVE ACTION: Maintain release detection monitoring and maintenance records for required time frames. | OBSERVATION: Maintenance and monitoring records for [note date range] were not found onsite. Monitoring records include: (1) date and time of all monitoring or sampling; (2) monitoring equipment calibration and maintenance records; (3) results of any visual observations; (4) results of sample analysis performed a lab or in the field; (5) logs of all readings of gauges or other monitoring equipment, ground water elevations, or other test results; (6) results of inventory readings and reconciliations. These records shall be kept onsite for at least 3 years. CORRECTIVE ACTION: Immediately locate and maintain the maintenance and monitoring records for [note date range] onsite and submit copies to the CUPA by [date, 30 days from now]. |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030020 |  |  | Emergency Generator Piping - Exemption | Failure to meet one or more exemption requirements for emergency generator tank system unburied fuel piping: 1) Conduct visual inspections each time the tank is operated but no less than monthly. 2) Maintain a log of inspection results for review by the UPA. | HSC 6.7 25281.5(b)(3) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 60 | On Site Records | Logs | Unburied fuel piping visually inspected at least monthly and log kept | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet one or more exemption requirements for emergency generator tank system unburied fuel piping: 1) Conduct visual inspections each time the tank is operated but no less than monthly. 2) Maintain a log of inspection results for review by the UPA. |  |  | OBSERVATION: Owner/Operator did not conduct visual inspections each time the tank is operated, but not less than monthly, and maintain a log of inspection results for review by the CUPA. CORRECTIVE ACTION: Conduct visual inspections each time the tank is operated, but not less than monthly, and maintain a log of inspection results for review by the CUPA. | OBSERVATION: A log of monthly checks of the unburied single walled piping was not found onsite. For an emergency generator tank system, the unburied piping is exempt from regulation if visual inspections are made each time the system is operated, but no less than monthly, and a log is maintained. CORRECTIVE ACTION: Immediately begin inspecting the system each time the system is operated, but no less than monthly, and maintain a log of the inspections, or submit a permit application to upgrade the UST system to meet Title 23 UST regulations. |  |  |  | Yes | No | No
UST Program | Operations/Maintenance | 2030049 | Release Detection (USEPATCR 9d) |  | Single-Walled Conventional Suction Monitoring and Record Keeping (USEPATCR 9d) (USEPA Priority) | Failure to conduct monitoring and maintain written records for single-walled conventional suction systems. | 23 CCR 16 2643(d) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 61 | On Site Records | Logs | Monitoring conducted and written records maintained for SW conventional suction system (TCR 9d) | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to conduct monitoring and maintain written records for single-walled conventional suction systems. | 9d |  | OBSERVATION: Owner/Operator did not conduct monitoring and/or maintain written records for single-walled conventional suction systems. CORRECTIVE ACTION: Monitor single-walled conventional suction systems and maintain adequate records. |  |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030032 |  |  | Marina Piping - Exclusion | Failure to meet one or more of the following requirements for exclusion of unburied fuel delivery piping at a marina: 1) Conduct daily inspections of the piping. 2) Maintains a log of inspection results for review by the UPA. | HSC 6.7 25281.5(b)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 62 | On Site Records | Logs | Unburied fuel piping at marinas visually inspected at least daily and log kept | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet one or more of the following requirements for exclusion of unburied fuel delivery piping at a marina: 1) Conduct daily inspections of the piping. 2) Maintains a log of inspection results for review by the UPA. |  |  | OBSERVATION: Owner/Operator at a marina did not conduct daily inspection of the unburied fuel piping and/or maintain a log of inspection results. CORRECTIVE ACTION: Conduct daily inspection of the unburied fuel piping and maintain a log of inspection results. | OBSERVATION: A log of visual inspections for the unburied marina fuel piping was not found onsite. To maintain exclusion of this piping from regulation, the owner or operator shall conduct daily visual inspections of this piping and maintain a log of inspection results for three years. CORRECTIVE ACTION: Immediately begin daily visual inspections, maintain a log of inspection results, and submit a copy of the log for the next 30 days to the CUPA, or submit a permit application to upgrade the UST system to meet Title 23 UST regulations. |  |  |  | Yes | No | No
UST Program | Operations/Maintenance | 2030057 |  |  | Statistical Inventory Reconciliation (SIR) (USEPA Priority) | When statistical inventory reconciliation (SIR) results indicate failure or are inconclusive, owner/operator failed to complete one or more of the following: 1) Notify UPA of a possible release within 24 hours; 2) Submit copy of the report to the UPA within 10 days; 3) Inspect records for errors; 4) Physically inspect the UST system within 24 hours; 5) Have meters recalibrated within 48 hours of receipt of report. | 23 CCR 16 2646.1(d) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 63 | On Site Records | Logs | The facility met all corrective action requirements when SIR results failed | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | When statistical inventory reconciliation (SIR) results indicate failure or are inconclusive, owner/operator failed to complete one or more of the following: 1) Notify UPA of a possible release within 24 hours; 2) Submit copy of the report to the UPA within 10 days; 3) Inspect records for errors; 4) Physically inspect the UST system within 24 hours; 5) Have meters recalibrated within 48 hours of receipt of report. |  |  | OBSERVATION: Owner/Operator failed to complete one or more of the following when statistical inventory reconciliation results indicate failure or are inconclusive: notify CUPA of a possible release within 24 hours; submit copy of the report to the CUPA within 10 days; inspect records for errors and physically inspect the UST system within 24 hours; have meters recalibrated within 48 hours of receipt of report. CORRECTIVE ACTION: When statistical inventory reconciliation results indicate failure or inconclusive, owner/operator shall complete one or more of the following: notify CUPA of a possible release within 24 hours; submit copy of the report to the CUPA within 10 days; inspect records for errors and physically inspect the UST system within 24 hours; have meters recalibrated within 48 hours of receipt of report. Submit verification. |  |  |  |  | Yes | No | Yes
UST Program | Operations/Maintenance | 2030058 | Release Detection (USEPATCR 9d) |  | Statistical Inventory Reconciliation (SIR) (USEPATCR 9d) (USEPA Priority) | Failure to meet one or more of the requirements of statistical inventory reconciliation (SIR), including, but not limited to: 1) Measurements taken daily, 2) Calculated every 30 days, 3) Capable of detecting a 0.2 gallons per hour release, 4) Report a quantitative leak rate using a threshold value that does not exceed one-half the minimum detectable leak rate, 5) Conduct a tank integrity test every 24 months, 6) Conduct piping and or tank test within 15 days of receipt of two successive SIR reports which are inconclusive or which indicate a possible release, 7) And/or calibrate dispenser meters. | 23 CCR 16 2643(b)(2), 2646.1(a)-(h),(j),(k) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 64 | On Site Records | Logs | All Statistical Inventory Reconciliation (SIR) requirements met (TCR 9d) | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet one or more of the requirements of statistical inventory reconciliation (SIR), including, but not limited to: 1) Measurements taken daily, 2) Calculated every 30 days, 3) Capable of detecting a 0.2 gallons per hour release, 4) Report a quantitative leak rate using a threshold value that does not exceed one-half the minimum detectable leak rate, 5) Conduct a tank integrity test every 24 months, 6) Conduct piping and or tank test within 15 days of receipt of two successive SIR reports which are inconclusive or which indicate a possible release, 7) And/or calibrate dispenser meters. | 9d |  | OBSERVATION: Owner/Operator using SIR did not do one or more of the following: measurements taken daily, calculated every 30 days, capable of detecting a 0.2 gph release, report a quantitative leak rate using a threshold value that does not exceed one-half the minimum detectable leak rate, conduct a tank integrity test every 24 months, conduct piping and or tank test within 15 days of receipt of two successive SIR reports which are inconclusive or which indicate a possible release and/or calibrate dispenser meters. CORRECTIVE ACTION: Conduct SIR in compliance with all requirements. Submit verification. |  |  |  |  | Yes | No | Yes
UST Program | Administration/Documentation | 2010012 |  |  | Record Keeping: General | Failure to maintain UST records in sufficient detail to enable the UPA to determine whether the UST systems are in compliance. | HSC 6.7 25293 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 65 | On Site Records | Maintenance/Tests | UST records sufficiently maintained to document compliance | 58 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain UST records in sufficient detail to enable the UPA to determine whether the UST systems are in compliance. |  |  | OBSERVATION: Owner/Operator did not maintain UST records in sufficient detail to enable the UPA to determine if UST systems are in compliance. CORRECTIVE ACTION: Maintain UST records in sufficient detail to enable the UPA to determine if UST systems are in compliance. |  |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010008 |  |  | Repair/Upgrade Record Retention | Failure to maintain records of repairs, linings, and upgrades on site, or off site if approved by the UPA, for the life of the UST. | 23 CCR 16 2712(b)(6) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 66 | On Site Records | Maintenance/Tests | Monitoring, maintenance, repairs, linings, and upgrade records maintained for life of UST | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain records of repairs, linings, and upgrades on site, or off site if approved by the UPA, for the life of the UST. |  |  | OBSERVATION: Records of repairs, linings, and upgrades for the UST system were not found onsite. These records shall be kept onsite for the life of the tank. CORRECTIVE ACTION: Immediately locate and maintain these records onsite and submit copies to the CUPA by [date, 30 days from now]. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030078 |  |  | Failure to Retain Operating Permit | Failure to retain a paper or electronic copy of the permit to operate at the facility. | 23 CCR 16 2712(i) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 67 | On Site Records | Documentation | Owner/Operator retained a paper or electronic copy of the permit to operate at the facility | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to retain a paper or electronic copy of the permit to operate at the facility. |  |  | OBSERVATION: Owner/Operator did not retain a paper or electronic copy of the permit to operate at the facility. CORRECTIVE ACTION: Retain a paper or electronic copy of the permit to operate at the facility. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030046 |  |  | Response Plan Available | Failure to submit and have a current UST Response Plan readily available on site. | 23 CCR 16 2712(i), 2632(d)(2), 2634(e), 2641(h) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 68 | On Site Records | Documentation | A current UST Response Plan has been submitted | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit and have a current UST Response Plan readily available on site. |  |  | OBSERVATION: Owner/Operator did not submit and/or maintain a current UST response plan readily available on site. CORRECTIVE ACTION: Submit a current UST response plan to CERS and maintain a current copy readily available on site. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030033 |  |  | Monitoring Plan Available | Failure to submit and have current UST Monitoring Plan readily accessible at the facility. | 23 CCR 16 2712(i) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 69 | On Site Records | Documentation | A current UST monitoring plan has been submitted and is readily accessible at the facility | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit and have current UST Monitoring Plan readily accessible at the facility. |  |  | OBSERVATION: Owner/Operator did not submit and/or maintain a current UST monitoring plan readily accessible at the facility. CORRECTIVE ACTION: Submit and maintain a current UST monitoring plan readily accessible at the facility. | OBSERVATION: Approved copy of the monitoring plan was not found onsite. CORRECTIVE ACTION: Immediately locate and retain a copy onsite. | OBSERVATION: The monitoring plan onsite is not current and [or] not approved by the CUPA. CORRECTIVE ACTION: Update the required information in CERS and submit for review by the CUPA and maintain current copy onsite. | OBSERVATION: Current approved copies of the monitoring plan was not found onsite. CORRECTIVE ACTION: Maintain a copy of the current and approved monitoring plan on-site. if the plan is not current update the plan in CERS and submit for review by the CUPA. Upon acceptable review maintain a copy of the approved monitoring plan on-site. |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030037 |  |  | Agreement Between UST Permit Holder and UST Operator (Owner/Operator Agreement) | Failure to implement or maintain a written agreement between the UST owner and operator. | 23 CCR 16 2620(b); HSC 6.7 25284(a)(3)(A) & (B); | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 70 | On Site Records | Documentation | Facility has a current written owner/operator agreement | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to implement or maintain a written agreement between the UST owner and operator. |  |  | Observation: Owner/Operator failed to implement or maintain a written agreement between the UST owner and the operator (owner/operator agreement). Corrective Action: Implement/Maintain written agreement between the UST owner and the operator (owner/operator agreement) |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030061 |  |  | Recording Unauthorized Releases (USEPA Priority) | Failure to record any unauthorized release from the primary containment. | 23 CCR 16 2651; HSC 6.7 25294 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 71 | On Site Records | Documentation | Any unauthorized release from the primary containment recorded | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to record any unauthorized release from the primary containment. |  |  | OBSERVATION: Owner/Operator did not record all unauthorized releases from the primary containment. CORRECTIVE ACTION: Record all actual unauthorized releases from the UST system primary containment. Submit verification. | OBSERVATION: [Describe the release that occurred, was found, etc.] on [date, if known] was not recorded. Any release from the primary containment that does not escape the secondary containment and was cleaned up within eight hours of being detected shall be recorded with the following information: 1. Operator’s name and phone number 2. List of types, quantities, and concentrations of hazardous substances released 3. Description of actions taken to control and clean the release 4. Method and location of disposal of the released substances 5. Description of actions taken to repair and prevent future releases 6. Description of method used to reactivate interstitial monitoring after repair or replacement of primary containment. CORRECTIVE ACTION: Immediately record this release with the information required, and maintain it onsite with the facility’s monitoring records. Submit a copy of the recordable release statement to the CUPA by [date, 30 days from now]. | OBSERVATION: [Describe the release that occurred, was found, etc.] on [date, if known] was not reported to the CUPA within 24 hours and [or] a full report was not submitted to the CUPA within five working days. Any release from the primary containment that does not escape the secondary containment and was not cleaned up within eight hours of detection, or any release that escapes the secondary containment shall be reported to the CUPA within 24 hours and a full report shall be submitted within five working days. The report shall include at least the following information: 1. Owner’s or operator’s name and telephone number 2. List of types, quantities, and concentrations of hazardous substances released 3. Approximate date of release 4. Date release was discovered 5. Date release was stopped 6. Description of actions taken to control and stop the release 7. Description of corrective and remedial actions 8. Methods of clean up implemented to date, and proposed clean up actions with a time schedule 9. Method and location of disposal of waste generated from release and clean up. Attach copies of any hazardous waste manifests. 10. Description of proposed methods of repair or replacement of primary or secondary containment 11. Description of additional actions taken to prevent future releases. CORRECTIVE ACTION: Immediately prepare a report with the required information and submit a copy to the CUPA. Ensure that any future releases are reported appropriately. |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030039 |  |  | Permit Conditions | Failure to comply with any of the applicable requirements of the permit issued for the operation of the UST system. | 23 CCR 16 2712 | 2016-06-01 | 2099-12-31 | 2016-06-10 15:19 | Existing | 72 | General Operating Requirements | Permit Condition/Approval | Compliance with all operating permit requirements | 49 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with one or more of the operating permit requirements. |  |  | OBSERVATION: Owner/Operator did not comply with all operating permit requirements. CORRECTIVE ACTION: Comply with all operating permit requirements. Submit verification. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030059 |  |  | Emergency Generator Tank System In Below-Grade Structure Exemption | Failure to meet the conditions required to exempt an emergency generator tank system in a below-grade structure from UST regulations. | HSC 6.7 25281.6(a) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 73 | General Operating Requirements | Permit Condition/Approval | UST system below ground connected to a E Gen system in compliance with exclusion/exemption req's | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the conditions required to exempt an emergency generator tank system in a below-grade structure from UST regulations. |  |  | OBSERVATION: Owner/Operator did not maintain compliance with conditions of exemption from UST regulation for an emergency generator system in a below grade structure. CORRECTIVE ACTION: Maintain UST system below ground connected to a emergency generator system in accordance with exclusion/exemption status. Submit verification. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030076 |  |  | Tank In Below-Grade Structure | Failure to meet the conditions required to exempt a tank system located in a below-grade structure from UST regulations. | HSC 6.7 25283.5(a) | 2016-06-01 | 2099-12-31 | 2016-05-13 14:32 | Existing | 74 | General Operating Requirements | Permit Condition/Approval | Tank system located in below grade structure meets the exemption conditions | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the exemption conditions for a tank system located in a below grade structure. |  |  | OBSERVATION: Owner/Operator did not meet the exemption conditions for a tank system located in a below grade structure. CORRECTIVE ACTION: Maintain tank system so that it meets the exemption conditions for a tank system located in a below grade structure. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030014 |  |  | Designated Operator (DO) - Unstaffed Facility Training | Failure to obtain approval from the UPA for a training program at an unstaffed facility and/or implement the approved training program. | 23 CCR 16 2715(c)(2) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 75 | General Operating Requirements | Permit Condition/Approval | Owner/Operator received approval and has implemented a training program at an unstaffed facility | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to obtain approval from the UPA for a training program at an unstaffed facility and/or implement the approved training program. |  |  | OBSERVATION: The owner/operator did not obtain CUPA approval for a training program at an unstaffed facility and/or implement the approved training program. CORRECTIVE ACTION: Obtain CUPA approval for a training program at an unstaffed facility and/or implement the approved training program. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030015 | Release Detection (USEPATCR 9d) |  | Leak Detection Performance Certification (USEPATCR 9d) (USEPA Priority) | Failure to demonstrate to the UPA that the equipment and methods used to monitor the UST system are certified by an independent third-party as complying with the standards set forth in 23 CCR 2643(f). | 23 CCR 16 2630(d), 2632(c)(2)(A),2643(f),2644.1(a)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 76 | General Operating Requirements | Permit Condition/Approval | Facility demonstrated that methods used to monitor the UST system complies with standards (TCR 9d) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to demonstrate to the UPA that the equipment and methods used to monitor the UST system are certified by an independent third-party as complying with the standards set forth in 23 CCR 2643(f). | 9d |  | OBSERVATION: Owner/Operator did not demonstrate to the CUPA that the methods approved to monitor the UST system meets the standards set forth in 2643(f). CORRECTIVE ACTION: Demonstrate to the CUPA that the methods approved to monitor the UST system meets the standards set forth in 2643(f). Submit verification. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030073 |  |  | Corrective Actions/Return to Compliance | Failure to implement the corrections specified in the inspection report within 30 days of receiving an inspection report from either the UPA or special inspector. | 23 CCR 16 2712(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 77 | General Operating Requirements | Permit Condition/Approval | Facility has corrected cited violations within 30 days of receiving report | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to implement the corrections specified in the inspection report within 30 days of receiving an inspection report from either the UPA or special inspector. |  |  | OBSERVATION: Owner/Operator did not implement the corrections specified in the inspection report within 30 days of receiving an inspection report from either the CUPA or special inspector. CORRECTIVE ACTION: Correct all deficiencies identified on the inspection report provided by the CUPA or special inspector within 30 days. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030077 | Release Detection (USEPATCR 9d) |  | Reporting Unauthorized Releases (USEPATCR 9d) (USEPA Priority) | Failure to notify and/or prepare a report to the UPA upon discovery of a reportable or failed to record unauthorized release. | 23 CCR 16 2650(e), 2652; HSC 6.7 25295(a)(1) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 78 | General Operating Requirements | Permit Condition/Approval | Owner/Operator notified/prepared report upon discovery of unauthorized release (TCR 9d) | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to notify and/or prepare a report to the UPA upon discovery of a reportable or failed to record unauthorized release. | 9d |  | OBSERVATION: Owner/Operator did not notify and/or prepare a report to the CUPA upon discovery of a reportable unauthorized release. CORRECTIVE ACTION: Notify and/or prepare a report to the CUPA upon discovery of a reportable unauthorized release. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030045 |  |  | Red Tag Tampering (USEPA Priority) | Red Tag has been removed, defaced, altered, or otherwise tampered with so that the information on the tag is not legible. | 23 CCR 16 2717.1(g) | 2011-07-01 | 2099-12-31 | 2012-04-24 12:56 | Existing | 79 | General Operating Requirements | Red Tag | Red Tag information is legible and has not been removed or tampered with | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Red Tag has been removed, defaced, altered, or otherwise tampered with so that the information on the tag is not legible. |  |  | OBSERVATION: Owner/operator failed to ensure that Red Tag was not tampered with. CORRECTIVE ACTION: Owner/operator shall ensure that Red Tag is not tampered with. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030044 |  |  | Red Tag Deposit (USEPA Priority) | Owner/operator deposited or allowed deposit of petroleum or a hazardous substance into a UST that has a red tag affixed to the fill pipe. | 23 CCR 16 2717.1(f), HSC 6.7 25292.3(c) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 80 | General Operating Requirements | Red Tag | Facility did not deposit/allow deposit of petroleum or a hazardous substance into a red tagged UST | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Owner/operator deposited or allowed deposit of petroleum or a hazardous substance into a UST that has a red tag affixed to the fill pipe. |  |  | OBSERVATION: Owner/Operator allowed petroleum or a hazardous substance to be deposited into a UST that has a red tag affixed to the fill pipe. CORRECTIVE ACTION: Owner/Operator shall not allow petroleum or hazardous substances to be deposited into a UST that has a red tag affixed to the fill pipe. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030079 |  |  | Red Tag Dispensing | Owner/operator allowed dispensing of petroleum or a hazardous substance from a UST that has a red tag affixed to the fill pipe. | HSC 6.7 25292.3(c)(1)(C) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 81 | General Operating Requirements | Red Tag | Facility did not dispense petroleum or a hazardous substance from a UST that has been red tagged | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Owner/operator allowed dispensing of petroleum or a hazardous substance from a UST that has a red tag affixed to the fill pipe. |  |  | OBSERVATION: Owner/Operator allowed petroleum or a hazardous substance to be dispensed from a UST that has a red tag affixed to the fill pipe. CORRECTIVE ACTION: Owner/Operator shall not allow petroleum or hazardous substances to be dispensed from a UST that has a red tag affixed to the fill pipe. |  |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030063 |  |  | Temporary Closure (USEPA Priority) | Failure to comply with temporary closure requirements. | 23 CCR 16 2670(b), (e), (f), 2671; HSC 6.7 25298 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 82 | General Operating Requirements | Tank Closure | Facility is in compliance with temporary closure requirements | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with temporary closure requirements. |  |  | OBSERVATION: Owner/Operator did not comply with temporary closure requirements. CORRECTIVE ACTION: Comply with Temporary Closure Requirements. Submit verification. | OBSERVATION: This UST system was found to be illegally abandoned. No person shall abandon an UST system without complying with the requirements of HSC 25298. [Name of tank owner], tank owner, states the UST system will be reused. CORRECTIVE ACTION: Immediately obtain a permit from the CUPA to temporarily close this UST system. A “Failure to Obtain a Permit” penalty applies. |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030038 |  |  | Permanent Closure (USEPA Priority) | Failure to comply with all permanent closure requirements. | 23 CCR 16 2670, 2672; HSC 6.7 25298(c) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 83 | General Operating Requirements | Tank Closure | UST system properly closed and complies with permanent closure requirements | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with all permanent closure requirements. |  |  | OBSERVATION: Owner/Operator did not properly close or comply with all permanent closure requirements. CORRECTIVE ACTION: Properly close or comply with all permanent closure requirements. Submit verification. | OBSERVATION: This UST system was found to be illegally abandoned. No person shall abandon an UST system without complying with the requirements of HSC 25298. CORRECTIVE ACTION: Immediately obtain a permit from the CUPA to remove this UST system. A “Failure to Obtain a Permit” penalty applies. |  |  |  | Yes | Yes | Yes
UST Program | Operations/Maintenance | 2030066 |  |  | Well Proximity Enhanced Leak Detection (ELD) Testing (USEPA Priority) | Failure to take appropriate action to repair and retest any leaking UST component which is discovered from an enhanced leak detection (ELD) test for UST systems located within 1,000 feet of a public drinking water well. | HSC 6.7 25292.4(d), 25292.5(c) | 2016-06-01 | 2099-12-31 | 2016-07-08 15:45 | Existing | 84 | General Operating Requirements | Install/Repair | Repaired/retested any leaks found when ELD testing a UST within 1,000 feet of a public water well | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to take appropriate action to repair and retest any leaking UST component which is discovered from an enhanced leak detection (ELD) test for UST systems located within 1,000 feet of a public drinking water well. |  |  | OBSERVATION: Owner/Operator failed to take appropriate action to repair and retest any leaking UST component which is discovered from an enhanced leak detection (ELD) test for UST systems located within 1,000 feet of a public drinking water well. CORRECTIVE ACTION: Repair and retest any leaking UST component discovered from an enhanced leak detection (UST systems located within 1,000 feet of a public drinking water well. Submit verification. | OBSERVATION: An enhanced leak detection test was performed on [date] which shows failures at the [UST component] and have not been repaired and [or] retested. If the results of the enhanced leak detection test indicate that any component of the UST system is leaking liquid or vapor, the owner or operator shall take appropriate actions to correct the leakage, and retest the system using enhanced leak detection until the system is no longer leaking liquid or vapor. CORRECTIVE ACTION: Immediately contact a properly licensed, trained, and certified contractor to make repairs to the UST system under permit and inspection of the CUPA. After repairs have been made, schedule an ELD retest and provide 48 hours notification to the CUPA. |  |  |  | Yes | Yes | Yes
UST Program | Design/Construction | 2060027 |  |  | UST Primary Containment (USEPA Priority) | Failure to construct, operate, and maintain primary containment as product-tight. | 23 CCR 16 2631(a); HSC 6.7 25290.1(c)(1), 25290.2(c)(1), 25291(a)(1) | 2016-06-01 | 2099-12-31 | 2016-05-13 14:36 | Existing | 85 | General Operating Requirements | Install/Repair | Tank system primary containment is constructed, operated, and maintained product-tight. | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | UST system primary containment is not constructed, operated, and maintained product-tight. |  |  | OBSERVATION: UST system primary containment is not constructed, operated, and maintained product-tight. CORRECTIVE ACTION: Construct, operate, and maintain UST primary containment system so that it is product tight. |  |  |  |  | Yes | Yes | Yes
UST Program | Design/Construction | 2060024 |  |  | UST Design/Construction - Compatibility (USEPA Priority) | UST system is not made of or lined with materials that are compatible with the substance stored in the UST system. | 23 CCR 16 2631.1, 2660(m); HSC 6.7 25290.1(c)(1), 25290.2(c)(1), 25291(a)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 86 | General Operating Requirements | Install/Repair | UST system is made of or lined with materials that are compatible with the substance stored. | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | UST system is not made of or lined with materials that are compatible with the substance stored in the UST system. |  |  | OBSERVATION: Tank number [tank #] was found to be storing [substance stored], which is not compatible with the UST system. Owners and operators must use an UST system made of or lined with materials that are compatible with the substance stored in the UST system. CORRECTIVE ACTION: Immediately remove the contents of this tank and have tank approved by Underwriters Laboratories (UL) prior to reuse. |  |  |  |  | Yes | Yes | Yes
UST Program | Design/Construction | 2060021 |  |  | Striker Plate | Failure to have either a striker plate installed or to have a drop tube-mounted bottom protector. | 23 CCR 16 2631(c), 2662(d) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 87 | General Operating Requirements | Install/Repair | Striker plate installed and positioned correctly. | 49 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to have either a striker plate installed or to have a drop tube-mounted bottom protector. |  |  | OBSERVATION: Owner/Operator failed to install a striker plate or to have a drop tube-mounted bottom protector. CORRECTIVE ACTION: Install a striker plate or drop tube-mounted bottom protector. Submit verification. |  |  |  |  | Yes | Yes | Yes
UST Program | Design/Construction | 2060007 |  |  | Independent Testing Organization Approval / Engineering Specification | Failure of primary or integral secondary containment to be approved for use by an independent testing organization or failure of non integral secondary containment to be designed and constructed to an engineering specification approved by a registered professional engineer or in accordance with a nationally recognized industry code or engineering standard. | 23 CCR 16 2631(b), 2631(d), 2666(b)(2), 2666(e)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 88 | General Operating Requirements | Install/Repair | Primary and secondary containment designed and constructed to an engineering specification. | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of primary and secondary containment to be designed and constructed to an engineering specification approved by a registered professional engineer or in accordance with a nationally recognized industry core or engineering standard. |  |  | OBSERVATION: Owner/Operator did not properly provide a design and/or construct the primary and/or secondary containment to an engineering specification approved by a registered professional engineer or in accordance with a nationally recognized industry core or engineering standard. CORRECTIVE ACTION: Owner/Operator shall provide a proper design and construct primary and secondary containment to an engineering specification approved by a registered professional engineer or in accordance with a nationally recognized industry core or engineering standard. Submit verification. |  |  |  |  | Yes | Yes | Yes
UST Program | Design/Construction | 2060008 |  |  | Enhanced Leak Detection Testing (ELD) (New Construction) | Failure to conduct enhanced leak detection (ELD) testing before the tank is placed into use. | HSC 6.7 25290.1(j) | 2016-06-01 | 2099-12-31 | 2016-06-20 08:33 | Existing | 89 | General Operating Requirements | Install/Repair | Enhanced leak detection testing performed before the tank is placed in use | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform enhanced leak detection testing before the tank is placed in use. |  |  | OBSERVATION: Owner/Operator did not perform enhanced leak detection testing before the tank is placed in use. CORRECTIVE ACTION: Perform enhanced leak detection testing before the tank is placed in use. Submit verification. | OBSERVATION: The UST system was not tested after installation to demonstrate it was product tight prior to use. A UST system shall be tested with one of the following methods prior to use: 1. Enhanced leak detection 2. Inert gas pressure test certified by a third party and approved by the SWRCB 3. Test method deemed to be equivalent one of the above. CORRECTIVE ACTION: Immediately schedule this test and provide 48 hours notification to the CUPA. Provide copies of the test results by [date, 30 days from now]. |  |  |  | Yes | Yes | No
UST Program | Design/Construction | 2060029 |  |  | Double-Walled Pipe Upgrade | Failure to upgrade single-walled pipe to double-walled continuous interstitially monitored pipe when replacement or repair is required. | 23 CCR 16 2666(b)(2) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 90 | General Operating Requirements | Install/Repair | SW piping has been upgraded to continuously monitored DW piping when replacement or repair needed | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to upgrade single-walled pipe to double-walled continuous interstitially monitored pipe when replacement or repair is required. |  |  | OBSERVATION: Owner/operator failed to upgrade single-walled pipe to double-walled continuous interstitially monitored pipe when replacement or repair is required. CORRECTIVE ACTION: Replace single-walled piping where replacement or repair is needed, with approved double-walled, continuously monitored piping. Submit application and workplan for approval prior to replacement of piping. |  |  |  |  | Yes | Yes | Yes
UST Program | Administration/Documentation | 2010 |  |  | UST-Administration/Documentation - General | UST Program - General - Must include violation description, proper statute and regulation citation in the "comment" section. | 23 CCR Chapter 16 Multiple Sections; HSC Chapter 6.7 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 91 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [7 empty] | Yes | Yes | Yes
UST Program | Administration/Documentation | 2015 |  |  | UST-Administration/Documentation - General Local Ordinance | UST Program - Administration/Documentation - General Local Ordinance - Must include violation description and proper ordinance citation in the "comment" section. |  | 2016-06-01 | 2099-12-31 | 2016-05-13 14:29 | Existing | 92 | General Facility Requirements |  | Administrative/Documentation - General Local Ordinance | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General Local Ordinance | [7 empty] | Yes | Yes | Yes
Note on N1: With the Checklist Item Order column in mind, this text represents text that will group one or more sub-headings and violations. If no Inspection Checklist Heading, the checklist items will not be grouped. Example: Leak Detection 100 Characters Max
Note on O1: With the Checklist Item Order field in mind and as a sub-item to Checklist Heading, this text represents text that will group one or more violations. If no Checklist Sub-Heading, the checklist items will fall under the Checklist Heading. Example: “Single Wall” 100 Characters Max
Note on P1: This is what appears on the checklist for the inspector. It should be descriptive and relatively short. May be the same as Name if sufficiently descriptive. Note: Decade recommends expressing the checklist item “in the positive.” For example, “Facility performs enhanced leak detection testing before the tank is placed in use” (positive) vs. “Failure to perform enhanced leak detection testing before the tank is placed in use” (negative). 100 Characters Max
Note on Q1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on R1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on S1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on T1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on U1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Note: Every checklist item should have at least one of the following visible: IN, OUT, NA, NO. Example: Y or N
Note on V1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Example: Y or N
Note on W1: Not every checkbox must be displayed for every checklist item. Tell us whether this checkbox should appear for this item by entering Y or N. Example: Y or N
Note on X1: For this checklist item, display the option to set/override the Degree of Violation (e.g., Class 1, Class2, Minor) Example: Y or N
Note on Y1: Is this violation typically recorded as a Class 1, Class 2, or Minor Violation. Blank (no default) is also a valid option. Example: Y or N
Note on Z1: If marked Y, then the inspection cannot be completed without selecting IN, OUT, NA, or NO. Otherwise, mark this item N. Example: Y or N
Note on AA1: Indicate the number of points that should be added/deducted when this item is marked OUT of compliance. Example: 5
Note on AB1: Indicate the number of days following the first Notice of Violation on which the regulator expects compliance. Example: 30
Note on AC1: This static text may appear on a printed inspection report when inspections are conducted electronically. May use “Description” column from the Unified Program Violation Library.
Note on AD1: For Summary Reporting, this field shall specify if the cited violation relates to Release Detection. Example: Y or N
Note on AE1: This static text may appear on a printed inspection report when inspections are conducted electronically.
Note on AF1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AG1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AH1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AI1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AJ1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AK1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AL1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.
Note on AM1: This text may be reviewed/selected/edited by the inspector in order to add additional information to the checklist item. If selected, comments of this type are almost always part of the printed inspection report.

## APSA
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | AST Conditionally Exempt | AST Non_Qualified | AST Tier I | AST Tier II
APSA Program | Administration/Documentation | 4010001 |  |  | SPCC Plan prepared | Failure to prepare a Spill Prevention, Control, and Countermeasure (SPCC) Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3, 112.6 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 1 | Requirement to Prepare and Implement |  | SPCC has been prepared | 22 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a Spill Prevention Control and Countermeasure (SPCC) Plan. |  |  | OBSERVATION: Failure to prepare SPCC. CORRECTIVE ACTION: Prepare SPCC. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010057 |  |  | SPCC Plan complete | Failure to prepare an SPCC Plan that meets all applicable requirements. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3, 112.6 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 2 | Requirement to Prepare and Implement |  | SPCC plan has been prepared that meets all applicable requirements | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an SPCC Plan that meets all applicable requirements. |  |  | OBSERVATION: Failure to prepare an SPCC Plan that meets all applicable requirements. CORRECTIVE ACTION: Complete or revise SPCC plan that meets all applicable requirements. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030038 |  |  | Implementation of SPCC Plan | Failure to implement the SPCC Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 3 | Requirement to Prepare and Implement |  | SPCC has been implemented | 26 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to implement a Spill Prevention Control and Countermeasure (SPCC) Plan. |  |  | OBSERVATION: Failure to implement SPCC. CORRECTIVE ACTION: Implement SPCC. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010008 |  |  | SPCC Plan available onsite | Failure to maintain a complete copy of the SPCC Plan at the facility if the facility is normally attended at least four hours per day, or at the nearest field office if the facility is not so attended. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3(e)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 4 | Requirement to Prepare and Implement |  | SPCC onsite If facility staffed 4 hrs/day, or at the nearest field office if not so attended | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to maintain SPCC plan onsite if facility is manned at least four (4) hours per day, or at the nearest field office if the facility is not so attended. |  |  | OBSERVATION: Failure to maintain SPCC plan onsite if facility is manned at least four (4) hours per day, or at the nearest field office if the facility is not so attended. CORRECTIVE ACTION: Maintain SPCC plan onsite If facility staffed 4 hrs/day, or at the nearest field office if the facility is not so attended. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010003 |  |  | Professional engineer certification | Failure to have a licensed professional engineer properly review and certify the SPCC Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3(d) | 2016-06-01 | 2099-12-31 | 2017-06-01 | Existing | 5 | Requirement to Prepare and Implement |  | Professional engineer has properly reviewed and certified the SPCC Plan | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have a licensed professional engineer properly review and certify the SPCC Plan. |  |  | OBSERVATION: PE failed to properly review and/or certify the SPCC Plan for one or more of the requirements. CORRECTIVE ACTION: Submit SPCC that has been properly reviewed and certified by a PE. | [6 empty] | No | Yes | No | No
APSA Program | Administration/Documentation | 4010045 |  |  | Professional engineer attestations | Failure of the owner or operator to ensure a professional engineer makes all required attestations in the SPCC Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.3(d)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 6 | Requirement to Prepare and Implement |  | A professional engineer made all required attestations in the SPCC Plan | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator to ensure a professional engineer makes all required attestations in the SPCC Plan. |  |  | OBSERVATION: Failure of to ensure a professional engineer makes all required attestations in the SPCC Plan as listed in 40 CFR 112.3(d)(1): [specify missing attestations]. CORRECTIVE ACTION: Amend the SPCC plan to ensure that the professional engineer's certification contains all the required attestations. | [6 empty] | No | Yes | No | No
APSA Program | Administration/Documentation | 4010047 |  |  | Qualified Facility - Certification of SPCC Plan | Failure to have management or a professional engineer certify the SPCC Plan and comply with certification requirements at a qualified facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(1), 112.6(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 7 | Requirement to Prepare and Implement |  | Qualified Facility's SPCC plan has been self or PE certified. | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to have management or a professional engineer certify the SPCC Plan and comply with certification requirements at a qualified facility. |  |  | OBSERATION: SPCC Plan has not been properly certified by management or professional engineer. CORRECTIVE ACTION: Facility must certify or have professional engineer certify the SPCC Plan. | [6 empty] | No | No | Yes | Yes
APSA Program | Administration/Documentation | 4010035 |  |  | Appropriate SPCC Plan | Failure to prepare an appropriate SPCC Plan within 6 months when the facility no longer meets the Tier I or Tier II qualified facility criteria. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(2), 112.6(b)(2) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Existing | 8 | Requirement to Prepare and Implement |  | Facility prepared appropriate SPCC when no longer meeting Tier I/II requirements | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an appropriate SPCC Plan within 6 months when the facility no longer meets the Tier I or Tier II qualified facility criteria. |  |  | OBSERVATION: Failure to prepare appropriate SPCC plan when no longer meeting the conditions of a Tier I or Tier II Qualified Facility: CORRECTIVE ACTION: Maintain compliance with Tier I or II qualified facility requirements or prepare and implement a SPCC plan for a Tier II or Non-Qualified Facility as is applicable. | [6 empty] | No | No | Yes | Yes
APSA Program | Administration/Documentation | 4010010 |  |  | SPCC Plan amended | Failure to amend the SPCC Plan within 6 months: 1. When the facility has had a change in design, construction, operation, or maintenance which affects the facility’s discharge potential. AND/OR 2. To include more effective proven technology at the time of the 5-year SPCC Plan review and evaluation. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.5(a), 112.5(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 9 | SPCC Amendments |  | Facility has amended SPCC as necessary | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to amend the SPCC Plan within 6 months: 1. When the facility has had a change in design, construction, operation, or maintenance which affects the facility’s discharge potential. AND/OR 2. To include more effective proven technology at the time of the 5-year SPCC Plan review and evaluation. |  |  | OBSERVATION: 1. Failure to amend SPCC plan within 6 months of when the facility has had a change in: design, construction, operation, or maintenance which affects the facility’s discharge potential. 2. Failure to amend SPCC plan within 6 months to include more effective proven technology at the time of the 5-year SPCC Plan review and evaluation. CORRECTIVE ACTION: Amend SPCC as required. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030039 |  |  | Implementation of SPCC Plan amendments | Failure to implement SPCC Plan amendments within 6 months. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.5(a), 112.5(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 10 | SPCC Amendments |  | SPCC has been implemented within 6 months of amendment | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to implement a Spill Prevention Control and Countermeasure (SPCC) Plan within 6 months of amendment . |  |  | OBSERVATION: Failure to implement SPCC within 6 months of amendment. CORRECTIVE ACTION: Implement amended SPCC. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010039 |  |  | Certification of technical amendments | Failure to have technical amendment(s) certified by a licensed professional engineer. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.5(c) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 11 | SPCC Amendments |  | Technical amendment(s) were certified by a licensed professional engineer | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have technical amendment(s) certified by a licensed professional engineer. |  |  | OBSERVATION: Failure to have Technical Amendment(s) that materially affect the potential for a discharge [list here] certified by a professional engineer. CORRECTIVE ACTION: All Technical Amendments listed above must be reviewed, modified as necessary and certified by a professional engineer. | [6 empty] | No | Yes | No | No
APSA Program | Administration/Documentation | 4010048 |  |  | Tier I - Certification of technical amendments | Failure of a Tier I qualified facility to certify the SPCC Plan according to 40 CFR 112.6(a)(1) if a technical change has been made to the facility design, construction, operation, or maintenance. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 12 | SPCC Amendments |  | Tier I Qualified Facility has certified tech amendments. | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a Tier I qualified facility to certify the SPCC Plan according to 40 CFR 112.6(a)(1) if a technical change has been made to the facility design, construction, operation, or maintenance. |  |  | OBSERVATION: Owner/Operator failed to certify technical amendments to the SPCC Plan when there has been a change in facility design, construction, operation or maintenance that may affect its potential for a discharge. CORRECTIVE ACTION: Certify technical amendments to the SPCC when there has been a change in facility design, construction, operation or maintenance that may affect its potential for a discharge. | [6 empty] | No | No | Yes | No
APSA Program | Administration/Documentation | 4010052 |  |  | Tier II – Certification of technical amendments | Failure to have technical amendment(s) certified by the owner or operator or a professional engineer for a Tier II qualified facility when required. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(b)(2); 112.6(b)(2)(i) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 13 | SPCC Amendments |  | Tech amendments certified when a change in facility design/operations occurs, & by PE when required | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to have technical amendment(s) certified by the owner or operator or a professional engineer for a Tier II qualified facility when required. |  |  | OBSERVATION: Technical amendments to the SPCC Plan have not been certified by owner/operator or professional engineer, when required, when there has been a change in facility design, construction, operation or maintenance that may affect its potential for a discharge. CORRECTIVE ACTION: Have technical amendments properly certified in SPCC Plan. | [6 empty] | No | No | No | Yes
APSA Program | Administration/Documentation | 4010009 |  |  | Five-year SPCC Plan review and documentation of the review | Failure to complete a review and evaluation of the SPCC Plan at least once every five years, document the completion of the review, and sign a statement as to whether the SPCC Plan will be amended. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.5(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 14 | Five Year Review |  | 5 year review performed on SPCC and documented | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to complete a review and evaluation of the SPCC Plan at least once every five years, document the completion of the review, and sign a statement as to whether the SPCC Plan will be amended. |  |  | OBSERVATION: Failure to perform and/or document the five-year review of the SPCC plan. CORRECTIVE ACTION: Complete and document the 5 year review of SPCC Plan and submit verification of proper completion. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010012 |  |  | SPCC Plan basic requirements | Failure to prepare an SPCC Plan which fulfills all basic requirements that include: 1. The SPCC Plan must be prepared in accordance with good engineering practices. 2. Have full approval of management at a level of authority to commit the necessary resources to fully implement the SPCC Plan. 3. Prepare the SPCC Plan in writing. 4. Follow the sequence of the SPCC rule or include a cross-reference. 5. If the SPCC Plan calls for additional procedures, methods, or equipment not yet fully operational, discuss the items in separate paragraphs. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 15 | General SPCC Requirements |  | SPCC in writing, follows code seq/cross ref, good eng practice, mgt approval, items not in place | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an SPCC Plan which fulfills all basic requirements that include: 1. The SPCC Plan must be prepared in accordance with good engineering practices. 2. Have full approval of management at a level of authority to commit the necessary resources to fully implement the SPCC Plan. 3. Prepare the SPCC Plan in writing. 4. Follow the sequence of the SPCC rule or include a cross-reference. 5. If the SPCC Plan calls for additional procedures, methods, or equipment not yet fully operational, discuss the items in separate paragraphs. |  |  | OBSERVATION: Failure to prepare SPCC Plan that meets the following requirements: 1. Follows the sequence of SPCC rule and/or includes cross-reference. 2. Prepared in accordance with good engineering practices. 3. Has the full approval of management at a level of authority to commit the necessary resources to fully implement the SPCC plan. 4. Plan is in writing. 5. Plan addresses additional procedures/methods/equipment not yet fully operational. CORRECTIVE ACTION: Prepare a SPCC plan that: 1. Follows a sequence of rule and/or includes a cross-reference. 2. Is prepared in accordance with good engineering practices. 3. Has full approval of management at a level of authority to commit the necessary resources to fully implement the SPCC plan. 4. Is in writing. 5. Addresses additional procedures/methods/equipment not yet fully operational. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010013 |  |  | SPCC Plan discussion of conformance with requirements | Failure to include in the SPCC Plan an adequate discussion of the facility's conformance with the requirements of 40 CFR Part 112, other effective discharge prevention and containment procedures listed in Part 112, or any applicable more stringent State rules, regulations, and guidelines. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(j) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 16 | General SPCC Requirements |  | SPCC Plan discusses conformance with all SPCC rule requirements, & state rules/regs/guidelines. | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to discuss in the SPCC Plan conformance with SPCC requirements and other effective discharge prevention and containment procedures, or any applicable more stringent State rules, regulations, and guidelines. |  |  | OBSERVATION: Failure of SPCC Plan to adequately discuss conformance with all SPCC rule requirements, other effective discharge prevention and containment procedures, or any applicable more stringent State rules, regulations, and guidelines. CORRECTIVE ACTION: Revise SPCC Plan to include an adequate discussion of conformance with all SPCC rule requirements, other effective discharge prevention and containment procedures, or any applicable more stringent State rules, regulations, and guidelines. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010014 |  |  | Equivalent environmental protection | Failure to state reasons for nonconformance and describe equivalent methods in detail if claiming equivalent environmental protection for SPCC requirements other than secondary containment. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(2) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 17 | General SPCC Requirements | Environmental Equivalence | Environmental Equivalence, if claimed, is addressed in SPCC, other than for secondary containment. | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to state reasons for nonconformance in SPCC Plan and describe in detail alternate methods used to achieve environmentally equivalent protection when claiming environmental equivalence for SPCC requirements other than secondary containment. |  |  | OBSERVATION: Failure to state reasons for nonconformance in SPCC Plan and describe in detail alternate methods used to achieve environmentally equivalent protection when claiming environmental equivalence for SPCC requirements other than secondary containment. CORRECTIVE: ACTION: In SPCC Plan discuss reasons for nonconformance and describe alternate methods used to achieve environmentally equivalent protection. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010050 |  |  | Tier II - Certification of alternative measures by professional engineer | Failure to have a professional engineer review and certify in writing one or more of the following alternative measures for a Tier II qualified facility: 1. Alternative method which achieves equivalent environmental protection pursuant to 40 CFR 112.7(a)(2). 2. Impracticability determination and measures in lieu of secondary containment pursuant to 40 CFR 112.7(d). 3. Measures pursuant to 40 CFR 112.9(c)(6) for produced water containers and any associated piping and appurtenances downstream from the container. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(b)(3); 112.6(b)(4)(iii) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 18 | General SPCC Requirements | Tier II Alternative Measures | PE certified enviro equivalence, impracticability, and produced water containers/piping, if needed | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have a professional engineer review and certify in writing one or more of the following alternative measures for a Tier II qualified facility: 1. Alternative method which achieves equivalent environmental protection pursuant to 40 CFR 112.7(a)(2). 2. Impracticability determination and measures in lieu of secondary containment pursuant to 40 CFR 112.7(d). 3. Measures pursuant to 40 CFR 112.9(c)(6) for produced water containers and any associated piping and appurtenances downstream from the container. |  |  | OBSERVATION: PE did not review and certify one or more of the following: 1. Alternative environmental equivalence methods 2. Impracticability for secondary containment 3. Produced water containers and associated piping as described in 112.9(c)(6). CORRECTIVE ACTION: Obtain a PE review and certification for one or more of the following: 1. Alternative environmental equivalence methods 2. Impracticability for secondary containment 3. Produced water containers and associated piping as described in 112.9(c)(6). | [6 empty] | No | No | No | Yes
APSA Program | Administration/Documentation | 4010051 |  |  | Tier II – Professional engineer attestations | Failure of the owner or operator to ensure a professional engineer makes all required attestations in the SPCC Plan when a professional engineer certification is necessary due to an alternative measure claim at a Tier II qualified facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(b)(4)(i) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 19 | General SPCC Requirements | Tier II Alternative Measures | PE required attestations in the SPCC Plan for alternative measure claim at a Tier II facility | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator to ensure a professional engineer makes all required attestations in the SPCC Plan when a professional engineer certification is necessary due to an alternative measure claim at a Tier II qualified facility. |  |  | OBSERVATION: PE did not attest to one or more of the following: 1. PE did not attest that they are familiar with the requirements of 112.6(b). 2. SPCC does not include that the PE or agent has visited the facility. 3. SPCC does not include that the PE attests that the alternate environmental equivalence or the determination of impracticability and alternative measures in accordance with § 112.7(d) is consistent with good engineering practice. CORRECTIVE ACTION: Obtain PE certification for one or more of the following: 1. Obtain PE certification that they are familiar with the requirements of 112.6(b). 2. Obtain PE or agent certification that they have visited the facility. 3.Have PE attest that the alternate environmental equivalence or the determination of impracticability and alternative measures in accordance with § 112.7(d) is consistent with good engineering practice | [6 empty] | No | No | No | Yes
APSA Program | Administration/Documentation | 4010016 |  |  | Facility Description | Failure to adequately and accurately describe in the SPCC Plan the physical layout of the facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 20 | General SPCC Requirements | Facility Description/Storage/Diagram | Physical layout of the facility is adequately and accurately described in SPCC | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately and accurately describe in the SPCC Plan the physical layout of the facility. |  |  | OBSERVATION: Failure to adequately and accurately describe the physical layout of the facility, or no description of the physical layout of the facility included in the SPCC plan. CORRECTIVE ACTION: Update SPCC plan to adequately and accurately describe the physical layout of facility. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010041 |  |  | Oil type and storage capacity of storage containers | Failure to address in the SPCC Plan the type of oil and storage capacity for each fixed container. For mobile or portable containers, either provide the type of oil and storage capacity, or an estimate of the potential number of mobile or portable containers, the types of oil, and anticipated storage capacities. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3)(i) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Existing | 21 | General SPCC Requirements | Facility Description/Storage/Diagram | SPCC Plan addresses the type of oil and storage capacity for all fixed and portable containers | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to address in the SPCC Plan the type of oil and storage capacity for each fixed container. For mobile or portable containers, either provide the type of oil and storage capacity, or an estimate of the potential number of mobile or portable containers, the types of oil, and anticipated storage capacities. |  |  | OBSERVATION: Failure to address in the SPCC Plan the type of oil and storage capacity for each fixed container, or, for portable and/or mobile containers, either provide the type of oil and storage capacity, or an estimate of the potential number of portable or mobile containers, the types of oil, and anticipated storage capacities. CORRECTIVE ACTION: Amend the SPCC Plan to properly address the type and storage capacity of all fixed and portable and/or mobile containers as required. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010015 |  |  | Facility Diagram | Failure to include in the SPCC Plan an adequate facility diagram, or no facility diagram included. The facility diagram is not required on a Tier I qualified facility SPCC Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 22 | General SPCC Requirements | Facility Description/Storage/Diagram | SPCC contains an adequate facility diagram | 42 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to have an adequate facility diagram, or no facility diagram included within the SPCC plan. |  |  | OBSERVATION: Failure to have an adequate facility diagram, or no facility diagram included within the SPCC plan. CORRECTIVE ACTION: Include an adequate facility diagram in the SPCC | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010030 |  |  | Discharge prevention measures | Failure to address in the SPCC Plan discharge prevention measures, including procedures for routine handling of products such as loading/unloading and facility transfers. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3)(ii) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 23 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC adequately addresses discharge prevention measures for routine handling, loading/unloading | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to address in the SPCC Plan discharge prevention measures, including procedures for routine handling of products such as loading/unloading and facility transfers. |  |  | OBSERVATION: Failure to address discharge prevention measures, including procedures for routine handling of products such as loading/unloading and facility transfers within the SPCC plan. CORRECTIVE ACTION: Revise SPCC plan to adequately discuss discharge prevention measures, including procedures for routine handling of products such as loading/unloading and facility transfers. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010042 |  |  | Countermeasures for discharge discovery, response, and cleanup | Failure to address in the SPCC Plan countermeasures for discharge discovery, response, and cleanup (both facility’s and contractor’s resources). | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3)(iv) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 24 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC Plan addressed countermeasures for discharge discovery, response and cleanup | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to address in the SPCC Plan countermeasures for discharge discovery, response, and cleanup (both facility’s and contractor’s resources). |  |  | OBSERVATION: Failure to address in the SPCC Plan countermeasures for discharge discovery, response, and cleanup. CORRECTIVE ACTION: Amend the SPCC Plan to fully address the countermeasures the facility will conduct to discover, respond and cleanup any discharge. This should include both the facility's and contractor's prescribed actions and resources. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010043 |  |  | Disposal methods | Failure to address in the SPCC Plan disposal methods for recovered materials. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3)(v) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 25 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC Plan addresses disposal methods for recovered materials | 60 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to address in the SPCC Plan disposal methods for recovered materials. |  |  | OBSERVATION: Failure to address in the SPCC Plan disposal methods for recovered materials. CORRECTIVE ACTION: Amend the SPCC Plan to address the disposal methods for recovered materials. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010017 |  |  | Discharge reporting procedures | Failure to include in the SPCC Plan: 1. A contact list and phone numbers for the facility response coordinator, National Response Center, cleanup contractors with an agreement for response, and all Federal, State, and local agencies who must be contacted in case of a discharge. 2. Information and procedures that would enable a person reporting an oil discharge to relate all information as described in 40 CFR 112.7(a)(4), unless facility submitted a Facility Response Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(3)(vi); 112.7(a)(4) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 26 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC contains procedures for reporting a discharge | 50 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include in the SPCC Plan: 1. A contact list and phone numbers for the facility response coordinator, National Response Center, cleanup contractors with an agreement for response, and all Federal, State, and local agencies who must be contacted in case of a discharge 2. Information and procedures that would enable a person reporting an oil discharge to relate all information as described in 40 CFR 112.7(a)(4), unless facility submitted a Facility Response Plan. |  |  | OBSERVATION: Failure to adequately discuss procedures for reporting a discharge, or no information and procedures for reporting a discharge are included within the SPCC plan. CORRECTIVE ACTION: Include procedures for reporting a discharge in the SPCC. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010018 |  |  | Discharge response procedures | Failure to organize the SPCC Plan so that portions describing procedures to be used when a discharge occurs will be readily usable in an emergency and include appropriate supporting material as appendices, unless facility submitted a Facility Response Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(5) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 27 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC organized so discharge procedures are readily usable if the facility has no response plan | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to organize the SPCC Plan so that portions describing procedures to be used when a discharge occurs will be readily usable in an emergency and include appropriate supporting material as appendices, unless facility submitted a Facility Response Plan. |  |  | OBSERVATION: Failure to organize the SPCC Plan so that portions describing procedures to be used when a discharge occurs will be readily usable in an emergency, unless facility submitted a Facility Response Plan. CORRECTIVE ACTION: Update SPCC Plan so that portions describing procedures to be used when a discharge occurs will be readily usable in an emergency. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010019 |  |  | Discharge predictions | Failure to include in the SPCC Plan a prediction of the direction, rate of flow, and total quantity of oil that could be discharged for each type of major equipment failure where experience indicates a reasonable potential for equipment failure. The rate of flow is not required on a Tier I qualified facility SPCC Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 28 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC predicts direction, rate of flow, total quantity of oil that could be released from a discharge | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include in the SPCC Plan a prediction of the direction, rate of flow, and total quantity of oil that could be discharged for each type of major equipment failure where experience indicates a reasonable potential for equipment failure. The rate of flow is not required on a Tier I qualified facility SPCC Plan. |  |  | OBSERVATION: Failure to predict the direction, rate of flow, and total quantity of oil that could be discharged for each type of major equipment failure in the SPCC plan. CORRECTIVE ACTION: Update SPCC plan to include prediction of the direction, rate of flow, and total quantity of oil that could be discharged for each type of major equipment failure. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010054 |  |  | Tier I - Failure analysis-direction and amount of flow | Failure to include in the SPCC Plan a prediction of direction and total quantity of oil potentially discharged from the facility as a result of each type of major equipment failure. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(3)(i) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 29 | General SPCC Requirements | Discharge Reporting/Response/Disposal/Prediction | SPCC contains a prediction of direction and total quantity of oil potentially discharged | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include in the SPCC Plan a prediction of direction and total quantity of oil potentially discharged from the facility as a result of each type of major equipment failure. |  |  | OBSERVATION: Failure to include in the SPCC Plan a prediction of direction and total quantity of oil potentially discharged from the facility as a result of each type of major equipment failure. CORRECTIVE ACTION: Update SPCC plan to include a prediction of direction and total quantity of oil potentially discharged from the facility as a result of each type of major equipment failure. | [6 empty] | No | No | Yes | No
APSA Program | Administration/Documentation | 4010020 |  |  | General Containment Description | Failure to discuss in the SPCC Plan the appropriate general containment, diversionary structures, or equipment to prevent a discharge, including typical failure mode and most likely quantity of discharge for the following: 1. Bulk storage containers, 2. Mobile/portable containers, 3. Oil-filled equipment, 4. Piping and related appurtenances, 5. Mobile refuelers or non-transportation-related tank cars, and 6. Transfer areas, equipment and activities. This does not apply to facilities with oil filled operational equipment implementing 112.7(k). | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(c) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 30 | General SPCC Requirements | Containment | SPCC addresses the appropriate general containment/diversionary structures/equipment | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to discuss in the SPCC Plan the appropriate general containment, diversionary structures, or equipment to prevent a discharge, including typical failure mode and most likely quantity of discharge for the following: 1. Bulk storage containers, 2. Mobile/portable containers, 3. Oil-filled equipment, 4. Piping and related appurtenances, 5. Mobile refuelers or non-transportation-related tank cars, and 6. Transfer areas, equipment and activities. This does not apply to facilities with oil filled operational equipment implementing 112.7(k). |  |  | OBSERVATION: Failure to discuss the appropriate general containment, diversionary structures, or equipment to prevent a discharge, including typical failure mode and most likely quantity of discharge within the SPCC plan. CORRECTIVE ACTION: Update SPCC plan to address the general containment, diversionary structures, and equipment in use at facility to prevent a discharge, including typical failure mode and most likely quantity of potential discharge. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030037 |  |  | General containment | Failure to provide appropriate secondary containment and/or diversionary structures or equipment for the following: 1. Bulk storage containers, 2. Mobile or portable containers, 3. Oil-filled equipment, 4. Piping and related appurtenances, 5. Mobile refuelers or non-transportation-related tank cars, and 6. Transfer areas, equipment and activities and ensure that the entire containment system, including walls and floor, are capable of containing oil and constructed so that any discharge will not escape the containment system before cleanup occurs. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(c) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 31 | General SPCC Requirements | Containment | Appropriate (general) containment/diversionary structures/equipment have been provided | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide appropriate secondary containment and/or diversionary structures or equipment for the following: 1. Bulk storage containers, 2. Mobile or portable containers, 3. Oil-filled equipment, 4. Piping and related appurtenances, 5. Mobile refuelers or non-transportation-related tank cars, and 6. Transfer areas, equipment and activities and ensure that the entire containment system, including walls and floor, are capable of containing oil and constructed so that any discharge will not escape the containment system before cleanup occurs. |  |  | OBSERVATION: Failure to provide the appropriate general containment/diversionary structures/equipment for the following: bulk storage containers, mobile or portable containers, oil-filled equipment, piping and related appurtenances, mobile refuelers or non-transportation-related tank cars, and transfer areas. CORRECTIVE ACTION: Provide appropriate general containment measures and/or diversionary structures/equipment capable of containing oil and constructed so that any discharge will not escape the containment system before cleanup occurs. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010004 |  |  | Impracticability claims of appropriate containment explained and certified | Failure to clearly explain why appropriate containment/diversionary structures are not practicable and/or SPCC Plan claiming impracticability is not certified by a licensed professional engineer. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(d) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 32 | General SPCC Requirements | Impracticability | Impracticability of containment/diversionary items, if claimed, is PE demonstrated and certified | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to clearly explain why appropriate containment/diversionary structures are not practicable and/or SPCC Plan claiming impracticability is not certified by a licensed professional engineer. Note: impracticability determinations must be certified by a PE for Tier II plans. |  |  | OBSERVATION: Failure to clearly explain why appropriate containment/diversionary structures are not practicable and/or SPCC Plan claiming impracticability is not certified by a licensed professional engineer. CORRECTIVE ACTION: SPCC Plan must clearly explain why appropriate containment/diversionary structures are not practicable and PE shall certify all claims of impracticability. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030033 |  |  | Secondary Containment Impracticability – Testing | Failure to perform required periodic integrity and leak testing when claiming secondary containment impracticability. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(d) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 33 | General SPCC Requirements | Impracticability | Periodic integrity/leak testing performed with impracticability claim | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform required periodic integrity and leak testing when claiming secondary containment impracticability. |  |  | OBSERVATION: Failure to perform periodic integrity and leak testing when claiming secondary containment impracticability. CORRECTIVE ACTION: Perform periodic integrity and leak testing of items in areas where making secondary containment impracticability claim. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010005 |  |  | Oil spill contingency plan prepared when claiming impracticability | Failure to prepare an oil spill contingency plan when claiming impracticability of appropriate containment/diversionary structures. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(d)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 34 | General SPCC Requirements | Impracticability | If claiming impracticability of containment/diversionary items a contingency plan has been included | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an oil spill contingency plan when claiming impracticability of appropriate containment/diversionary structures. Note: impracticability determinations must be certified by a PE for Tier II plans. |  |  | OBSERVATION: Failure to prepare an oil spill contingency plan when claiming impracticability of appropriate containment/diversionary structures. CORRECTIVE ACTION: If claiming impracticability of containment/diversionary items, include a contingency plan. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010006 |  |  | Written commitment of manpower, equipment, materials when claiming impracticability | Failure to provide a written commitment of manpower, equipment, and materials required to expeditiously control and remove any discharge that may be harmful when claiming impracticability of appropriate containment/diversionary structures. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(d)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 35 | General SPCC Requirements | Impracticability | If claiming impracticability written commitment of manpower, equipment, and materials provided | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide a written commitment of manpower, equipment, and materials required to expeditiously control and remove any discharge that may be harmful when claiming impracticability of appropriate containment/diversionary structures. |  |  | OBSERVATION: Failure to provide a written commitment of manpower, equipment, and materials required to expeditiously control and remove any discharge that may be harmful when claiming impracticability of appropriate containment/diversionary structures. CORRECTIVE ACTION: If claiming impracticability of containment/diversionary structures provide a written commitment of manpower, equipment, and materials. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010023 |  |  | Employee Training and Spill Prevention Briefings Description | Failure to include in the SPCC plan an adequate description of employee training. Training shall address, at a minimum: 1. Operation and maintenance of equipment to prevent discharges; 2. Discharge procedure protocols; 3. Applicable pollution control laws, rules, and regulations; 4. General facility operations; 5. Content of the facility SPCC plan; and 6. Annual discharge prevention briefings for oil-handling personnel to assure adequate understanding of the SPCC plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(f)(1), 112.7(f)(3) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 36 | General SPCC Requirements | Training | Employee training and spill prevention briefings discussed in SPCC plan | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include in the SPCC plan an adequate description of employee training. Training shall address, at a minimum: 1. Operation and maintenance of equipment to prevent discharges; 2. Discharge procedure protocols; 3. Applicable pollution control laws, rules, and regulations; 4. General facility operations; 5. Content of the facility SPCC plan; and 6. Annual discharge prevention briefings for oil-handling personnel to assure adequate understanding of the SPCC plan. |  |  | OBSERVATION: Failure to include in SPCC plan a discussion, or adequate description of all required employee training including annual spill prevention briefings provided to oil-handling personnel. CORRECTIVE ACTION: Revise SPCC plan to adequately describe employee training, addressing all training requirements including spill prevention briefings provided to oil-handling personnel at least once per year. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Training | 4020001 |  |  | Employee training requirements | Failure to provide the following training to all oil-handling personnel: 1. Operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. 5. Contents of the SPCC Plan. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(f)(1) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 37 | General SPCC Requirements | Training | Training provided for op/maint of equip, discharge procedures, laws/regs, general fac ops, and SPCC | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide the following training to all oil-handling personnel: 1. Operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. 5. Contents of the SPCC Plan. |  |  | OBSERVATION: Failure to provide training to all oil-handling personnel regarding one or more of the following: 1. The operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. AND 5. The contents of the SPCC Plan. CORRECTIVE ACTION: Provide training in: 1. The operation and maintenance of equipment to prevent discharges. 2. Discharge procedure protocols. 3. Applicable pollution control laws, rules, and regulations. 4. General facility operations. AND 5. The contents of the SPCC Plan. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010022 |  |  | Designated Person | Failure to designate person who reports to management as accountable for discharge prevention at facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(f)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 38 | General SPCC Requirements | Training | Person has been designated as accountable for discharge prevention and reports to management | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to designate a person accountable for discharge prevention and who reports to facility management. |  |  | OBSERVATION: Failure to designate a person accountable for discharge prevention and who reports to facility management. CORRECTIVE ACTION: Designate a person accountable for discharge prevention and who reports to facility management. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Training | 4020002 |  |  | Spill prevention briefings | Failure to conduct spill prevention briefing for oil-handling personnel at least once a year to assure adequate understanding of the SPCC Plan, including: 1. Known discharges or failures. 2. Malfunctioning components. 3. Any recently developed precautionary measures. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(f)(3) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 39 | General SPCC Requirements | Training | Spill prevention briefings are conducted annually | 49 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to conduct spill prevention briefing for oil-handling personnel at least once a year to assure adequate understanding of the SPCC Plan, including: 1. Known discharges or failures. 2. Malfunctioning components. 3. Any recently developed precautionary measures. |  |  | OBSERVATION: Failure to conduct spill prevention briefings at least once a year, or failure to highlight or describe one or more of the following: Known discharges or failures; Malfunctioning components; Recently developed precautionary measures. CORRECTIVE ACTION: Conduct spill prevention briefings annually. Provide compliance verification. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010024 |  |  | Facility security description | Failure to describe in the SPCC Plan facility security measures including: 1. How access to the oil handling, processing, and storage areas is secured and controlled. 2. How master flow and drain valves are secured. 3. How unauthorized access to starter controls on oil pumps is prevented. 4. How out-of-service and loading/unloading connections of oil pipelines is secured. 5. The appropriateness of security lighting to both prevent acts of vandalism and assist in the discovery of oil discharges. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(g) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 40 | General SPCC Requirements | Security | SPCC addresses security measures-lighting, access to handling/storage, valves/pumps/transfer equip | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to describe in the SPCC plan facility security measures including: 1. How access to the oil handling, processing, and storage areas is secured and controlled. 2. How master flow and drain valves are secured. 3. How unauthorized access to starter controls on oil pumps is prevented. 4. How out-of-service and loading/unloading connections of oil pipelines is secured. 5. The appropriateness of security lighting to both prevent acts of vandalism and assist in the discovery of oil discharges. |  |  | OBSERVATION: Failure to describe in the SPCC plan security measures required by 40 CFR Part 112.7(g), including: Securing access to oil handling, processing, and storage areas; Securing master flow and drain valves; Prevention of unauthorized access to starter controls on oil pumps; Securing loading/unloading connections of oil pipelines; Appropriateness of security lighting. CORRECTIVE ACTION: Update SPCC plan to properly address security measures required by 40 CFR Part 112.7(g). | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030001 |  |  | Facility security measures | Failure to implement security measures listed in the SPCC Plan and/or one or more of the following security measures for the facility: 1. Secure and control access to the oil handling, processing, and storage areas. 2. Secure the master flow and drain valves. 3. Prevent unauthorized access to starter controls and oil pumps. 4. Secure out-of-service and loading/unloading connections of oil pipelines. 5. Address the appropriateness of security lighting to both prevent acts of vandalism and assist in the discovery of oil discharges. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(g) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 41 | General SPCC Requirements | Security | Handling areas, valves, pumps/starter controls, load/unload connections secured, lighting adequate | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to implement security measures listed in the SPCC Plan and/or one or more of the following security measures for the facility: 1. Secure and control access to the oil handling, processing, and storage areas. 2. Secure the master flow and drain valves. 3. Prevent unauthorized access to starter controls and oil pumps. 4. Secure out-of-service and loading/unloading connections of oil pipelines. 5. Address the appropriateness of security lighting to both prevent acts of vandalism and assist in the discovery of oil discharges. |  |  | OBSERVATION: Facility failed to implement one or more security measures. CORRECTIVE ACTION: implement the following security measures for the facility: 1. Secure and control access to the oil handling, processing, and storage areas. 2. Secure the master flow and drain valves. 3. Prevent unauthorized access to starter controls and oil pumps. 4. Secure out-of-service and loading/unloading connections of oil pipelines. 5. Security lighting to both prevent acts of vandalism and assist in the discovery of oil discharges. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010025 |  |  | Loading/Unloading Racks | Failure to discuss in the SPCC Plan all requirements pertaining to a tank car or tank truck loading/unloading rack. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(h) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 42 | General SPCC Requirements | Loading/Unloading Racks | SPCC adequately discusses facility tank car and tank truck loading/unloading rack | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately discuss facility tank car and tank truck loading/unloading rack requirements in the SPCC plan. |  |  | OBSERVATION: SPCC plan does not adequately discuss facility tank car and tank truck loading/unloading rack requirements. CORRECTIVE ACTION: Amend SPCC plan to adequately discuss facility tank car and tank truck loading/unloading rack requirements. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030002 |  |  | Secondary containment at loading/unloading racks | Failure to ensure loading/unloading rack drainage flows to catchment basin or treatment facility designed to handle discharges, or use a quick drainage system when a tank car or tank truck loading/unloading rack is present at the facility. The containment system must be designed to hold at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(h)(1) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 43 | General SPCC Requirements | Loading/Unloading Racks | Loading rack containment has capacity to contain single largest compartment of tank car/truck | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure loading/unloading rack drainage flows to catchment basin or treatment facility designed to handle discharges, or use a quick drainage system when a tank car or tank truck loading/unloading rack is present at the facility. The containment system must be designed to hold at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. |  |  | OBSERVATION: Failure to ensure loading/unloading rack drainage flows to catchment basin or treatment facility designed to handle discharges, or use a quick drainage system when a tank car or tank truck loading/unloading rack is present at the facility, and is designed to hold at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. CORRECTIVE ACTION: Ensure loading/unloading rack drainage flows to containment or treatment system with at least the maximum capacity of any single compartment of a tank car or tank truck loaded or unloaded at the facility. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030003 |  |  | Warning to prevent vehicular departure at loading/unloading rack | Failure to provide an interlocked warning light or physical barriers, warning signs, wheel chocks, or vehicle brake interlock system in the area adjacent to the loading/unloading rack to prevent vehicles from departing before complete disconnection of flexible or fixed oil transfer lines when a loading/unloading rack is present at the facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(h)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 44 | General SPCC Requirements | Loading/Unloading Racks | Vehicular departure warning system in place at facility with a loading/unloading rack | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide an interlocked warning light or physical barriers, warning signs, wheel chocks, or vehicle brake interlock system in the area adjacent to the loading/unloading rack to prevent vehicles from departing before complete disconnection of flexible or fixed oil transfer lines when a loading/unloading rack is present at the facility. |  |  | OBSERVATION: Failure to provide an interlocked warning light or physical barriers, warning signs, wheel chocks, or vehicle brake interlock system in the area adjacent to the loading/unloading rack to prevent vehicles from departing before complete disconnection of flexible or fixed oil transfer lines when a loading/unloading rack is present at the facility. CORRECTIVE ACTION: Provide interlocked warning lights, physical barriers, warning signs, wheel chocks or vehicle brake interlock system in the area adjacent to the loading/unloading rack to prevent vehicles from departing before complete disconnection of flexible or fixed oil transfer lines | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010040 |  |  | Brittle fracture evaluation documentation | Failure to document evaluation of field-constructed aboveground tanks or containers for risk of discharge or failure due to brittle fracture or other catastrophe after tank undergoes repairs, alterations, reconstruction, or change in service. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(i) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 45 | General SPCC Requirements | Brittle Fracture | Documented evaluation of field-constructed tanks for risk of discharge due to brittle fracture | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to document evaluation of field-constructed aboveground tanks or containers for risk of discharge or failure due to brittle fracture or other catastrophe after tank undergoes repairs, alterations, reconstruction, or change in service. |  |  | OBSERVATION: Failure to document the evaluation of all field-constructed tanks for their risk of discharge due to brittle fracture or other catastrophe. This pertains to the [repair, alteration, reconstruction, change in service] of [describe affected tanks] that are currently at risk of discharge or failure due to brittle fracture. CORRECTIVE ACTION: Immediately conduct and document an evaluation of the impacted tanks and take any appropriate corrective action. | [6 empty] | No | Yes | No | No
APSA Program | Operations/Maintenance | 4030016 |  |  | Risk Analysis – Field constructed tanks | Failure to perform a brittle fracture evaluation of field-constructed aboveground tanks after tank repair, alteration, reconstruction, or change in service that might affect the risk of a discharge, and take appropriate action. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(i) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 46 | General SPCC Requirements | Brittle Fracture | Brittle fracture evaluation of field-constructed aboveground tanks performed | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform a brittle fracture evaluation of field-constructed aboveground tanks after tank repair, alteration, reconstruction, or change in service that might affect the risk of a discharge, and take appropriate action. |  |  | OBSERVATION: Failure to perform a brittle fracture evaluation of field-constructed aboveground tanks after tank repair, alteration, reconstruction, or change in service that might affect the risk of a discharge, and take appropriate action. CORRECTIVE ACTION: Perform a brittle fracture evaluation of field-constructed aboveground tanks after tank repair, alteration, reconstruction, or change in service that might affect the risk of a discharge, and take appropriate action. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030034 |  |  | Containment for qualified oil-filled operational equipment | Failure to provide general secondary containment or failure to fulfill alternative requirements to general secondary containment for oil-filled operational equipment. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(k) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 47 | General SPCC Requirements | Oil-Filled Operation Equipment | Oil filled operational equipment containment standards are met | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide general secondary containment or failure to fulfill alternative requirements to general secondary containment for oil-filled operational equipment. |  |  | OBSERVATION: Failure to provide general secondary containment or failure to fulfill alternative requirements to general secondary containment for oil-filled operational equipment. CORRECTIVE ACTION: Provide items needed to satisfy conditions of general secondary containment or demonstrate how alternate oil containment standards for oil filled operational equipment are being met. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010027 |  |  | Facility Drainage | Failure to adequately discuss in the SPCC Plan facility drainage or drainage controls such as secondary containment around containers and other structures, equipment, and procedures for the control of a discharge. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(a)(3)(iii); 112.8(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 48 | SPCC Requirements for Onshore Facilities | Drainage | Facility drainage or drainage controls adequately discussed | 59 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately discuss in the SPCC Plan facility drainage or drainage controls such as secondary containment around containers and other structures, equipment, and procedures for the control of a discharge. |  |  | OBSERVATION: Failure to adequately discuss facility drainage or drainage controls, or no discussion of facility drainage included within the SPCC plan. CORRECTIVE ACTION: Revise SPCC plan to adequately discuss facility drainage or drainage controls. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030035 |  |  | Facility drainage from diked storage areas | Failure to ensure drainage from diked storage areas is restrained by valves, except where facility systems are designed to control such discharge, or failure to ensure manually activated pumps or ejectors are used and the condition of the accumulation is inspected prior to draining. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(b)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 49 | SPCC Requirements for Onshore Facilities | Drainage | Facility drainage adequately restrained unless conditions met | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately use valves to restrain drainage from diked storage areas unless system designed to control drainage, or failure to use manually activated pumps to empty diked areas, and/or failure to inspect condition of accumulation prior to draining. |  |  | OBSERVATION: Failure to adequately use valves to restrain drainage from diked storage areas or failure to use manually activated pumps to empty diked areas, and/or failure to inspect condition of accumulation prior to draining. CORRECTIVE ACTION: Ensure that valves remain closed to prevent drainage from diked areas, only use manually activated pumps to empty diked areas, and inspect condition of accumulation prior to draining. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030005 |  |  | Valves for drainage of diked areas | Failure to use drain valves in diked storage areas that are manual, open-and-closed design (not flapper-type drain valves). | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(b)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 50 | SPCC Requirements for Onshore Facilities | Drainage | Valves used for drainage are manual (not flapper-type) to prevent a discharge | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to use drain valves in diked storage areas that are manual, open-and-closed design (not flapper-type drain valves). |  |  | OBSERVATION: Failure to use drain valves in diked storage areas that are manual, open-and-closed design (not flapper-type drain valves). CORRECTIVE ACTION: Use drain valves in diked storage areas that are manual, open-and-closed design (not flapper-type drain valves). | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030008 |  |  | Drainage from undiked areas | Failure to design drainage from undiked areas to either: 1. Flow into catchment basins, ponds, or lagoons to retain oil or return it to the facility. OR 2. Equip the facility with a diversion system that would retain oil in the facility. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(b)(3), 112.8(b)(4) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 51 | SPCC Requirements for Onshore Facilities | Drainage | Drainage from undiked areas or diversion systems designed to retain final discharge in facility | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to design drainage from undiked areas to either: 1. Flow into catchment basins, ponds, or lagoons to retain oil or return it to the facility. OR 2. Equip the facility with a diversion system that would retain oil in the facility. |  |  | OBSERVATION: Failure to design drainage from undiked areas to either: 1. Flow into catchment basins, ponds, or lagoons to retain oil or return it to the facility. OR 2. Equip the facility with a diversion system that would retain oil in the facility. CORRECTIVE ACTION: Design drainage from undiked areas to flow into catchment basins ponds, or lagoons, or, equip the facility with a diversion system that would retain oil in the facility. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030009 |  |  | Lift pumps for treated drainage water | Failure to provide two lift pumps, and permanently install at least one of the pumps, if facility drainage waters are continuously treated in more than one treatment unit and pump transfer is needed. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(b)(5) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 52 | SPCC Requirements for Onshore Facilities | Drainage | Lift pumps provided for treated drainage waters when more than one treatment unit | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide two lift pumps, and permanently install at least one of the pumps, if facility drainage waters are continuously treated in more than one treatment unit and pump transfer is needed. |  |  | OBSERVATION: Failure to provide two lift pumps, and permanently install at least one of the pumps, where drainage waters are continuously treated in more than one treatment unit and pump transfer is needed. CORRECTIVE ACTION: Provide two lift pumps, and permanently install at least one of the pumps, for drainage waters that are continuously treated in more than one treatment unit and pump transfer is needed. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010029 |  |  | Bulk Storage Containers | Failure to adequately discuss in the SPCC Plan all applicable bulk storage containers, including compatibility with material stored and conditions of storage, and description of sized secondary containment capable of containing the largest single container and sufficient freeboard to contain precipitation. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.8(c)(1)&(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 53 | SPCC Requirements for Onshore Facilities | Bulk Storage Container-SPCC Plan/Compatibility | Adequate discussion of all bulk storage containers located at the facility | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately discuss in the SPCC Plan all applicable bulk storage containers, including compatibility with material stored and conditions of storage, and description of sized secondary containment capable of containing the largest single container and sufficient freeboard to contain precipitation. |  |  | OBSERVATION: SPCC plan does not adequately discuss all bulk storage containers, including compatibility with material stored and conditions of storage, and description of sized secondary containment capable of containing the largest single container and sufficient freeboard to contain precipitation. CORRECTIVE ACTION: Amend the SPCC Plan to address all bulk storage containers stored at this facility. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030012 |  |  | Tanks compatible with stored materials | Failure to use containers with material and construction compatible with material stored and conditions of storage such as pressure and temperature. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 54 | SPCC Requirements for Onshore Facilities | Bulk Storage Container-SPCC Plan/Compatibility | Material and construction of all containers are compatible with the material stored | 83 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to use containers with material and construction compatible with material stored and conditions of storage such as pressure and temperature. |  |  | OBSERVATION: Failure to use containers with material and construction compatible with material stored and conditions of storage such as pressure and temperature. CORRECTIVE ACTION: Immediately remove all oil stored in non-compatible containers. Store oil in containers with material and construction compatible with the material stored and conditions of storage such as pressure and temperature. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030010 |  |  | Sized secondary containment | Failure to provide and maintain secondary containment for bulk storage tank installations (except for mobile refuelers and other non-transportation-related tank trucks) sufficient to hold the capacity of the largest container and sufficient freeboard for precipitation. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 55 | SPCC Requirements for Onshore Facilities | Secondary Containment | Adequately sized secondary containment provided and maintained for bulk storage containers | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide and maintain secondary containment for bulk storage tank installations (except for mobile refuelers and other non-transportation-related tank trucks) sufficient to hold the capacity of the largest container and sufficient freeboard for precipitation. |  |  | OBSERVATION: Failure to provide and maintain secondary containment for bulk storage tank installations sufficient to hold the capacity of the largest container and sufficient freeboard for precipitation. CORRECTIVE ACTION: Provide and maintain adequate secondary containment for bulk storage containers. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030041 |  |  | Tier I - Bulk storage container sized secondary containment | Failure to provide bulk storage containers with adequate secondary containment large enough to contain the entire capacity of the largest container plus additional capacity to contain precipitation when applicable, and/or failure to position/locate mobile or portable containers to prevent a discharge. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(3)(ii) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 56 | SPCC Requirements for Onshore Facilities | Secondary Containment | All bulk storage containers have secondary containment to prevent a discharge at Tier I facility | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide bulk storage containers with adequate secondary containment large enough to contain the entire capacity of the largest container plus additional capacity to contain precipitation when applicable, and/or failure to position/locate mobile or portable containers to prevent a discharge. |  |  | OBSERVATION: Bulk storage containers do not have adequate secondary containment. CORRECTIVE ACTION: Provide secondary containment for bulk storage containers large enough to contain the entire capacity of the largest container plus additional capacity to contain precipitation. | [6 empty] | No | No | Yes | No
APSA Program | Operations/Maintenance | 4030043 |  |  | Secondary containment and leak detection for TIUGA piping | Failure to have secondary containment and/or leak detection, pursuant to 24 CCR Part 9, Chapter 57, Section 5703.6.2.2, if piping connected to a tank in an underground area (TIUGA) cannot be directly viewed on all sidesfor the entire length of the piping that is beneath the surface of the ground. This does not apply to: 1. Piping connected to a tank that contains new oil/used oil for lubricant or coolant in a motor engine or transmission, or oil-filled operational/manufacturing equipment. 2. Piping connected to a tank used solely in connection with a fire pump or emergency system, legally required standby system, or optional standby system. 3. Piping connected to a petroleum hazardous waste tank that complies with hazardous waste tank standards (22 CCR Ch. 15, Art. 10) and facility has been issued a unified program facility permit pursuant to HSC Section 25404.2 for generation, treatment, accumulation, or storage of hazardous waste. | HSC 6.67 25270.2(o)(1)(C)(iv) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 57 | SPCC Requirements for Onshore Facilities | Secondary Containment | Secondary containment and/or leak detection provided for TIUGA piping if not viewable on all sides | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have secondary containment and/or leak detection, pursuant to 24 CCR Part 9, Chapter 57, Section 5703.6.2.2, if piping connected to a tank in an underground area (TIUGA) cannot be directly viewed on all sidesfor the entire length of the piping that is beneath the surface of the ground. This does not apply to: 1. Piping connected to a tank that contains new oil/used oil for lubricant or coolant in a motor engine or transmission, or oil-filled operational/manufacturing equipment. 2. Piping connected to a tank used solely in connection with a fire pump or emergency system, legally required standby system, or optional standby system. 3. Piping connected to a petroleum hazardous waste tank that complies with hazardous waste tank standards (22 CCR Ch. 15, Art. 10) and facility has been issued a unified program facility permit pursuant to HSC Section 25404.2 for generation, treatment, accumulation, or storage of hazardous waste. |  |  | OBSERVATION: Owner/Operator failed to provide secondary containment and/or leak detection for piping connected to a tank in an underground area (TIUGA) that cannot be directly viewed for the entire length of the piping that is beneath the surface of the ground on all sides. [Not applicable to piping connected to tank containing new/used oil used for lube or coolant in engine/transmission, oil-filled equipment, piping connected to tank used for fire pump or emergency system, or for piping connected to permitted hazardous waste tank]. CORRECTIVE ACTION: Provide secondary containment and/or leak detection for piping connected to a tank in an underground area (TIUGA) that cannot be directly viewed for the entire length of the piping that is beneath the surface of the groundon all sides. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030013 |  |  | Diked areas sufficiently impervious to oil | Failure to ensure that containment systems of diked areas in all bulk storage tank installations are either: 1. Sufficiently impervious to contain discharged oil until cleaned up. OR 2. Any discharge to a drainage trench system will be safely confined in a facility catchment basin or holding pond until cleaned up. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 58 | SPCC Requirements for Onshore Facilities | Secondary Containment | Containment systems are sufficiently impervious to contain oil | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure that containment systems of diked areas in all bulk storage tank installations are either: 1. Sufficiently impervious to contain discharged oil until cleaned up. OR 2. Any discharge to a drainage trench system will be safely confined in a facility catchment basin or holding pond until cleaned up. |  |  | OBSERVATION: Failure to ensure that containment systems of diked areas in all bulk storage tank installations are either: 1. Sufficiently impervious to contain discharged oil until cleaned up. OR 2. Discharge to a drainage trench system that is safely confined in a facility catchment basin or holding pond until cleaned up. CORRECTIVE ACTION: Maintain/Install containment systems, including walls and floors to be sufficiently impervious to contain oil. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030006 |  |  | Drainage inspections and valves | Failure to ensure the following before allowing drainage of uncontaminated rainwater from diked area into a storm drain or discharge of an effluent into an open watercourse, lake, or pond, bypassing the facility treatment system: 1. Keep bypass valve normally sealed closed. 2. Inspect the retained rainwater. 3. Open and reseal bypass valves under responsible supervision. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(3)(i), 112.8(c)(3)(ii), 112.8(c)(3)(iii) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 59 | SPCC Requirements for Onshore Facilities | Drainage Inspections/Records | Rainwater in diked areas is inspected before draining | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to ensure the following before allowing drainage of uncontaminated rainwater from diked area into a storm drain or discharge of an effluent into an open watercourse, lake, or pond, bypassing the facility treatment system: 1. Keep bypass valve normally sealed closed. 2. Inspect the retained rainwater 3. Open and reseal bypass valves under responsible supervision. |  |  | OBSERVATION: Failure to ensure the following before allowing drainage of uncontaminated rainwater from diked area into a storm drain or discharge of an effluent into an open watercourse, lake, or pond, bypassing the facility treatment system: 1. Keep bypass valve normally sealed closed. 2. Inspect the retained rainwater 3. Open and reseal bypass valves under responsible supervision. CORRECTIVE ACTION: Before draining rainwater from diked areas be sure to Inspect the retained rainwater, and open and reseal bypass valves under responsible supervision. Keep bypass valve normally sealed closed. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010026 |  |  | Drainage records | Failure to maintain adequate records of drainage when there is drainage of uncontaminated rainwater from diked areas into a storm drain or open watercourse; for example, records required under NPDES permit. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(3)(iv) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 60 | SPCC Requirements for Onshore Facilities | Drainage Inspections/Records | Records maintained of drainage from diked areas | 47 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain adequate records of drainage when there is drainage of uncontaminated rainwater from diked areas into a storm drain or open watercourse; for example, records required under NPDES permit. |  |  | OBSERVATION: Failure to maintain adequate records (or NPDES permit records) of drainage from diked areas. CORRECTIVE ACTION: Maintain adequate records (or NPDES permit records) of drainage from diked areas. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030017 |  |  | Corrosion Protection | Failure to protect the buried section of a partially buried or bunkered metallic tank from corrosion by coatings or cathodic protection compatible with local soil conditions. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(5) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 61 | SPCC Requirements for Onshore Facilities | Cathodic Protection | Buried section of partially buried or bunkered metallic tank has corrosion protection | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to protect the buried section of a partially buried or bunkered metallic tank from corrosion by coatings or cathodic protection compatible with local soil conditions. |  |  | OBSERVATION: Failure to protect the buried section of a partially buried or bunkered metallic tank from corrosion. CORRECTIVE ACTION: Provide corrosion protection for partially buried tanks. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010028 |  |  | Integrity testing and inspection procedures | Failure to discuss in the SPCC Plan procedures to test or inspect each aboveground container for integrity in accordance with industry standards: 1. On a regular schedule. 2. After material repairs are made. 3. By qualified personnel. 4. The frequency and type of testing and inspections based on container size, configuration, and design. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.8(c)(6) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 62 | SPCC Requirements for Onshore Facilities | Inspections & Testing | SPCC discusses procedures to test/inspect storage containers for integrity per industry standards | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to discuss in the SPCC Plan procedures to test or inspect each aboveground container for integrity in accordance with industry standards: 1. On a regular schedule. 2. After material repairs are made. 3. By qualified personnel. 4. The frequency and type of testing and inspections based on container size, configuration, and design. |  |  | OBSERVATION: SPCC Plan does not adequately discuss procedures to test or inspect each aboveground container for integrity in accordance with industry standards, and/or does not address one or more of the following: Inspections and testing completed on a regular schedule, after material repairs are made, by qualified personnel, the frequency and type of testing and inspections based on container size, configuration, and design. CORRECTIVE ACTION: Revise SPCC Plan to adequately discuss facility's procedures to test and inspect aboveground/bulk storage containers in accordance with specified industry standards. This must include, but not be limited to, inspection/testing schedule/frequency, and personnel qualifications. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030014 |  |  | Tanks inspected or tested by qualified person | Failure to ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(e), 112.8(c)(6) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 63 | SPCC Requirements for Onshore Facilities | Inspections & Testing | Tanks inspected and tested by qualified person in accordance with industry standards | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. |  |  | OBSERVATION: Failure to ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. CORRECTIVE ACTION: Ensure that tanks are inspected and tested by an appropriately qualified person in accordance with industry standards. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030015 |  |  | Tanks inspected and/or integrity tested | Failure to test or inspect each aboveground container for integrity based on industry standards as discussed in the SPCC Plan: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(e), 112.8(c)(6) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 64 | SPCC Requirements for Onshore Facilities | Inspections & Testing | Aboveground containers tested or inspected for integrity based on industry standards | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to test or inspect each aboveground container for integrity based on industry standards as discussed in the SPCC Plan: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. |  |  | OBSERVATION: Failure to test or inspect each aboveground container for integrity based on industry standards as discussed in the SPCC Plan: 1. On a regular schedule. 2. After making material repairs. 3. Use non-destructive testing. 4. Inspect each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. CORRECTIVE ACTION: Test or inspect each aboveground container for integrity based on industry standards on a regular schedule, after making material repairs, using non-destructive testing, inspecting each container’s supports, foundations, and outside for signs of deterioration, discharges, or accumulation of oil inside diked areas. Maintain testing and inspection records. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030045 |  |  | Direct Viewing and leak detection for TIUGA | Failure to meet one of the following criteria for a tank in an underground area (TIUGA): 1. The structure in which the tank is located provides enough space for direct viewing of the exterior of the tank except for the part of the tank in contact with the surface of the floor. OR 2. Inspections of the interstitial space or containment structure are performed, or the tank has a mechanical or electronic device that will detect leaks in the interstitial space or containment structure and alert the tank operator. Direct viewing does not apply to a tank that stores hazardous waste petroleum and meets the requirements of CCR Title 22. | HSC 6.67 25270.2(o)(1)(C)(i), (iii), (iv)(III), 25270.2(o)(2) | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 65 | SPCC Requirements for Onshore Facilities | Inspections & Testing | TIUGAs meet requirements for direct viewing or inspections/ leak detection | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to meet one of the following criteria for a tank in an underground area (TIUGA): 1. The structure in which the tank is located provides enough space for direct viewing of the exterior of the tank except for the part of the tank in contact with the surface of the floor. OR 2. Inspections of the interstitial space or containment structure are performed, or the tank has a mechanical or electronic device that will detect leaks in the interstitial space or containment structure and alert the tank operator. Direct viewing does not apply to a tank that stores hazardous waste petroleum and meets the requirements of CCR Title 22. |  |  | OBSERVATION: Owner/Operator failed to meet one of the following criteria for a tank in an underground area (TIUGA): 1. The structure in which the tank is located provides enough space for direct viewing of the exterior of the tank except for the part of the tank in contact with the surface of the floor. OR; 2. Inspections of the interstitial space or containment structure are performed, or the tank has a mechanical or electronic device that will detect leaks in the interstitial space or containment structure and alert the tank operator. Direct viewing does not apply to a tank that stores hazardous waste petroleum and meets the requirements of CCR Title 22. CORRECTIVE ACTION: Begin implementing one of the two options and provide documentation of compliance. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010021 |  |  | Written records of inspections and tests | Failure to comply with one or more of the following requirements: 1. Have record of inspections and tests, including integrity tests, signed by the appropriate supervisor or inspector. 2. Keep written procedures and records of inspections and tests, including integrity tests, for at least three years. 3. Keep comparison records for bulk storage tanks subject to 40 CFR 112.8(c)(6). | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.7(e), 112.8(c)(6) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 65 66 | SPCC Requirements for Onshore Facilities | Inspections & Testing | Written Inspection/testing procedures kept, inspection/testing records signed, kept for 3 years | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with one or more of the following requirements: 1. Have record of inspections and tests, including integrity tests, signed by the appropriate supervisor or inspector. 2. Keep written procedures and records of inspections and tests, including integrity tests, for at least three years. 3. Keep comparison records for bulk storage tanks subject to 40 CFR 112.8(c)(6). |  |  | OBSERVATION: Failure to comply with one or more of the following requirements: 1. Have record of inspections and tests, including integrity tests, signed by the appropriate supervisor or inspector. 2. Keep written procedures and records of inspections and tests, including integrity tests, for at least three years. 3. Keep comparison records for bulk storage containers subject to 40 CFR 112.8(c)(6). CORRECTIVE ACTION: Keep written inspection procedures, records of inspections and testing, signed by appropriate supervisor/inspector, for at least 3 years. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030018 |  |  | Steam return/exhaust monitored | Failure to monitor the steam return and exhaust lines of any internal heating coils for contamination if they discharge into an open watercourse, or failure to pass the steam return and exhaust lines through a settling tank, skimmer, or other separation or retention system. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(7) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 66 67 | SPCC Requirements for Onshore Facilities | Steam Return/Exhaust | Steam return/exhaust lines that discharge to watercourse are monitored or have treatment system | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to monitor the steam return and exhaust lines of any internal heating coils for contamination if they discharge into an open watercourse, or failure to pass the steam return and exhaust lines through a settling tank, skimmer, or other separation or retention system. |  |  | OBSERVATION: Failure to monitor the steam return and exhaust lines of any internal heating coils for contamination, or failure to pass the steam return and exhaust lines through a separation or retention system. CORRECTIVE ACTION: Monitor or implement a treatment system for steam return/exhaust of internal heating coils which discharge into a water course. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010056 |  |  | Overfill prevention | Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the devices or systems in place for each container to prevent overfills. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.8(c)(8) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 67 68 | SPCC Requirements for Onshore Facilities | Overfill Prevention | SPCC adequately describes overfill prevention methods, and devices/systems used for each container | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the devices or systems in place for each container to prevent overfills. |  |  | OBSERVATION: Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the devices or systems in place for each container to prevent overfills. CORRECTIVE ACTION: Update SPCC plan to properly address overfill prevention methods, including a description of the devices or systems in place for each container to prevent overfills. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010055 |  |  | Tier I - Overfill prevention | Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the systems or procedures used to prevent overfills for each container. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(3)(iii) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 68 69 | SPCC Requirements for Onshore Facilities | Overfill Prevention | SPCC plan adequately describes overfill prevention methods, including system or procedures used | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the systems or procedures used to prevent overfills for each container. |  |  | OBSERVATION: Failure to adequately describe in the SPCC Plan, overfill prevention methods, including a description of the systems or procedures used to prevent overfills for each container. CORRECTIVE ACTION: Update SPCC plan to properly address overfill prevention methods, including a description of the systems or procedures used to prevent overfills for each container. | [6 empty] | No | No | Yes | No
APSA Program | Operations/Maintenance | 4030042 |  |  | Tier I - Overfill prevention implementation | Failure to provide systems or follow procedures to prevent overfills as described in the SPCC Plan, and/or failure to routinely test to ensure proper operation. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.6(a)(3)(iii) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 69 70 | SPCC Requirements for Onshore Facilities | Overfill Prevention | Overfill prevention systems or procedures are used and tested routinely to ensure proper operation | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide systems or follow procedures to prevent overfills as described in the SPCC Plan, and/or failure to routinely test to ensure proper operation. |  |  | OBSERVATION: Failure to provide systems or follow procedures to prevent overfills as described in the SPCC Plan, and/or failure to routinely test to ensure proper operation. CORRECTIVE ACTION: Provide systems or begin following procedures to prevent overfills as described in SPCC plan, and routinely test systems or devices used to prevent overfilling. | [6 empty] | No | No | Yes | No
APSA Program | Operations/Maintenance | 4030019 |  |  | Overfill prevention implementation | Failure to engineer or update each container installation in accordance with good engineering practice to avoid discharges and/or failure to provide at least one of the following devices on each container installation: 1. An audible or visual high liquid level alarm. 2. High liquid level pump cutoff devices. 3. Audible or code signal communications between tank gauger and pumping station. 4. A fast response system for determining liquid levels, such as computers, telepulse or direct vision gauges. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(8), 112.8(c)(8)(i), 112.8(c)(8)(ii), 112.8(c)(8)(iii), 112.8(c)(8)(iv) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 70 71 | SPCC Requirements for Onshore Facilities | Overfill Prevention | Each container installation has a liquid level sensing device. | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to engineer or update each container installation in accordance with good engineering practice to avoid discharges and/or failure to provide at least one of the following devices on each container installation: 1. An audible or visual high liquid level alarm. 2. High liquid level pump cutoff devices. 3. Audible or code signal communications between tank gauger and pumping station. 4. A fast response system for determining liquid levels, such as computers, telepulse or direct vision gauges. |  |  | OBSERVATION: Failure to engineer or update each container installation in accordance with good engineering practice to avoid discharges and/or failure to provide for each container installation: An audible or visual high liquid level alarm; High liquid level pump cutoff devices; Audible or code signal communications between tank gauger and pumping station; or A fast response system for determining liquid levels, such as computers, telepulse or direct vision gauges. CORRECTIVE ACTION: Provide at least one of the required items listed for each container installation. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030022 |  |  | Testing of liquid level sensing devices | Failure to regularly test liquid level sensing devices to ensure proper operation. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(8)(v) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 71 72 | SPCC Requirements for Onshore Facilities | Overfill Prevention | Liquid level sensing devices regularly tested to ensure proper operation | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to regularly test liquid level sensing devices to ensure proper operation. |  |  | OBSERVATION: Failure to regularly test liquid level sensing devices to ensure proper operation. CORRECTIVE ACTION: Test liquid level sensing devices to ensure proper operation. Submit test results | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030023 |  |  | Observation of effluent discharge to navigable waters | Failure to observe effluent treatment facilities frequently enough to detect possible system upsets that could cause a discharge as described in 40 CFR 112.1(b). | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(9) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 72 73 | SPCC Requirements for Onshore Facilities | Effluent Treatment | Discharge from effluent treatment facilities which discharge to navigable waterways observed | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to observe effluent treatment facilities frequently enough to detect possible system upsets that could cause a discharge as described in 40 CFR 112.1(b). |  |  | OBSERVATION: Failure to observe effluent treatment facilities frequently enough to detect possible system upsets that could cause a discharge. CORRECTIVE ACTION: Observe effluent treatment facilities frequently enough to detect possible system upsets that could cause a discharge. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030021 |  |  | Leaks addressed and oil removed | Failure to promptly correct visible discharges and promptly remove any accumulations of oil in diked areas. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(10) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 73 74 | SPCC Requirements for Onshore Facilities | Response to Release | Visible discharges promptly corrected and any accumulation of oil in diked areas promptly removed. | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to promptly correct visible discharges and promptly remove any accumulations of oil in diked areas. |  |  | OBSERVATION: Failure to promptly correct visible discharges and promptly remove any accumulations of oil in diked areas. CORRECTIVE ACTION: Promptly correct any visible discharges and promptly remove any accumulations of oil in diked areas. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030020 |  |  | Mobile or portable storage container positioning and sized containment | Failure to position or locate mobile or portable storage containers to prevent a discharge as described in 40 CFR 112.1(b), and/or failure to provide adequate secondary containment for mobile or portable oil storage containers (excluding mobile refuelers and other non-transportation-related tank trucks) with sufficient capacity to contain the largest single compartment or container and sufficient freeboard to contain precipitation. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(c)(11) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 74 75 | SPCC Requirements for Onshore Facilities | Mobile/Portable Container | Adequate secondary containment provided for mobile/portable storage containers | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to position or locate mobile or portable storage containers to prevent a discharge as described in 40 CFR 112.1(b), and/or failure to provide adequate secondary containment for mobile or portable oil storage containers (excluding mobile refuelers and other non-transportation-related tank trucks) with sufficient capacity to contain the largest single compartment or container and sufficient freeboard to contain precipitation. |  |  | OBSERVATION: Failure to position or locate mobile or portable storage containers to prevent a discharge as described in 40 CFR 112.1(b), and/or failure to provide mobile or portable oil storage containers (excluding mobile refuelers and other non-transportation-related tank trucks) with adequate secondary containment with sufficient capacity to contain the largest single compartment or container and sufficient freeboard to contain precipitation. CORRECTIVE ACTION: Position or locate mobile or portable storage containers to prevent a discharge, and/or provide adequate secondary containment for mobile or portable oil storage tanks. | [6 empty] | No | Yes | No | Yes
APSA Program | Administration/Documentation | 4010058 |  |  | Piping | Failure to include in the SPCC Plan, when required, a discussion of aboveground piping, buried piping, piping inspections, or vehicle warnings. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.7(a)(1), 112.8(d)(1), (4) & (5) | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 76 | SPCC Requirements for Onshore Facilities | Piping | SPCC Plan discusses aboveground piping, buried piping, piping inspections, and vehicle warnings. | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include in the SPCC Plan a discussion of aboveground piping, buried piping, piping inspections, or vehicle warnings. |  |  | OBSERVATION: SPCC Plan does not discuss, or inadequatly describes aboveground piping, buried piping, piping inspections, or vehicle warnings. CORRECTIVE ACTION: Update SPCC Plan to include a discussion of aboveground piping, buried piping, piping inspections, and vehicle warnings. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030025 |  |  | Inspection and/or repair of buried piping | Failure to inspect for deterioration any section of buried piping that is exposed for any reason, and to undertake additional examination and corrective action if corrosion damage is found. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 75 77 | SPCC Requirements for Onshore Facilities | Piping | Buried piping is inspected for deterioration if exposed and repaired if corrosion damage is found | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to inspect for deterioration any section of buried piping that is exposed for any reason, and to undertake additional examination and corrective action if corrosion damage is found. |  |  | OBSERVATION: Failure to inspect for deterioration any section of buried piping that is exposed for any reason, and to undertake additional examination and corrective action if corrosion damage is found. CORRECTIVE ACTION: Inspect for deterioration any buried piping that is exposed and undertake corrective action if corrosion damage is found. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030027 |  |  | Protection of buried piping | Failure to provide buried piping that is installed or replaced on or after August 16, 2002, with a protective wrapping or coating, and to ensure it is cathodically protected or otherwise satisfies the corrosion protection standards for piping in 40 CFR part 280 or 281. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 76 78 | SPCC Requirements for Onshore Facilities | Piping | Buried piping is corrosion protected with protective wrapping, coating, or cathodic protection | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide buried piping that is installed or replaced on or after August 16, 2002, with a protective wrapping or coating, and to ensure it is cathodically protected or otherwise satisfies the corrosion protection standards for piping in 40 CFR part 280 or 281. |  |  | OBSERVATION: Failure to provide buried piping with protective wrapping or coating, and to ensure it is cathodically protected or otherwise satisfies corrosion protection standards for piping. CORRECTIVE ACTION: Provide buried piping with protective wrapping or coating, or cathodic protection. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030028 |  |  | Stand-by piping | Failure to cap or blank-flange the terminal connection at the transfer point and mark it as to origin when piping is not in service or is in standby service for an extended time. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(2) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 77 79 | SPCC Requirements for Onshore Facilities | Piping | Terminal connection capped/blank flanged at transfer point & origin marked if not in service/standby | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to cap or blank-flange the terminal connection at the transfer point and mark it as to origin when piping is not in service or is in standby service for an extended time. |  |  | OBSERVATION: Failure to cap or blank-flange the terminal connection at the transfer point and mark it as to origin when piping is not in service or is in standby service for an extended time. CORRECTIVE ACTION: Cap or blank-flange the terminal connection at the transfer point and label as to origin. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030029 |  |  | Piping supports | Failure to properly design pipe supports to minimize abrasion and corrosion, and allow for expansion and contraction. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(3) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 78 80 | SPCC Requirements for Onshore Facilities | Piping | Pipe supports designed to minimize abrasion and corrosion, and allow for expansion and contraction | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly design pipe supports to minimize abrasion and corrosion, and allow for expansion and contraction. |  |  | OBSERVATION: Failure to properly design pipe supports to minimize abrasion and corrosion, and allow for expansion and contraction. CORRECTIVE ACTION: Design and install pipe supports to minimize abrasion and corrosion, and allow for expansion and contraction. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030026 |  |  | Inspection of aboveground piping | Failure to regularly inspect aboveground valves, piping, and appurtenances. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(4) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 79 81 | SPCC Requirements for Onshore Facilities | Piping | Aboveground valves, piping, and appurtenances are regularly inspected | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to regularly inspect aboveground valves, piping, and appurtenances. |  |  | OBSERVATION: Failure to regularly inspect aboveground valves, piping, and appurtenances. CORRECTIVE ACTION: Regularly inspect aboveground valves, piping, and appurtenances. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030030 |  |  | Testing of buried piping | Failure to perform integrity and leak testing of buried piping at the time of installation, modification, construction, relocation, or replacement. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(4) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 80 82 | SPCC Requirements for Onshore Facilities | Piping | Integrity/leak tested buried piping when installed, modified, constructed, relocated, or replaced | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to perform integrity and leak testing of buried piping at the time of installation, modification, construction, relocation, or replacement. |  |  | OBSERVATION: Failure to perform integrity and leak testing of buried piping at the time of installation, modification, construction, relocation, or replacement. CORRECTIVE ACTION: Perform integrity and leak testing of buried piping at the time of installation, modification, construction, relocation, or replacement. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030031 |  |  | Warning to vehicles about aboveground piping | Failure to warn vehicle traffic regarding aboveground piping or other oil transfer operations. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.8(d)(5) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 81 83 | SPCC Requirements for Onshore Facilities | Piping | Vehicle traffic warned of aboveground piping or other oil transfer operations | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to warn vehicle traffic regarding aboveground piping or other oil transfer operations. |  |  | OBSERVATION: Failure to warn vehicle traffic about aboveground piping or other oil transfer operations. CORRECTIVE ACTION: Warn vehicle traffic about aboveground piping or other oil transfer operations. | [6 empty] | No | Yes | No | Yes
APSA Program | Operations/Maintenance | 4030044 |  |  | Excluded TIUGA with less than 55-gallon capacity | Failure of an owner/operator of an excluded tank in an underground area (TIUGA) with less than 55-gallon capacity to have secondary containment, conduct monthly inspections, and/or maintain a log of inspections. | HSC 6.67 25270.2(a)(8) | 2019-09-01 | 2099-12-31 | 2019-09-01 | Revised | 82 84 | Excluded TIUGA Requirements |  | Excluded TIUGA <55 gal has secondary containment, inspected monthly and log of inspections kept | 95 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of an owner/operator of an excluded tank in an underground area (TIUGA) with less than 55-gallon capacity to have secondary containment, conduct monthly inspections, and/or maintain a log of inspections. |  |  | OBSERVATION: Owner/operator of an excluded tank in an underground area (TIUGA) with less than 55-gallon capacity failed to have secondary containment, conduct monthly inspections, and/or maintain a log of inspections. CORRECTIVE ACTION: Provide secondary containment, conduct monthly inspections and maintain log for excluded TIUGA or include in your SPCC plan. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010037 |  |  | Excluded oil-filled electrical equipment | Failure to prepare an appropriate SPCC Plan or amend an existing SPCC Plan when the facility does not meet the criteria for exclusion for oil-filled electrical equipment. | HSC 6.67 25270.2(a)(4), 25270.4.5(a) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 83 85 | Oil Filled Electrical Equipment |  | Oil filled electrical equipment exclusions have been met, and where not met is included in SPCC plan | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare an appropriate SPCC Plan or amend an existing SPCC Plan when the facility does not meet the criteria for exclusion for oil-filled electrical equipment. |  |  | OBSERVATION: Failure to complete SPCC plan or include oil-filled electrical equipment in SPCC plan for any oil-filled electrical equipment that does not meet provisions of excluded oil-filled electrical equipment. CORRECTIVE ACTION: Maintain oil-filled electrical equipment so that it meets the exclusion criteria or include the oil-filled equipment in the SPCC Plan. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030032 |  |  | Conditionally exempt facility conditions | Failure of a conditionally exempt facility to allow the UPA to conduct a periodic inspection, install secondary containment when the UPA determines that it is necessary, and/or conduct daily visual inspections to protect the waters of the state. | HSC 6.67 25270.4.5(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 84 86 | Conditionally Exempt Facilities |  | Exempt facility allowed UPA inspections, has secondary containment, conducted daily inspections. | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a conditionally exempt facility to allow the UPA to conduct a periodic inspection, install secondary containment when the UPA determines that it is necessary, and/or conduct daily visual inspections to protect the waters of the state. |  |  | OBSERVATION: Failure to allow the UPA to conduct a periodic inspection, install secondary containment when the UPA determines that it is necessary, and/or conduct daily visual inspections to protect the waters of the state. CORRECTIVE ACTION: Allow the UPA to conduct a periodic inspection, install secondary containment when the UPA determines that it is necessary, and/or conduct daily visual inspections to protect the waters of the state. | [6 empty] | Yes | No | No | No
APSA Program | Administration/Documentation | 4010032 |  |  | Annual tank facility statement | Failure to submit a tank facility statement on or before January 1 annually unless a current Business Plan has been submitted. | HSC 6.67 25270.6(a)(1), 25270.6(a)(2) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 85 87 | General Facility Requirements |  | Tank Facility Statement or Business Plan has been submitted | 59 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to submit a Tank Facility Statement or Business Plan. |  |  | OBSERVATION: Failure to submit a Tank Facility Statement or Business Plan. CORRECTIVE ACTION: Submit a Tank Facility Statement or Business Plan. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Release/Leaks/Spills | 4040001 |  |  | Release Reporting | Failure to report immediately upon discovery spills or other releases of one barrel (42 gallons) or more of petroleum in or on any waters of the State in accordance with Section 13272(a) of the California Water Code to Cal OES and UPA or 911. | HSC 6.67 25270.8 | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 86 88 | General Facility Requirements |  | Spills/releases of 42 gallons or more of petroleum reported upon discovery to Cal OES & UPA or 911 | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to report immediately upon discovery spills or other releases of one barrel (42 gallons) or more of petroleum in or on any waters of the State in accordance with Section 13272(a) of the California Water Code to Cal OES and UPA or 911. |  |  | OBSERVATION: Failure to report immediately upon discovery spills or other releases of one barrel (42 gallons) or more of petroleum in or on any waters of the State in accordance with Section 13272(a) of the California Water Code to Cal OES and UPA or 911. CORRECTIVE ACTION: Immediately upon discovery report spills or other releases of one barrel (42 gallons) or more of petroleum in or on any waters of the State in accordance with Section 13272(a) of the California Water Code to Cal OES and UPA or 911. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010033 |  |  | APSA Fee | Failure to pay the APSA Program fee. | HSC 6.67 25270.6(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 87 89 | General Facility Requirements |  | APSA program fee paid | 21 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to pay the APSA Program fee. |  |  | OBSERVATION: Fee for the APSA Program were not paid as required by statute. CORRECTIVE ACTION: Pay the APSA Program fee. | [6 empty] | Yes | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030036 |  |  | Permanently closed tanks | Failure to properly close tanks when making a claim of "permanently closed." | HSC 6.67 25270.4.5(a); 40 CFR 1 112.1(b)(3), 112.2 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 88 90 | General Facility Requirements |  | All/any permanently closed tanks are properly closed under the definition in 40 CFR 112.2 | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly permanently close all/any tanks under the definition of “Permanently Closed “ in 40 CFR 112.2. 1) All liquid and sludge has been removed from each container and connecting line. 2) All connecting lines and piping have been disconnected from the container blanked off. 3) All valves have been closed and locked. 4) Conspicuous signs have been posted on the container stating that it is a permanently closed container and denoting the date of closure. |  |  | OBSERVATION: Owner/Operator failed to comply with one or more of the following permanent closure requirements: 1. All liquid and sludge has been removed from each container and connecting line; 2. All connecting lines and piping have been disconnected from the container blanked off; 3. All valves have been closed and locked; 4. Conspicuous signs have been posted on the container stating that it is a permanently closed container and denoting the date of closure. CORRECTIVE ACTION: Tanks that are not being used and are not addressed in the SPCC plan must either be included in your plan or meet the permanent closure requirements noted above. Provide verification to the CUPA of proper closure of the tanks. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010044 |  |  | Substantial Harm Criteria | Failure to complete and maintain at the facility the Substantial Harm Criteria certification form when owner or operator determines that the facility could not be reasonably expected to cause substantial harm to the environment. | HSC 6.67 25270.4.5(a); 40 CFR 1 112.20(e) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 89 91 | General Facility Requirements |  | Substantial Harm Criteria certification maintained at the facility as required | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to complete and maintain at the facility the Substantial Harm Criteria certification form when owner or operator determines that the facility could not be reasonably expected to cause substantial harm to the environment. |  |  | OBSERVATION: Failure to complete and maintain at the facility the Substantial Harm Criteria certification form when the owner or operator determined that the facility could not be reasonably expected to cause substantial harm to the environment. CORRECTIVE ACTION: Complete and maintain at the facility the Substantial Harm Criteria certification form. | [6 empty] | No | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4010 |  |  | APSA-Administration/Documentation - General | Administration/Documentation - General | HSC 6.67 Multiple Sections; 40 CFR 1 112 | 07/01/2011 | 2099-12-31 | 07/01/2011 | Revised | 90 92 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Administration/Documentation | 4015 |  |  | APSA-Administration/Documentation - General Local Ordinance | Administration/Documentation - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 91 93 | General Facility Requirements |  | Administration/Documentation - General Local Ordinance | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Training | 4020 |  |  | Training - General | Training - General | HSC 6.67 Multiple Sections; 40 CFR 1 112 | 07/01/2011 | 2099-12-31 | 07/01/2011 | Revised | 92 94 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Training | 4025 |  |  | APSA-Training - General Local Ordinance | Training - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 93 95 | General Facility Requirements |  | Training - General Local Ordinance | 34 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4030 |  |  | APSA-Operations/Maintenance - General | Operations/Maintenance - General | HSC 6.67 Multiple Sections; 40 CFR 1 112 | 07/01/2011 | 2099-12-31 | 07/01/2011 | Revised | 94 96 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Operations/Maintenance | 4035 |  |  | APSA-Operations/Maintenance - General Local Ordinance | Operations/Maintenance - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 95 97 | General Facility Requirements |  | Operations/Maintenance - General Local Ordinance | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Release/Leaks/Spills | 4040 |  |  | APSA-Release/Leaks/Spills - General | Release/Leaks/Spills - General | HSC 6.67 Multiple Sections; 40 CFR 1 112 | 07/01/2011 | 2099-12-31 | 07/01/2011 | Revised | 96 98 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Release/Leaks/Spills | 4045 |  |  | APSA-Release/Leaks/Spills - General Local Ordinance | Release/Leaks/Spills - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 97 99 | General Facility Requirements |  | Release/Leaks/Spills - General Local Ordinance | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 4050 |  |  | APSA-Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | HSC 6.67 Multiple Sections; 40 CFR 1 112 | 07/01/2011 | 2099-12-31 | 07/01/2011 | Revised | 98 100 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes | Yes | Yes | Yes
APSA Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 4055 |  |  | APSA-Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 99 101 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes

## HW
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | HazWaste SQG | HazWaste LQG
Hazardous Waste Generator | Administration/Documentation | 3010002 |  |  | Hazardous Waste Generator: Identification Number | Failure to obtain an Identification Number prior to treating, storing, disposing of, transporting or offering for transportation any hazardous waste. | 22 CCR 12 66262.12 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 1 | Recordkeeping/ Documentation | ID Number | Obtained an Identification Number (unless exempted HSC 25143.13) | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to obtain an Identification Number prior to treating, storing, disposing of, transporting or offering for transportation any hazardous waste. |  |  | OBSERVATION: The generator has not obtained an Identification Number to manage hazardous waste. A hazardous waste generator shall not treat, store, dispose of, transport or offer for transportation, hazardous waste without obtaining an Identification Number. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you have obtained an Identification Number. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030040 |  |  | Large Quantity Generator: Contingency Plan | Failure to prepare and implement a written Contingency Plan to minimize hazards to human health or the environment from fires, explosions, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.51 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 2 | Recordkeeping/ Documentation | Contingency Plan | Contingency Plan prepared and implemented | 41 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to prepare and implement a written Contingency Plan to minimize hazards to human health or the environment from fires, explosions, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water. |  |  | OBSERVATION: Facility failed to prepare an Contingency Plan. The owner or operator shall prepare an Emergency Response Plan designed to minimize hazards to human health or the environment from fires, explosions, or any unplanned release of hazardous waste to air, soil, or surface water. CORRECTIVE ACTION: Immediately prepare an Contingency Plan and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010024 |  |  | Large Quantity Generator: Contingency Plan Copies | Failure to maintain a copy of the contingency plan and all its revisions at the facility and to submit a copy to all local police departments, fire departments, hospitals, and State and local emergency response teams that may be called upon to provide emergency services. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.53 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 3 | Recordkeeping/ Documentation | Contingency Plan | Contingency Plan and all revisions maintained at the facility | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain a copy of the contingency plan and all its revisions at the facility and to submit a copy to all local police departments, fire departments, hospitals, and State and local emergency response teams that may be called upon to provide emergency services. |  |  | OBSERVATION: A copy of the Contingency Plan is not maintained at the facility. CORRECTIVE ACTION: Locate a copy of the Contingency Plan, maintain it at the facility, and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010023 |  |  | Large Quantity Generator: Contingency Plan Emergency Action Plan | Failure to include all of the following in the Contingency Plan: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. (If the owner or operator has already prepared a Spill Prevention, Control, and Countermeasures (SPCC) Plan or some other emergency or contingency plan, the owner or operator need only amend that plan to incorporate hazardous waste management provisions.) | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.52 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 4 | Recordkeeping/ Documentation | Contingency Plan | Contingency plan contains all required content | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include all of the following in the Contingency Plan: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. (If the owner or operator has already prepared a Spill Prevention, Control, and Countermeasures (SPCC) Plan or some other emergency or contingency plan, the owner or operator need only amend that plan to incorporate hazardous waste management provisions.) |  |  | OBSERVATION: The Contingency Plan does not contain [LIST MISSING CONTENT]. CORRECTIVE ACTION: Revise the Contingency Plan to include all the content required by 22 CCR 15 66265.52 and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Training | 3020001 |  |  | Small Quantity Generator: Employee Training | Failure to ensure that all employees are thoroughly familiar with proper waste handling and emergency procedures, relevant to their responsibilities during normal facility operations and emergencies. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(5)(iii) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 5 | Recordkeeping/ Documentation | Training | Employees thoroughly familiar with all waste handling and emergency procedures | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to ensure that all employees are thoroughly familiar with proper waste handling and emergency procedures, relevant to their responsibilities during normal facility operations and emergencies. |  |  | OBSERVATION: Employees are not thoroughly familiar with proper waste handling and emergency procedures as demonstrated by the number and/or type of hazardous waste violations observed at the time of inspection. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that employees have been properly trained. | [6 empty] | Yes | No
Hazardous Waste Generator | Training | 3020002 |  |  | Large Quantity Generator: Employee Hazardous Waste Training | Failure to provide employees with hazardous waste training program of class room instructions or on-the-job training within 180 days after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. Training records on current personnel shall be kept until closure of the facility and for former employees the record shall be kept for at least three years from the date the employee last worked at the facility. The records shall include the following: the job title for each position at the facility related to hazardous waste management, and the name of the employee filling each job; a written job description for each position, duties of facility personnel assigned to each position, and a written description of the type and amount of both introductory and continuing training that will be given to each person filling a position. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.16 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 6 | Recordkeeping/ Documentation | Training | Facility personnel are trained annually and maintain required documentation until closure | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to provide employees with hazardous waste training program of class room instructions or on-the-job training within 180 days after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. Training records on current personnel shall be kept until closure of the facility and for former employees the record shall be kept for at least three years from the date the employee last worked at the facility. The records shall include the following: the job title for each position at the facility related to hazardous waste management, and the name of the employee filling each job; a written job description for each position, duties of facility personnel assigned to each position, and a written description of the type and amount of both introductory and continuing training that will be given to each person filling a position. |  |  | OBSERVATION: As demonstrated by the number and type of hazardous waste violations observed at the time of inspection, personnel are not adequately trained to perform their duties in a way that ensures the facility's compliance with hazardous waste laws and regulations, and/or employee training records have not been kept or do not contain all required information, or employees were not trained within 180 days after their hire date or assignment to a new facility or position, and annually thereafter. CORRECTIVE ACTION: Conduct training with applicable personnel and document it according to the requirements of 22 CCR 15 66265.16(d). Submit a copy of the documentation to the CUPA. | OBSERVATION: Documented training of personnel was not available at the time of inspection. CORRECTIVE ACTION: Locate training documentation or conduct training with applicable personnel and document it. Submit a copy of the training documentation to the CUPA. | [5 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010007 |  |  | Hazardous Waste Generator: Preparation of the Hazardous Waste Manifest | Failure to prepare a Uniform Hazardous Waste Manifest and, if necessary, a Continuation Sheet, before the transport of a hazardous waste off-site for transfer, treatment, storage, or disposal. | 22 CCR 12 66262.20 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 7 | Recordkeeping/ Documentation | Manifest | Prepared a Uniform Hazardous Waste Manifest for transportation of hazardous waste | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to prepare a Uniform Hazardous Waste Manifest and, if necessary, a Continuation Sheet, before the transport of a hazardous waste off-site for transfer, treatment, storage, or disposal. |  |  | OBSERVATION: [LIST WASTE] was transported by [LIST TRANSPORTER] to [LIST LOCATION] and a Uniform Hazardous Waste Manifest was not prepared. CORRECTIVE ACTION: For future shipments of the above noted waste, prepare a Uniform Hazardous Waste Manifest prior to being transported to, or offered for transportation to, an off-site facility. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010008 |  |  | Hazardous Waste Generator: Hazardous Waste Manifest Completeness | Failure to properly complete the Uniform Hazardous Waste Manifest. | 22 CCR 12 66262.23(a) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 8 | Recordkeeping/ Documentation | Manifest | Properly completed all Uniform Hazardous Waste Manifests | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to properly complete the Uniform Hazardous Waste Manifest. |  |  | OBSERVATION: The Uniform Hazardous Waste Manifest [MANIFEST #] does not contain [LIST MISSING REQUIREMENTS]. CORRECTIVE ACTION: Contact the DTSC to make necessary corrections to the manifests and submit a copy to the CUPA. | OBSERVATION: The Uniform Hazardous Waste Manifest [MANIFEST #] contained the following errors: [LIST ERRORS]. CORRECTIVE ACTION: Contact the DTSC to make necessary corrections to the manifests and submit a copy to the CUPA. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010030 |  |  | Small Quantity Generator: Hazardous Waste Manifest Exception Reporting | Failure to determine the status of any hazardous waste if a signed copy of the manifest isn’t received within 35 days of the date the waste was accepted by the initial transporter and/or to submit an Exception Report to DTSC if a signed copy of the manifest isn’t received within 60 days of the date the waste was accepted by the initial transporter. | 22 CCR 12 66262.42 (a),(c), (d); HSC 6.5 25123.3(h)(2) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 9 | Recordkeeping/ Documentation | Manifest | Completed all Uniform Hazardous Waste Manifest exception reporting requirements | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to determine the status of any hazardous waste if a signed copy of the manifest isn’t received within 35 days of the date the waste was accepted by the initial transporter and/or to submit an Exception Report to DTSC if a signed copy of the manifest isn’t received within 60 days of the date the waste was accepted by the initial transporter. |  |  | Observation: The generator failed to determine the status of a uniform hazardous waste manifested shipment within 35 days from the date the waste was shipped. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the generator has determined the status of the hazardous waste manifest shipment for [LIST MANIFESTS]. | OBSERVATION: The generator failed to file an exception report with the DTSC after not receiving a destination facility signed copy of the uniform hazardous waste manifest within 60 days of the waste shipment date. CORRECTIVE ACTION: Either locate a copy of the missing manifests or prepare and submit an exception report to DTSC (DTSC Report Repository; Generator Information Services Section; P.O. Box 806; Sacramento, CA 95812-0806). Submit copies to the CUPA. | [5 empty] | Yes | No
Hazardous Waste Generator | Administration/Documentation | 3010009 |  |  | Large Quantity Generator: Hazardous Waste Manifest Exception Reporting | Failure to determine the status of any hazardous waste if a signed copy of the manifest isn’t received within 35 days of the date the waste was accepted by the initial transporter and/or to submit an Exception Report to DTSC if a signed copy of the manifest isn’t received within 45 days of the date the waste was accepted by the initial transporter. | 22 CCR 12 66262.42(a), (b), (d); HSC 25160(b)(3) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 10 | Recordkeeping/ Documentation | Manifest | Completed all Uniform Hazardous Waste Manifest exception reporting requirements | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to determine the status of any hazardous waste if a signed copy of the manifest isn’t received within 35 days of the date the waste was accepted by the initial transporter and/or to submit an Exception Report to DTSC if a signed copy of the manifest isn’t received within 45 days of the date the waste was accepted by the initial transporter. |  |  | Observation: The generator failed to determine the status of a uniform hazardous waste manifested shipment within 35 days from the date the waste was shipped, and/or to submit an exception report to DTSC if a signed copy of the manifest isn't received within 45 days of the date the waste was accepted by the initial transporter. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the generator has determined the status of the hazardous waste manifest shipment for [LIST MANIFESTS], or a copy of the exception report submitted to DTSC, if applicable. | OBSERVATION: The generator failed to file an exception report with the DTSC after not receiving a destination facility signed copy of the uniform hazardous waste manifest within 45 days of the waste shipment date. CORRECTIVE ACTION: Either locate a copy of the missing manifests or prepare and submit an exception report to DTSC (DTSC Report Repository; Generator Information Services Section; P.O. Box 806; Sacramento, CA 95812-0806). Submit copies to the CUPA. | [5 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010010 |  |  | Hazardous Waste Generator: Hazardous Waste Disposal Documentation | Failure to keep a copy of each properly signed manifest for at least three years from the date the waste was accepted by the initial transporter. The manifest signed at the time the waste was accepted for transport shall be kept until receiving a signed copy from the designated facility which received the waste. | 22 CCR 12 66262.40(a) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 11 | Recordkeeping/ Documentation | Manifest | Signed copy of Uniform Hazardous Waste Manifest kept for 3 years | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to keep a copy of each properly signed manifest for at least three years from the date the waste was accepted by the initial transporter. The manifest signed at the time the waste was accepted for transport shall be kept until receiving a signed copy from the designated facility which received the waste. |  |  | OBSERVATION: Uniform Hazardous Waste Manifests for [LIST HAZARDOUS WASTES] were not available at the time of inspection. CORRECTIVE ACTION: Locate a copy of all manifests for [LIST HAZARDOUS WASTES] and submit copies to the CUPA. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010011 |  |  | Hazardous Waste Generator: Hazardous Waste Manifest Not Sent to DTSC | Failure to send a legible copy of each hazardous waste manifest that originated in paper form to the Department within 30 days of each shipment of hazardous waste. | 22 CCR 12 66262.23(a)(4); HSC 25160(b)(1)(C) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 12 | Recordkeeping/ Documentation | Manifest | Sent a legible copy of each Uniform Hazardous Waste Manifest to the DTSC within 30 days of shipment | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to send a legible copy of each hazardous waste manifest that originated in paper form to the Department within 30 days of each shipment of hazardous waste. |  |  | OBSERVATION: The generator has not sent a legible copy of each Uniform Hazardous Waste Manifest, that originated in paper form, to the DTSC within 30 days of shipment. CORRECTIVE ACTION: Send a copy of all hazardous waste manifests that originated in paper form to the DTSC and submit a statement to the CUPA demonstrating compliance. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010013 |  |  | Hazardous Waste Generator: Consolidated Manifest | Failure of a generator of hazardous waste that meets the conditions to be transported on a consolidated manifest to comply with one or more of the required consolidated manifesting procedures and retain copies of receipts for three years. | HSC 6.5 25160.2 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 13 | Recordkeeping/ Documentation | Manifest | All consolidated manifest requirements are met | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of a generator of hazardous waste that meets the conditions to be transported on a consolidated manifest to comply with one or more of the required consolidated manifesting procedures and retain copies of receipts for three years. |  |  | OBSERVATION: Owner/Operator failed to comply with one or more consolidated manifesting requirements. CORRECTIVE ACTION: Ensure that all wastes transported on a consolidated manifest meet all consolidated manifest requirements, and maintain copies of manifests for three years. | OBSERVATION: Consolidated manifest receipts for [LIST HAZARDOUS WASTES] were observed missing the following required information [insert missing required regulatory component]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating how all consolidated manifest receipts will be properly completed in the future. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010015 |  |  | Hazardous Waste Generator: Used Oil Certification Form | Failure to record in an operating log and retain for three years the following information for each shipment of recycled or exempted oil: 1) The name and address of the used oil recycling facility or generator claiming the oil meets the requirements of HSC 6.5 25250.1. 2) The name and address of the facility receiving the shipment. 3) The quantity of oil delivered. 4) The date of shipment or delivery. 5) A cross-reference to the records and documentation required under HSC 6.5 25250.1. | HSC 6.5 25250.1(c); 25250.18(a); 25250.19(c) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 14 | Recordkeeping/ Documentation | Manifest | Exempt used oil management operating log records are retained for 3 years | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to record in an operating log and retain for three years the following information for each shipment of recycled or exempted oil: 1) The name and address of the used oil recycling facility or generator claiming the oil meets the requirements of HSC 6.5 25250.1. 2) The name and address of the facility receiving the shipment. 3) The quantity of oil delivered. 4) The date of shipment or delivery. 5) A cross-reference to the records and documentation required under HSC 6.5 25250.1. |  |  | OBSERVATION: The generator failed to retain an operating log recording the management of exempt used oil. CORRECTIVE ACTION: Submit documentation to the CUPA that shows the generator has implemented an adequate operating log recording the management of exempt used oil. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010014 |  |  | Hazardous Waste Generator: Lead Battery Disposal Documentation | Failure to retain for at least three years a legible copy of each manifest or bill of lading which identifies spent lead-acid storage batteries shipped to a person who stores the batteries or who uses, reuses, recycles or reclaims the batteries or their components. | 22 CCR 16 66266.81(a)(4)(B) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 15 | Recordkeeping/ Documentation | Manifest | Owner/Operator retained copy of manifest or bill of lading for spent lead acid batteries for 3 years | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to retain for at least three years a legible copy of each manifest or bill of lading which identifies spent lead-acid storage batteries shipped to a person who stores the batteries or who uses, reuses, recycles or reclaims the batteries or their components. |  |  | OBSERVATION: Manifests or bills of lading for spent lead acid batteries recording the shipments off site were not retained at the facility for the past three years. CORRECTIVE ACTION: Obtain copies of all bills of lading for lead-acid batteries recording shipments off site over the past three years. Submit copies of the bills of lading for the past year to the CUPA. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030005 |  |  | Hazardous Waste Generator: Hazardous Waste Determination | Failure to determine if wastes generated are hazardous waste by using generator knowledge or applying testing method. | 22 CCR 12 66262.11 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 16 | Recordkeeping/ Documentation | Waste Determination | Determined if waste generated is hazardous waste | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to determine if wastes generated are hazardous waste by using generator knowledge or applying testing method. |  |  | OBSERVATION: The [WASTE] located in the [LOCATION] was observed being [DESCRIBE: HOW DISPOSED OF / HOW TREATED AND DISPOSED OF / ACCUMULATED] and a proper waste determination has not been made. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [WASTE] has been properly characterized to determine if it is a hazardous waste. If determined to be hazardous submit a manifest/receipt documenting proper disposal and a statement demonstrating how you will manage it in the future. | OBSERVATION: Finely divided metal generated from [DESCRIBE PROCESS] are being [RECYCLED AS SCRAP METAL/ DISPOSED OF TO THE TRASH]. Finely divided metal less than 100 microns in size does not meet the definition of scrap metal. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the finely divided metal has been properly characterized to determine if it is a hazardous waste. If determined to be hazardous submit manifests/receipts documenting proper disposal and a statement demonstrating how you will manage it in the future. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030053 |  |  | Hazardous Waste Generator: Maintaining records of test result for three years | Failure to keep records of any test results, waste analyses, or other determinations made in accordance with section 66262.11 for at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. | 22 CCR 12 66262.40(c) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 17 | Recordkeeping/ Documentation | Waste Determination | Kept records of any test results, waste analyses, or other determinations | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to keep records of any test results, waste analyses, or other determinations made in accordance with section 66262.11 for at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. |  |  | Observation: The hazardous waste determination documentation for [LIST WASTE] was not available at the time of inspection for the previous 3 years from the date the waste stream was last managed on site or sent off site for treatment. ORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [WASTE] has been properly characterized to determine if it is a hazardous waste. If determined to be hazardous submit a manifest/receipt documenting proper disposal and a statement demonstrating how you will manage it in the future. | OBSERVATION: The [WASTE] located in the [LOCATION] was observed being [DESCRIBE: HOW DISPOSED OF / HOW TREATED AND DISPOSED OF / ACCUMULATED] and a proper waste determination has not been made. CORRECTIVE ACTION: Immediately cease [DESCRIBE: HOW DISPOSED OF / HOW TREATED AND DISPOSED OF] of [WASTE]. Submit documentation to the CUPA demonstrating that the [WASTE] has been properly characterized to determine if it is a hazardous waste. If determined to be hazardous submit a manifest/receipt documenting proper disposal and a statement demonstrating how you will manage it in the future. Keep the test results, waste analyses, or other determinations at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030006 |  |  | Hazardous Waste Generator: Land Disposal Restriction | Failure to determine if the waste has to be treated before it can be land disposed and retain the documentation at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. | 22 CCR 12 66262.34(a)(4); 22 CCR 18 66268.7(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 18 | Recordkeeping/ Documentation | Waste Determination | Determined land disposal restrictions for hazardous waste | 57 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to determine if the waste has to be treated before it can be land disposed and retain the documentation at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. |  |  | OBSERVATION: Land Disposal Restriction (LDR) documentation for [HAZARDOUS WASTE] was not available at the time of inspection. CORRECTIVE ACTION: Submit LDR documentation for [HAZARDOUS WASTE] to this department. Retain the documentation at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010036 |  |  | General: Electronic data | Failure to report, and report accurately, program data (such as hazardous waste generation activities) electronically. | 27 CCR 1 15188(b), (c); HSC 6.11 25404(e)(4) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Existing | 19 | Recordkeeping/ Documentation | Reporting | Program data reported electronically, and accurately, when required | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to report, and report accurately, program data (such as hazardous waste generation activities) electronically. |  |  | OBSERVATION: Owner/Operator failed to report program data electronically into CERS, or reported information incorrectly. CORRECTIVE ACTION: Complete all required reporting into CERS. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010016 |  |  | Hazardous Waste Generator: Excluded Recyclable Materials Report | Failure of any person who recycles more than 100 kilograms per month of recyclable material under a claim that the material qualifies for exclusion or exemption, to submit recyclable materials report every two years. | HSC 6.5 25143.10 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 20 | Recordkeeping/ Documentation | Reporting | Submitted Recyclable Materials Report every two years | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of any person who recycles more than 100 kilograms per month of recyclable material under a claim that the material qualifies for exclusion or exemption, to submit recyclable materials report every two years. |  |  | OBSERVATION: The generator was observed recycling more than 100 kilograms per month of hazardous waste and has not submitted the Recyclable Materials Report in CERS or has failed to submit it every two years. CORRECTIVE ACTION: Complete the recyclable materials report for the most recent reporting period and submit a copy in CERS. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010035 |  |  | Remote Consolidation: Notification | Failure to annually submit notification of generator’s intent to remotely consolidate hazardous waste. | HSC 6.5 25110.10(d) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 21 | Recordkeeping/ Documentation | Reporting | Remote Waste Consolidation Site Annual Notification submitted | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failed to submit Remote Waste Consolidation Site Annual Notification. |  |  | OBSERVATION: The generator consolidates hazardous waste from a remote site and has not submitted the Remote Waste Consolidation Site Annual Notification to the CUPA. CORRECTIVE ACTION: Complete and submit the Remote Waste Consolidation Site Annual Notification to the CUPA through CERS. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010018 |  |  | Large Quantity Generator: Source Reduction Evaluation Review and Plan | Failure of a generator to conduct, when required, a source reduction evaluation review and plan every four years, and/or failure of the review and plan to contain all required information. | 22 CCR 31 67100.7, 67100.8; HSC 6.5 25244.19 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 22 | Recordkeeping/ Documentation | Reporting | LQG conducted a source reduction evaluation review and plan every four years | 76 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a generator to conduct, when required, a source reduction evaluation review and plan every four years, and/or failure of the review and plan to contain all required information. |  |  | OBSERVATION: Failure of the Owner/Operator to conduct a source reduction evaluation review and plan every four years, or the review and/or plan failed to contain all required information. CORRECTIVE ACTION: Conduct a source reduction evaluation review and plan at this time and every four years thereafter, and ensure review and plan contain all required information. Submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010019 |  |  | Large Quantity Generator: Summary Progress Report | Failure of a large quantity generator to prepare a summary progress report every four years, using DTSC’s Form # 1262 (3/99) titled "Summary Progress Report". | 22 CCR 31 67100.9 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 23 | Recordkeeping/ Documentation | Reporting | LQG prepared a Summary Progress Report using DTSC form #1262 every four years | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a large quantity generator to prepare a summary progress report every four years, using DTSC’s Form # 1262 (3/99) titled "Summary Progress Report". |  |  | OBSERVATION: The generator failed to prepare a summary progress report every four years. CORRECTIVE ACTION: Prepare a summary progress report and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010021 |  |  | Large Quantity Generator: Source Reduction Implementation | Failure to adequately complete, and maintain for review, all requirements of the source reduction evaluation review and plan (SB-14). | 22 CCR 31 67100.5; HSC 6.5 25244.19, 25244.21 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 24 | Recordkeeping/ Documentation | Reporting | LQG completed all source reduction evaluation review and plan requirements | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately complete, and maintain for review, all requirements of the source reduction evaluation review and plan (SB-14). |  |  | OBSERVATION: A source reduction evaluation review and plan with all the required information has not been completed and maintained for review. CORRECTIVE ACTION: Complete a source reduction report with all the required information and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050001 |  |  | Hazardous Waste Generator: Hazardous Waste Not Transported by Registered Hauler | Failure to use a DTSC registered hazardous waste transporter to transport hazardous waste. | HSC 6.5 25163(a) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 25 | Hazardous Waste Management | Disposal | Registered hazardous waste transporter used to transport hazardous waste | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to use a DTSC registered hazardous waste transporter to transport hazardous waste. |  |  | OBSERVATION: Owner/Operator failed to use a DTSC registered hazardous waste transporter to transport hazardous waste. CORRECTIVE ACTION: Ensure all hazardous waste is transported by a DTSC registered hazardous waste transporter and submit a statement to the CUPA indicating this will be how all hazardous waste will be transported in the future. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050002 |  |  | Hazardous Waste Generator: Improper Disposal of Hazardous Waste | Failure to dispose of hazardous waste at a facility which has a permit from DTSC or disposing of hazardous waste at any point which is not authorized. | HSC 6.5 25189.5(a) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 26 | Hazardous Waste Management | Disposal | Disposed of hazardous waste at an authorized location | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to dispose of hazardous waste at a facility which has a permit from DTSC or disposing of hazardous waste at any point which is not authorized. |  |  | OBSERVATION: Owner/Operator failed to dispose of hazardous waste at a facility which has a permit from DTSC or disposed of hazardous waste at a point which is not authorized pursuant to HSC chapter 6.5. CORRECTIVE ACTION: Immediately discontinue disposing of hazardous waste at any facility not permitted by DTSC or to any point which is not authorized pursuant to HSC chapter 6.5. Submit a statement to the CUPA indicating improperly disposed of hazardous waste has been properly managed, and that all hazardous wastes will only be disposed at facilities permitted by DTSC in the future. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Release/Leaks/Spills | 3040002 |  |  | Hazardous Waste Generator: Quarantine Order | No person shall remove, transfer, or dispose of the hazardous waste until permission for removal, transfer, or disposal is given by an authorized agent. Failure to obtain permission from an authorized agent or court to remove, transfer, or dispose of hazardous waste that is under quarantine. | HSC 6.5 25187.6 | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 27 | Hazardous Waste Management | Disposal | Quarantined HW not removed,/ transferred, or /disposed without permission by authorized agent or a court | 104 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to obtain permission from an authorized agent or court to remove, transfer, or dispose of hazardous waste that is under quarantined. |  |  | OBSERVATION: Quarantined HW was removed, transferred, or disposed of without permission by authorized agent or a court. CORRECTIVE ACTION: Submit a statement to the CUPA demonstrating that you have read the quarantine notice and trained all applicable employees on the requirements. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030009 |  |  | Generator of < 100 kg/mth: Accumulation Time Exceeded (180/270, or 90 Days for Acutely/Extremely) | Failure to send hazardous waste offsite for treatment, storage, or disposal within 180 days (or 270 days if waste is transported over 200 miles) of when the accumulation period begins*, for a generator who generates less than 100 kilogram per month if all of the following conditions are met: (1) The quantity of hazardous waste accumulated onsite never exceeds 6,000 kilograms. (2) The generator complies with the requirements of 40 Code of Federal Regulations section 262.34(d), (e) and (f). (3) The generator does not hold acutely hazardous waste or extremely hazardous waste in an amount greater than one kilogram for more than 90 days. *The accumulation period begins when the generator has accumulated 100 kilograms of hazardous waste or one kilogram of extremely hazardous waste or acutely hazardous waste. | 22 CCR 12 66262.34(d); HSC 6.5 25123.3(c), 25123.3(h)(1) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 28 | Hazardous Waste Management | Accumulation Time Limits | <100 kg/mth generator disposed of waste within 180 days of accumulation start date (90 days for AHW) | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to send hazardous waste offsite for treatment, storage, or disposal within 180 days (or 270 days if waste is transported over 200 miles) of when the accumulation period begins*, for a generator who generates less than 100 kilogram per month if all of the following conditions are met: (1) The quantity of hazardous waste accumulated onsite never exceeds 6,000 kilograms. (2) The generator complies with the requirements of 40 Code of Federal Regulations section 262.34(d), (e) and (f). (3) The generator does not hold acutely hazardous waste or extremely hazardous waste in an amount greater than one kilogram for more than 90 days. *The accumulation period begins when the generator has accumulated 100 kilograms of hazardous waste or one kilogram of extremely hazardous waste or acutely hazardous waste. |  |  | OBSERVATION: Owner/Operator who is a generator of <100 kg/mth failed to send hazardous waste offsite for treatment, storage, or disposal within 180/270 days of accumulating 100 kilograms, or within 90 days of accumulating 1 kg of extremely/acutely hazardous waste. CORRECTIVE ACTION: Dispose of hazardous waste and submit a copy of the manifest/receipt to the CUPA. Ensure that hazardous waste is not stored for more than 180/270 days after the accumulation period begins, and that acute/extremely hazardous waste is not stored for more than 90 days after accumulating 1 kilogram. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030010 |  |  | Small Quantity Generator: Time Exceeded for Hazardous Waste Conditional Accumulation (180 Days) | Failure to send hazardous waste offsite for treatment, storage, or disposal within 180 days (or 270 days if waste is transported over 200 miles) for a generator who generates less than 1000 kilograms per month if all of the following conditions are met: (1) The quantity of hazardous waste accumulated onsite never exceeds 6,000 kilograms. (2) The generator complies with the requirements of 40 Code of Federal Regulations section 262.34(d), (e) and (f). (3) The generator does not hold acutely hazardous waste or extremely hazardous waste in an amount greater than one kilogram for more than 90 days. | 22 CCR 12 66262.34(d); HSC 6.5 25123.3(h)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 29 | Hazardous Waste Management | Accumulation Time Limits | Disposed of hazardous waste within 180 days of accumulation start date | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to send hazardous waste offsite for treatment, storage, or disposal within 180 days (or 270 days if waste is transported over 200 miles) for a generator who generates less than 1000 kilograms per month if all of the following conditions are met: (1) The quantity of hazardous waste accumulated onsite never exceeds 6,000 kilograms. (2) The generator complies with the requirements of 40 Code of Federal Regulations section 262.34(d), (e) and (f). (3) The generator does not hold acutely hazardous waste or extremely hazardous waste in an amount greater than one kilogram for more than 90 days. |  |  | OBSERVATION: Owner/Operator is a small quantity generator and failed to send hazardous waste offsite for treatment, storage, or disposal within 180 days (or 270 days if waste is transported over 200 miles), or has failed to comply with the conditions of CCR 66262.34(d) and has stored hazardous waste over 90 days. CORRECTIVE ACTION: Dispose of hazardous waste that has been stored over the applicable time limit and provide documentation that the violation has been corrected. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030012 |  |  | Large Quantity Generator: Hazardous Waste Accumulation Time Exceeded | Failure to send hazardous waste offsite for treatment, storage, or disposal within 90 days for a generator who generates 1000 kilograms or more per month. | 22 CCR 12 66262.34(a), (c); HSC 6.5 25123.3(b)(1) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 30 | Hazardous Waste Management | Accumulation Time Limits | Disposed of hazardous waste within 90 days of accumulation start date | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to send hazardous waste offsite for treatment, storage, or disposal within 90 days for a generator who generates 1000 kilograms or more per month. |  |  | OBSERVATION: Owner/Operator failed to send hazardous waste offsite for treatment, storage, or disposal within 90 days of accumulation start date. CORRECTIVE ACTION: Dispose of hazardous waste and submit a copy of the manifest/receipt to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030057 |  |  | Hazardous Waste Generator: Satellite Accumulation | Failure to meet the following conditions of satellite accumulation regulations: • Accumulate up to 55 gallons of hazardous waste or one quart of acute hazardous waste at or near the initial point of accumulation which was under the control of the operator. • Total time hazardous waste can be accumulated onsite in any generator accumulation area is either one year from the initial date of accumulation, or 90/180/270 days (depending on size of generator and distance transported) from the date on which the quantity limitation of 55 gallons of hazardous waste or one quart of acutely hazardous waste is reached, whichever comes first. • The generator complies with section 66265.171, 66265.172, and 66265.173(a). • The container must be clearly marked with the initial date that hazardous waste is first placed in the container and labelled with the words “Hazardous Waste” including specified information • Container must be labelled with the date the satellite accumulation limit is reached and moved within three days after reaching the 55 gallon (or one quart) limit to a central accumulation area • 55 gallons (or one quart of acute hazardous waste) of waste per process may be accumulated | 22 CCR 12 66262.34(e) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 31 | Hazardous Waste Management | Accumulation Time Limits | Met all requirements for hazardous waste satellite accumulation | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to meet the following conditions of satellite accumulation regulations: • Accumulate up to 55 gallons of hazardous waste or one quart of acute hazardous waste at or near the initial point of accumulation which was under the control of the operator. • Total time hazardous waste can be accumulated onsite in any generator accumulation area is either one year from the initial date of accumulation, or 90/180/270 days (depending on size of generator and distance transported) from the date on which the quantity limitation of 55 gallons of hazardous waste or one quart of acutely hazardous waste is reached, whichever comes first. • The generator complies with section 66265.171, 66265.172, and 66265.173(a). • The container must be clearly marked with the initial date that hazardous waste is first placed in the container and labelled with the words “Hazardous Waste” including specified information • Container must be labelled with the date the satellite accumulation limit is reached and moved within three days after reaching the 55 gallon (or one quart) limit to a central accumulation area • 55 gallons (or one quart of acute hazardous waste) of waste per process may be accumulated |  |  | OBSERVATION: Failure of the Owner/Operator to comply with one or more satellite accumulation requirements. {Describe as needed} CORRECTIVE ACTION: Ensure that all hazardous wastes being accumulated pursuant to satellite accumulation meet all applicable requirements and submit documentation of compliance to the CUPA. {Describe specific corrections as needed} | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030007 |  |  | Hazardous Waste Generator: Hazardous Waste Labeling Standards | Failure to properly label hazardous waste accumulation containers and portable tanks with the following requirements: "Hazardous Waste", name and address of the generator, physical and chemical characteristics of the Hazardous Waste, and starting accumulation date. | 22 CCR 12 66262.34(f) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 32 | Hazardous Waste Management | Container Management | Labeled all containers or portable tanks containing hazardous waste | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly label hazardous waste accumulation containers and portable tanks with the following requirements: "Hazardous Waste", name and address of the generator, physical and chemical characteristics of the Hazardous Waste, and starting accumulation date. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed without a hazardous waste label. CORRECTIVE ACTION: Submit a photo to the CUPA demonstrating that the container listed above has been properly labeled. | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed without the following information on the label: [LIST MISSING INFORMATION]. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that the container listed above has been properly labeled. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030013 |  |  | Small Quantity Generator: Container in Poor Condition or Damaged | Failure to accumulate hazardous waste in a container that is in good condition. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(1), 262.34(d)(2), 265.171 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 33 | Hazardous Waste Management | Container Management | Accumulated hazardous waste in containers that are in good condition | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to accumulate hazardous waste in a container that is in good condition. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [LIST HAZARDOUS WASTE] located in the [LOCATION] was observed [DESCRIBE CONDITION]. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is in good condition or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030015 |  |  | Small Quantity Generator: Hazardous Waste Container Incompatible with Material Stored | Failure to accumulate or store hazardous waste in container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(2), 265.172 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 34 | Hazardous Waste Management | Container Management | Hazardous waste accumulated in lined and/or compatible containers | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to accumulate or store hazardous waste in container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed in an [UNLINED / INCOMPATIBLE] container. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is compatible with the hazardous waste or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030017 |  |  | Small Quantity Generator: Open Hazardous Waste Containers | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(2), 265.173 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 35 | Hazardous Waste Management | Container Management | Containers of hazardous waste closed except when adding or removing waste | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed open. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that the container listed above has been properly closed. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030019 |  |  | Small Quantity Generator: Weekly Hazardous Waste Storage Area Inspection | Failure to inspect hazardous waste storage areas at least weekly and look for leaking and deteriorating containers. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(2), 265.174 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 36 | Hazardous Waste Management | Container Management | Inspects all hazardous waste storage areas at least weekly | 58 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to inspect hazardous waste storage areas at least weekly and look for leaking and deteriorating containers. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed [LEAKING / DETERIORATING]. CORRECTIVE ACTION: Submit a copy of the inspection log to the CUPA demonstrating that the hazardous waste storage area is being inspected weekly. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030022 |  |  | Small Quantity Generator: Incompatible Waste Storage | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(2), 265.17(b), 265.177 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 37 | Hazardous Waste Management | Container Management | Incompatible waste in containers managed properly to prevent a reaction | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [LIST HAZARDOUS WASTES] located in the [LOCATION] are not compatible and were observed stored in a manner that could result a reaction. CORRECTIVE ACTION: Transfer or separate the containers of incompatible wastes noted above to other compatible containers or by separating containers to prevent a reaction and submit photos to the CUPA demonstrating compliance. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030014 |  |  | Large Quantity Generator: Container in Poor Condition or Damaged | Failure to accumulate hazardous waste in a container that is in good condition. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.171 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 38 | Hazardous Waste Management | Container Management | Accumulated hazardous waste in containers that are in good condition | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to accumulate hazardous waste in a container that is in good condition. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed [DESCRIBE CONDITION]. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is in good condition or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030016 |  |  | Large Quantity Generator: Hazardous Waste Container Incompatible with Material Stored | Failure to accumulate or store hazardous waste in container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.172 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 39 | Hazardous Waste Management | Container Management | Hazardous waste accumulated in lined and/or compatible containers | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to accumulate or store hazardous waste in container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed in an [UNLINED / INCOMPATIBLE] container. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is compatible with the hazardous waste or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030018 |  |  | Large Quantity Generator: Open Hazardous Waste Container | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.173 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 40 | Hazardous Waste Management | Container Management | Containers of hazardous waste closed except when adding or removing waste | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed open. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that the container listed above has been properly closed. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030020 |  |  | Large Quantity Generator: Weekly Hazardous Waste Storage Areas Inspection | Failure to inspect weekly, areas where hazardous waste containers are stored or transferred. The owner or operator shall look for leaking containers and for deterioration of containers and the containment system caused by corrosion or other factors. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.174 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 41 | Hazardous Waste Management | Container Management | Inspects all hazardous waste containers at least weekly | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to inspect weekly, areas where hazardous waste containers are stored or transferred. The owner or operator shall look for leaking containers and for deterioration of containers and the containment system caused by corrosion or other factors. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed [LEAKING / DETERIORATING]. CORRECTIVE ACTION: Submit a copy of the inspection log to the CUPA demonstrating that the hazardous waste storage area is being inspected weekly. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030021 |  |  | Large Quantity Generator: Reactive and Ignitable Waste 15 meters (50 feet) from Property Line | Failure to locate reactive and ignitable waste at least 15 meters (50 feet) from the facility's property line. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.176 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 42 | Hazardous Waste Management | Container Management | Reactive and ignitable waste containers located at least 50 ft from property line | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to locate reactive and ignitable waste at least 15 meters (50 feet) from the facility's property line. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [HAZARDOUS WASTES] located in the [LOCATION] were observed closer than 50 feet from the property line. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that all containers holding ignitable or reactive waste are stored at least 50 feet from the property line. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030023 |  |  | Large Quantity Generator: Incompatible Waste Storage | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.17(b), 66265.177 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 43 | Hazardous Waste Management | Container Management | Incompatible waste in containers managed properly to prevent a reaction | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [LIST HAZARDOUS WASTES] located in the [LOCATION] are not compatible and were observed stored in a manner that could result a reaction. CORRECTIVE ACTION: Transfer or separate the containers of incompatible wastes noted above to other compatible containers or by separating containers to prevent a reaction and submit photos to the CUPA demonstrating compliance. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030061 |  |  | Large Quantity Generator: Air Emissions for Waste in Containers | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.178 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 44 | Hazardous Waste Management | Container Management | Complied with air emission requirements for HW in containers | 60 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with air emission requirements for HW in containers as specified in articles 27, 28, and 28.5 of chapter 15. |  |  | OBSERVATION: The facility Owner/Operator failed to meet air emission requirements for hazardous waste containers as observed by [ENTER SPECIFIC OBSERVATIONS]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the air emission requirements specified in articles 27, 28, and 28.5 of chapter 15 have been met. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030058 |  |  | Hazardous Waste Generator: Empty Containers >5 Gallons | Failure to manage empty containers greater than 5 gallons in capacity that previously held a hazardous material/waste including but not limited to the following: (1) By reclaiming its scrap value onsite or shipping the container or inner liner to a person who reclaims its scrap value; or (2) By reconditioning or remanufacturing the container or inner liner onsite for subsequent reuse, or shipping the container or inner liner to a person who reconditions or remanufactures the container or inner liner; or (3) By shipping the container or inner liner to a supplier or to another intermediate collection location for accumulation prior to managing the container or inner liner; or (4) By shipping the container or inner liner back to the supplier for the purpose of being refilled. (5) A container or an inner liner removed from a container shall be marked with the date it has been emptied and shall be managed within one year of being emptied. | 22 CCR 11 66261.7 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 45 | Hazardous Waste Management | Container Management | Empty containers > 5 gallons properly managed | 45 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to manage empty containers greater than 5 gallons in capacity that previously held a hazardous material/waste including but not limited to the following: (1) By reclaiming its scrap value onsite or shipping the container or inner liner to a person who reclaims its scrap value; or (2) By reconditioning or remanufacturing the container or inner liner onsite for subsequent reuse, or shipping the container or inner liner to a person who reconditions or remanufactures the container or inner liner; or (3) By shipping the container or inner liner to a supplier or to another intermediate collection location for accumulation prior to managing the container or inner liner; or (4) By shipping the container or inner liner back to the supplier for the purpose of being refilled. (5) A container or an inner liner removed from a container shall be marked with the date it has been emptied and shall be managed within one year of being emptied. |  |  | OBSERVATION: Owner/Operator failed to properly manage empty containers greater than 5 gallons in capacity that previously held a hazardous material/waste. {describe specific violation as needed} CORRECTIVE ACTION: Submit photos/documentation to the UPA demonstrating that the empty containers have been marked with the date they were emptied and are being properly managed pursuant to 22 CCR 11 66261.7. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030056 |  |  | Hazardous Waste Generator: Hazardous Waste Tank Label | Failure to label stationary hazardous waste tanks as "hazardous waste" and mark with an accumulation start date. | 22 CCR 12 66262.34(f) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 46 | Hazardous Waste Management | Tank Management | Stationary tanks marked as "Hazardous Waste" and marked with accumulation start date | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to label stationary hazardous waste tanks as "hazardous waste" and mark with an accumulation start date. |  |  | OBSERVATION: The [HAZARDOUS WASTE] tank was observed without a label. CORRECTIVE ACTION: Submit a photo to the CUPA demonstrating that the [HAZARDOUS WASTE] tank has been properly labeled. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030025 |  |  | Small Quantity Generator: Hazardous Waste Tank Spill Control/Overfill | Failure to equip a continuously fed hazardous waste tank with a means to stop the inflow (e.g., waste feed cutoff system or by-pass system to a stand-by tank). | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(3), 265.201(b)(4) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 47 | Hazardous Waste Management | Tank Management | Continuously fed hazardous waste tanks are equipped with an overfill protection device | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to equip a continuously fed hazardous waste tank with a means to stop the inflow (e.g., waste feed cutoff system or by-pass system to a stand-by tank). |  |  | OBSERVATION: An overfill protection device on the continuously fed [HAZARDOUS WASTE] tank has not been provided. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the [HAZARDOUS WASTE] tank has been equipped with an overfill prevention device. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030027 |  |  | Small Quantity Generator: Daily Tank, Monitoring, and Discharge Inspection | Failure to inspect hazardous waste tanks at least once each operating day for the following, when present: (1) Discharge control equipment (e.g., waste feed cutoff systems, by-pass systems, and drainage systems) to ensure that it is in good working order; (2) Data gathered from monitoring equipment (e.g., pressure and temperature gauges) to ensure that the tank is being operated according to its design; (3) The level of waste in the tank. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(3), 265.201(c)(1), 265.201(c)(2), 265.201(c)(3) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 48 | Hazardous Waste Management | Tank Management | Daily inspections of the hazardous waste tank systems conducted | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to inspect hazardous waste tanks at least once each operating day for the following, when present: (1) Discharge control equipment (e.g., waste feed cutoff systems, by-pass systems, and drainage systems) to ensure that it is in good working order; (2) Data gathered from monitoring equipment (e.g., pressure and temperature gauges) to ensure that the tank is being operated according to its design; (3) The level of waste in the tank. |  |  | OBSERVATION: Daily hazardous waste tank inspections for the [HAZARDOUS WASTE] tank have not been conducted. CORRECTIVE ACTION: Conduct daily inspections of the hazardous waste tank according to the requirements identified above and submit a copy of the documentation to the CUPA. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030028 |  |  | Small Quantity Generator: Weekly Hazardous Waste Tank Construction and System Fixture Inspection | Failure to inspect hazardous waste tanks for the following, when present: 1) The construction materials of the tank at least weekly to detect corrosion or leaking of fixtures or seams. 2) The construction materials of, and the area immediately surrounding, discharge confinement structures (e.g., dikes) at least weekly to detect erosion or obvious signs of leakage (e.g., wet spots or dead vegetation). | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(3), 265.201(c)(4), 265.201(c)(5) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 49 | Hazardous Waste Management | Tank Management | Weekly inspections of the hazardous waste tank system conducted | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to inspect hazardous waste tanks for the following, when present: 1) The construction materials of the tank at least weekly to detect corrosion or leaking of fixtures or seams. 2) The construction materials of, and the area immediately surrounding, discharge confinement structures (e.g., dikes) at least weekly to detect erosion or obvious signs of leakage (e.g., wet spots or dead vegetation). |  |  | OBSERVATION: OBSERVATION: Weekly hazardous waste tank inspections for the [HAZARDOUS WASTE] tank have not been conducted. CORRECTIVE ACTION: Conduct weekly inspections of the hazardous waste tank according to the requirements identified above and submit a copy of the documentation to the CUPA. | [6 empty] | Yes | No
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050007 |  |  | Small Quantity Generator: Hazardous Waste Facility Closure | Failure to remove all hazardous waste from tanks, discharge control equipment, and discharge confinement structures upon closure of the facility. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(3), 265.201(f) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 50 | Hazardous Waste Management | Tank Management | Removed hazardous waste from tanks, equipment, and discharge confinement structures upon closure | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to remove all hazardous waste from tanks, discharge control equipment, and discharge confinement structures upon closure of the facility. |  |  | OBSERVATION: The [HAZARDOUS WASTE] has not been removed from the hazardous waste tank, discharge control equipment, and discharge confinement structures upon closure. CORRECTIVE ACTION: Submit manifests/receipts demonstrating [HAZARDOUS WASTE] has been removed from the tank, discharge control equipment, and discharge confinement structures. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030024 |  |  | Small Quantity Generator: Tank 2ft Freeboard | Failure to operate uncovered tanks to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system, or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(3), 265.201(b)(3) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 51 | Hazardous Waste Management | Tank Management | Uncovered hazardous waste tanks have 2 feet of freeboard unless equipped with adequate containment | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to operate uncovered tanks to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system, or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. |  |  | OBSERVATION: The uncovered [HAZARDOUS WASTE] tank does not contain 2 feet of freeboard and is not equipped with a containment structure, drainage control system, or diversion structure. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank is covered or meets the requirements identified above. | [6 empty] | Yes | No
Hazardous Waste Generator | Administration/Documentation | 3010025 |  |  | Large Quantity Generator: New Hazardous Waste Tank System P.E. Certification | Failure to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service. The written assessment shall state that, the new hazardous waste tank system has sufficient structural integrity, is acceptable for the transferring, storing and treating of hazardous waste, and that the tanks and containment system including the foundation, structural support, seams, connections, and pressure controls (if applicable) are suitably designed to meet the regulation. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.192(a) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 52 | Hazardous Waste Management | Tank Management | Obtained a written hazardous waste tank system assessment prior to placing into use | 83 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service. The written assessment shall state that, the new hazardous waste tank system has sufficient structural integrity, is acceptable for the transferring, storing and treating of hazardous waste, and that the tanks and containment system including the foundation, structural support, seams, connections, and pressure controls (if applicable) are suitably designed to meet the regulation. |  |  | OBSERVATION: A written hazardous waste tank assessment has not been obtained for the [HAZARDOUS WASTE] tank system prior to placing system into service. CORRECTIVE ACTION: Obtain a written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192 and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010032 |  |  | Large Quantity Generator: Reassessment for Hazardous Waste Tank System P.E. Certification | Failure of generator to obtain assessment or reassessment every five (5) years or the remaining service life of the tank system, as stated in the engineer's assessment, whichever is less. This assessment applies to onground or aboveground tank systems containing only non-RCRA hazardous wastes generated onsite, or for a small quantity generator onground or aboveground tank systems containing RCRA hazardous wastes generated onsite. | 22 CCR 15 66265.192(h) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 53 | Hazardous Waste Management | Tank Management | Written hazardous waste tank system assessment/reassessment by P.E. completed | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of generator to obtain assessment or reassessment every five (5) years or the remaining service life of the tank system, as stated in the engineer's assessment, whichever is less. This assessment applies to onground or aboveground tank systems containing only non-RCRA hazardous wastes generated onsite, or for a small quantity generator onground or aboveground tank systems containing RCRA hazardous wastes generated onsite. |  |  | OBSERVATION: A hazardous waste tank reassessment has not been conducted for the [HAZARDOUS WASTE] tank system within 5 years of the previous tank system assessment or within the remaining service life of the tank system as stated in the engineer's report, whichever is less. CORRECTIVE ACTION: Obtain a written hazardous waste tank system reassessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192 and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010026 |  |  | Large Quantity Generator: New Tank Assessment Standards | Failure to include all required information in the tank system assessment. | 22 CCR 15 66265.192(k) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 54 | Hazardous Waste Management | Tank Management | Written hazardous waste tank system assessment meets all requirements | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to include all required information in the tank system assessment. |  |  | OBSERVATION: The written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system did not include the following: [LIST] CORRECTIVE ACTION: Revise the written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192(k) and submit a copy to the CUPA. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030026 |  |  | Large Quantity Generator: Hazardous Waste Tank Standards | Failure to comply with general tank operating requirements: (a) Hazardous wastes or treatment reagents shall not be placed in a tank system if they could cause the tank, its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail; (b) The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: (1) spill prevention controls (e.g., check valves, dry discount couplings); (2) overfill prevention controls (e.g., level sensing devices, high level alarms, automatic feed cutoff, or bypass to a standby tank); and (3) maintenance of sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., standby tank with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank). | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.194 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 55 | Hazardous Waste Management | Tank Management | Tanks are compatible with hazardous waste and have spill/overflow prevention provided | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to comply with general tank operating requirements: (a) Hazardous wastes or treatment reagents shall not be placed in a tank system if they could cause the tank , its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail; (b) The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: (1) spill prevention controls (e.g., check valves, dry discount couplings); (2) overfill prevention controls (e.g., level sensing devices, high level alarms, automatic feed cutoff, or bypass to a standby tank); and (3) maintenance of sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. (Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., standby tank with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank). |  |  | OBSERVATION: Owner/Operator failed to comply with general tank operating requirements by either, placing wastes or treatment reagents into tank system that caused or could cause the tank, its ancillary equipment, or secondary containment to rupture, leak, corrode, or otherwise fail, and/or by failing to use appropriate controls/practices to prevent spills and overflows from tank system, such as check valves, dry discount couplings, level sensing devices, high level alarms, automatic feed cutoff or bypass to standby tank. For uncovered hazardous waste tanks owner/operator failed to maintain 2 ft of freeboard on tanks not equipped with secondary containment. CORRECTIVE ACTION: Correct the violations noted and/or equip waste tank as needed to comply with spill and overfill prevention requirements. Submit photos/documentation to the CUPA demonstrating that the tank or secondary containment system meets all requirements identified above. | OBSERVATION: The [HAZARDOUS WASTE] tank system is not compatible with [HAZARDOUS WASTE] observed accumulating in the tank system. Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] has been removed from the tanks system and has been placed in compatible containers/tanks. | [5 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030041 |  |  | Large Quantity Generator: Secondary Containment | Failure to meet required secondary containment requirements for hazardous waste tank systems or components. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.193 | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 56 | Hazardous Waste Management | Tank Management | Secondary containment provided and meets requirements for all hazardous waste tank systems | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to meet required secondary containment requirements for hazardous waste tank systems or components. |  |  | OBSERVATION: Secondary containment is not provided for the [HAZARDOUS WASTE] tank system. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating that secondary containment has been provided for the [HAZARDOUS WASTE] tank system and is in accordance with the requirements of 22 CCR 15 66265.193. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030029 |  |  | Large Quantity Generator: Hazardous Waste Tank Inspections | Failure to conduct and document inspections of hazardous waste tank systems each operating day and retain records of those inspections at the facility. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.195(a), 66265.195(c) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 57 | Hazardous Waste Management | Tank Management | Conducts/documents daily inspections of hazardous waste tank system | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to conduct and document inspections of hazardous waste tank systems each operating day and retain records of those inspections at the facility. |  |  | OBSERVATION: Daily inspections of the [HAZARDOUS WASTE] tank system have not been conducted and documented. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank system is being properly inspected and documented. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030042 |  |  | Large Quantity Generator: Hazardous Waste Tank Cathodic Inspection | Failure to inspect cathodic protection systems, if present, according to the following schedule to ensure that they are functioning properly: (1) the proper operation of the cathodic protection system shall be confirmed within six months after initial installation, and annually thereafter; and (2) all sources of impressed current shall be inspected and/or tested, as appropriate, at least bimonthly (i.e., every other month). (c) The owner or operator shall document in the operating record of the facility an inspection of the above items. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.195(b), 66265.195(c) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 58 | Hazardous Waste Management | Tank Management | Inspect/document the HW tank system cathodic protection system annually/impressed current bimonthly | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to inspect cathodic protection systems, if present, according to the following schedule to ensure that they are functioning properly: (1) the proper operation of the cathodic protection system shall be confirmed within six months after initial installation, and annually thereafter; and (2) all sources of impressed current shall be inspected and/or tested, as appropriate, at least bimonthly (i.e., every other month). (c) The owner or operator shall document in the operating record of the facility an inspection of the above items. |  |  | OBSERVATION: Annual cathodic protection and bimonthly impressed current inspections of the [HAZARDOUS WASTE] tank system have not been conducted and documented. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank system has been inspected for cathodic protection and all sources of impressed current. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010027 |  |  | Large Quantity Generator: Hazardous Waste Tank Equipment Replacement | Failure to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). | 22 CCR 15 66265.192(m) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 59 | Hazardous Waste Management | Tank Management | Obtained approval before replacement of identical/equivalent tank system parts not in 66265.192(l) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). |  |  | OBSERVATION: Owner/Operator failed to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). CORRECTIVE ACTION: Provide CUPA with documentation on the tank system parts or components that have been replaced. CUPA will then determine if a new written hazardous waste tank system assessment for the tank system is required. | [6 empty] | No | Yes
Hazardous Waste Generator | Release/Leaks/Spills | 3040001 |  |  | Large Quantity Generator: Hazardous Waste Tank Release | Failure to immediately remove from service a tank system or secondary containment system from which there has been a leak, spill, is unfit for use and comply with applicable requirements. | 22 CCR 15 66265.196 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 60 | Hazardous Waste Management | Tank Management | Leaking/unfit HW tank or secondary containment removed from service | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to immediately remove from service a tank system or secondary containment system from which there has been a leak, spill, is unfit for use and comply with applicable requirements. |  |  | OBSERVATION: Owner/Operator failed to immediately remove from service a hazardous waste tank system or secondary containment system from which there has been a leak, spill, or is unfit for use, and comply with applicable requirements. CORRECTIVE ACTION: Immediately remove the [HAZARDOUS WASTE] tanks system from service. Submit documentation to the CUPA demonstrating that all requirements in 22 CCR 15 66265.196 have been met. | [6 empty] | No | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050006 |  |  | Large Quantity Generator: Tank Closure Requirements and Documentation | Failure of owner or operator to properly close a hazardous waste tank system ensuring the minimization of further maintenance and that the required requirements have been met. | 22 CCR 15 66265.111, 66265.114, 66265.197 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 61 | Hazardous Waste Management | Tank Management | All hazardous waste tank system closure requirements have been met. | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of owner or operator to properly close a hazardous waste tank system ensuring the minimization of further maintenance and that the required requirements have been met. |  |  | OBSERVATION: Owner/Operator failed to properly close hazardous waste tank system. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the hazardous waste tank system has been closed in accordance with the requirements of 22 CCR 15 66265.197, and facility has complied with the requirements of 22 CCR 15 66265.111. and 66265.114. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030062 |  |  | Large Quantity Generator: Air Emissions for Wastes in Tanks | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.202 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 62 | Hazardous Waste Management | Tank Management | Complied with air emissions requirements for HW in tanks | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with air emission requirements for HW in tanks as specified in articles 27, 28, and 28.5 of chapter 15. |  |  | OBSERVATION: The facility Owner/Operator failed to meet the air emission requirements for hazardous waste tanks as observed by [ENTER SPECIFIC OBSERVATIONS]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the air emission requirements specified in articles 27, 28, and 28.5 of chapter 15 have been met. | [6 empty] | No | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050005 |  |  | Hazardous Waste Generator: Recyclable Materials | Failure to properly manage a recyclable material. | HSC 6.5 25143.2, 25143.9 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 63 | Hazardous Waste Management | Recyclable Materials | Recyclable material is managed properly | 39 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to properly manage a recyclable material. |  |  | OBSERVATION: Owner/Operator failed to properly manage a recyclable material {Describe observed issues}. CORRECTIVE ACTION: Submit documentation demonstrating compliance with the requirements of HSC 6.5 25143.2 for any material you claim qualifies as an excluded recyclable material, or indicate that this material is to be managed as a hazardous waste. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050004 |  |  | Hazardous Waste Generator: Contamination of Used Oil | Failure to prevent intentional contamination of used oil with other hazardous waste other than minimal amounts of vehicle fuel. | HSC 6.5 25250.7(a) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 64 | Hazardous Waste Management | Used Oil | Generator does not intentionally contaminate used oil with other hazardous wastes | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prevent intentional contamination of used oil with other hazardous waste other than minimal amounts of vehicle fuel. |  |  | OBSERVATION: Generator failed to prevent intentional contamination of used oil with other hazardous waste other than minimal amounts of vehicle fuel. CORRECTIVE ACTION: Submit a statement to the CUPA demonstrating how you will prevent contamination of used oil with other hazardous wastes. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030004 |  |  | Hazardous Waste Generator: Used Oil Filter and Fuel Filter Handling Requirements | Failure to properly manage used oil filters and/or fuel filters in accordance with the requirements. | 22 CCR 16 66266.130; HSC 6.5 25250.22 | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 65 | Hazardous Waste Management | Used Oil and Fuel Filters | Properly manages used oil filters and fuel filters | 50 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly manage used oil filters and/or fuel filters in accordance with the requirements. |  |  | OBSERVATION: Used oil and/or fuel filters were observed [DESCRIBE: WITHOUT LIDS, WITHOUT A LABEL, WITHOUT AN ACCUMULATION START DATE / WITH AN ACCUMULATED START DATE OF (DATE)]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the used oil and/or fuel filters are being properly managed or submit a bill of lading to this department demonstrating proper disposal. | OBSERVATION: Bills of lading for used oil and fuel filters were not available at the time of inspection. CORRECTIVE ACTION: Obtain copies of all bills of lading for used oil and fuel filters for the past three years and submit copies to the CUPA. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030001 |  |  | Hazardous Waste Generator: Management of Spent Vehicle Lead-Acid Batteries | Failure to meet the spent lead acid battery management requirements, when handling, storing, or transporting more than 10 lead acid batteries at any one time. | 22 CCR 16 66266.81(a)(1) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 66 | Hazardous Waste Management | Lead Acid Batteries | Meets requirements for handling/storing/transporting lead acid batteries | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the spent lead acid battery management requirements, when handling, storing, or transporting more than 10 lead acid batteries at any one time. |  |  | OBSERVATION: Generator failed to meet the spent lead acid battery management requirements, when handling, storing, or transporting more than 10 lead acid batteries at any one time. CORRECTIVE ACTION: Owner/Operator shall immediately begin to handle, store, and/or transport lead acid batteries in accordance with Title 22 regulations. | OBSERVATION: Bills of lading for spent lead acid batteries recording the shipments off site were not retained at the facility for the past three years. CORRECTIVE ACTION: Obtain copies of all bills of lading for lead-acid batteries over the past three years and submit copies to the CUPA. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030002 |  |  | Hazardous Waste Generator: Management of 11 or More Spent Vehicle Lead-Acid Batteries | Failure of facilities that accept spent lead acid batteries in exchange or partial exchange for operable lead-acid storage batteries to comply with storage requirements by violating one of the following: 1) Storing more than one ton of spent batteries at any one location for more than 180 days. 2) Storing one ton or less of spent batteries at any one location for more than one year, or 3) Removing the electrolyte. | 22 CCR 16 66266.81(a)(3) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 67 | Hazardous Waste Management | Lead Acid Batteries | Meets all requirements when accepting spent lead-acid batteries | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of facilities that accept spent lead acid batteries in exchange or partial exchange for operable lead-acid storage batteries to comply with storage requirements by violating one of the following: 1) Storing more than one ton of spent batteries at any one location for more than 180 days. 2) Storing one ton or less of spent batteries at any one location for more than one year, or 3) Removing the electrolyte. |  |  | OBSERVATION: The generator accepts lead acid batteries and was observed storing [MORE THAN ONE TON/LESS THAN ONE TON] of spent lead acid batteries for greater than [180 DAYS/1 YEAR], an/or removing electrolyte. CORRECTIVE ACTION: Submit a bill of lading or manifest to the CUPA demonstrating that the spent lead acid batteries have been properly managed or disposed of. Discontinue practice of removing electrolyte if applicable. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030003 |  |  | Hazardous Waste Generator: Damaged Lead Battery Handling | Failure to properly manage, store, and label a damaged lead acid battery in a nonreactive, structurally secure, closed container, and/or failure to label damaged lead acid battery with the date that the first battery in the container was placed there with ink, paint or other weather-resistant material so as to minimize the release of acid and lead and to protect the environment. | 22 CCR 16 66266.81(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 68 | Hazardous Waste Management | Lead Acid Batteries | Properly manages, stores and labels all damaged lead-acid batteries | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly manage, store, and label a damaged lead acid battery in a nonreactive, structurally secure, closed container, and/or failure to label damaged lead acid battery with the date that the first battery in the container was placed there with ink, paint or other weather-resistant material so as to minimize the release of acid and lead and to protect the environment. |  |  | OBSERVATION: Damage lead acid batteries were observed in the [LOCATION] and were not [LABELED WITH AN ACCUMULATION START DATE, IN A CLOSED, COMPATIBLE CONTAINER] CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the damaged battery has been properly managed. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010033 |  |  | Certified Appliance Recyclers: Certification | Failure to obtain Certified Appliance Recycler certification (CAR) from DTSC. | HSC 6.5 25211.4 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 69 | Hazardous Waste Management | Certified Appliance Recyclers | Obtained Certified Appliance Recycler certification (CAR) from the DTSC | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to obtain Certified Appliance Recycler certification (CAR) from DTSC. |  |  | OBSERVATION: Owner/Operator is removing materials that require special handling from appliances and does not have a Certified Appliance Recycler Certification from the DTSC. CORRECTIVE ACTION: Discontinue removing materials requiring special handling from appliances until you have obtained a Certified Appliance Recycler certification from DTSC. Provide copy of Certification when received from DTSC. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030055 |  |  | Certified Appliance Recyclers: MRSH properly managed | Failure of certified appliance recycler (CAR) to properly remove and dispose of all materials that require special handling (MRSH). | HSC 6.5 25212 | 2021-08-02 | 2099-12-31 | 2021-08-02 | Existing | 70 | Hazardous Waste Management | Certified Appliance Recyclers | CAR properly managed all MSRH as hazardous waste | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of certified appliance recycler (CAR) to properly remove and dispose of all materials that require special handling (MRSH). |  |  | OBSERVATION: The CAR has failed to properly remove and dispose of materials requiring special handling (MRSH) removed from appliances. CORRECTIVE ACTION: Immediately begin proper removal and disposal of all MRSH as hazardous waste. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010034 |  |  | Certified Appliance Recyclers: Documentation | Failure of certified appliance recycler (CAR) to provide documentation that all materials that require special handling (MRSH) have been properly removed and managed. | HSC 6.5 25211.2, 25211.3 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 71 | Hazardous Waste Management | Certified Appliance Recyclers | CAR maintains documentation regarding removal and management of MRSH from appliances | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of certified appliance recycler (CAR) to provide documentation that all materials that require special handling (MRSH) have been properly removed and managed. |  |  | OBSERVATION: Certified Appliance Recycler (CAR) failed to maintain required documentation demonstrating that all materials requiring special handling (MRSH) have been removed from appliances and properly managed. CORRECTIVE ACTION: Facility must comply with all requirements of sections 25211-25212 of the California Health & Safety Code, including, but not limited to, all documentation required related to the removal and management of MRSH from appliances processed by the CAR. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030054 |  |  | Hazardous Waste Generators: Reusable soiled textile materials. | Failure to properly manage reusable soiled textile materials prior to being sent for laundering. | HSC 6.5 25144.6(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 72 | Hazardous Waste Management | Reusable Soiled Textiles | Properly managed reusable soiled textile materials prior to being sent for laundering | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet all of the following requirements for reusable soiled textile materials: (1) The materials or the management of the materials are not otherwise regulated by the Environmental Protection Agency pursuant to the federal act. (2) The materials are not used to clean up or control a spill or release that is required to be reported to any state or federal agency. (3) No hazardous waste has been added after the materials’ original use. (4) No free liquids, as defined by Section 22-66260.10 of Title 26 of the California Code of Regulations, are released during transportation or storage of the materials. (5) The facility laundering or cleaning the materials maintains records of the date, type, and quantities by piecework or weight of the materials collected and laundered. (6) The facility laundering or cleaning the materials prepares a contingency plan which specifies procedures for handling both onsite and offsite emergencies involving the materials, and employees are trained in the execution of the plan. |  |  | OBSERVATION: Owner/Operator failed to meet all requirements applicable to managing reusable soiled textiles. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you are properly managing reusable soiled textiles in accordance with HSC 25144.6(b). | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030059 |  |  | Hazardous Waste Generator: Laboratory Accumulation Areas | Failure of the owner or operator managing laboratory hazardous waste in a laboratory accumulation area to comply with the quantity limitations, management, training, or documentation requirements. | HSC 6.5 25200.3.1(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 73 | Hazardous Waste Management | Laboratory Waste | Laboratory waste managed in accordance with HSC 25200.3.1(b) | 60 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator managing laboratory hazardous waste in a laboratory accumulation area to comply with the quantity limitations, management, training, or documentation requirements, in accordance with the HSC 25200.3.1(b). |  |  | OBSERVATION: Laboratory hazardous waste was observed being accumulated not in accordance with requirements 25200.3.1(b). CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the laboratory waste is being managed in accordance with HSC 25200.3.1(b). | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030060 |  |  | Hazardous Waste Generator: Laboratory Waste Treatment | Failure to treat laboratory hazardous waste according to all of the following requirements: 1) treated in containers and follow published procedures, 2) at a location as close as practical, and within 10 days, 3) single batch quantity limit to be 5 gallons or 18 kg, 4) waste from a single procedure or from the same laboratory process, 5) performed by trained personnel, 6) training records are maintained for 3 years, 7) waste and residuals are managed according to applicable requirements, and 8) records are made available for inspection. | HSC 6.5 25200.3.1 (c) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 74 | Hazardous Waste Management | Laboratory Waste | Laboratory waste treated in accordance with HSC 25200.3.1(c) | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to treat laboratory hazardous waste in accordance with HSC 25200.3.1(c) by not complying with one or more of the following requirements: 1) treated in containers and follow published procedures, 2) at a location as close as practical, and within 10 days, 3) single batch quantity limit to be 5 gallons or 18 kg, 4) waste from a single procedure or from the same laboratory process, 5) performed by trained personnel, 6) training records are maintained for 3 years, 7) waste and residuals are managed according to applicable requirements, and 8) records are made available for inspection. |  |  | OBSERVATION: Laboratory hazardous waste was observed being treated not in accordance with the requirements of 25200.3.1(c). CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the laboratory waste is being treated in accordance with HSC 25200.3.1(c). | [6 empty] | Yes | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050009 |  |  | Hazardous Waste Generator: Unauthorized Treatment | Failure to obtain a hazardous waste facilities permit, or other grant authorization, prior to accepting, treating, storing, or disposing of a hazardous waste at the facility, area, or site. | HSC 6.5 25201(a) | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 75 | Hazardous Waste Management | Unauthorized Treatment | Obtained a HW facilities permit or grant of authorization prior to treating hazardous waste | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain a hazardous waste facilities permit, or other grant authorization, prior to accepting, treating, storing, or disposing of a hazardous waste at the facility, area, or site. |  |  | OBSERVATION: Failure or the Owner/Operator to obtain a hazardous waste facilities permit or other grant of authorization prior to accepting, treating, storing, or disposing of a hazardous waste at the facility, area, or site. CORRECTIVE ACTION: Discontinue accepting, treating, storing, or disposing of hazardous waste until you have obtained a hazardous waste facilities permit or other grant of authorization. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010022 |  |  | Small Quantity Generator: Emergency Plan | Failure to post the following information next to the telephone: (A) The name and telephone number of the emergency coordinator; (B) Location of fire extinguishers and spill control material, and, if present, fire alarm; and (C) The telephone number of the fire department, unless the facility has a direct alarm. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(5)(ii) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 75 76 | General Facility Operations | Site Safety | Posted emergency information next to the telephone | 50 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to post the following information next to the telephone: (A) The name and telephone number of the emergency coordinator; (B) Location of fire extinguishers and spill control material, and, if present, fire alarm; and (C) The telephone number of the fire department, unless the facility has a direct alarm. |  |  | OBSERVATION: Emergency information is not posted next to the telephone. CORRECTIVE ACTION: Complete and post all required emergency information next to the telephone. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030039 |  |  | Small Quantity Generator: Emergency Coordinator | Failure to have at least one employee either on the premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(5)(i) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 76 77 | General Facility Operations | Site Safety | Emergency coordinator on the premises or on call | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to have at least one employee either on the premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. |  |  | OBSERVATION: An emergency coordinator was not on the premises or available on call. CORRECTIVE ACTION: Submit documentation to this office demonstrating that at least one employee is either on the premises or on call with the responsibility for coordinating all emergency response measures. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030032 |  |  | Small Quantity Generator: Facility Emergency Equipment | Failure of the facility to maintain the following emergency equipment or equivalents: 1) An internal communications or alarm system; 2) A device, such as a telephone (immediately available at the scene of Operations/ Maintenance ) or a hand-held two-way radio, capable of summoning emergency assistance from local police departments, fire departments, or State or local emergency response teams; 3) Portable fire extinguishers, fire control equipment, spill control equipment, and decontamination equipment; and 4) Water at adequate volume and pressure to supply water hose streams, or foam producing equipment, or automatic sprinklers, or water spray systems. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(4), 265.32 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 77 78 | General Facility Operations | Site Safety | Facility equipped with all required emergency equipment | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of the facility to maintain the following emergency equipment or equivalents: 1) An internal communications or alarm system; 2) A device, such as a telephone (immediately available at the scene of Operations/ Maintenance ) or a hand-held two-way radio, capable of summoning emergency assistance from local police departments, fire departments, or State or local emergency response teams; 3) Portable fire extinguishers, fire control equipment, spill control equipment, and decontamination equipment; and 4) Water at adequate volume and pressure to supply water hose streams, or foam producing equipment, or automatic sprinklers, or water spray systems. |  |  | OBSERVATION: The facility has not been equip with [LIST EQUIPMENT]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the facility has been equip with [LIST EQUIPMENT]. to the CUPA within [# days]. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030034 |  |  | Small Quantity Generator: Emergency Equipment Maintenance | Failure to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(4), 265.33 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 78 79 | General Facility Operations | Site Safety | Tests and maintains all required safety equipment at the facility | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. |  |  | OBSERVATION: [LIST EQUIPMENT] has not been tested and maintained to assure its proper operation in time of emergency. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating [LIST EQUIPMENT] has been properly tested or maintained. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030036 |  |  | Small Quantity Generator: Aisle Space | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless aisle space is not needed for any of these purposes. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(4), 265.35 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 79 80 | General Facility Operations | Site Safety | Maintains adequate aisle space | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless aisle space is not needed for any of these purposes. |  |  | OBSERVATION: The hazardous waste storage area located in the [LOCATION] did not have adequate aisle space allowing for unobstructed movement. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that adequate aisle space has been provided. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030030 |  |  | Small Quantity Generator: Facility Maintained to Prevent Fire/Explosion/Release | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. | 22 CCR 12 66262.34(d)(2); 40 CFR 1 262.34(d)(4), 265.31 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 80 81 | General Facility Operations | Site Safety | Maintains and operates the facility to minimize the possibility of fire/explosion/release | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. |  |  | OBSERVATION: [HAZARDOUS WASTE] was observed [DESCRIBE SPILL] in the [LOCATION]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the spill has been properly removed and managed. | [6 empty] | Yes | No
Hazardous Waste Generator | Operations/Maintenance | 3030063 |  |  | Large Quantity Generator: Emergency Coordinator | Failure to have at least one employee either on the facility premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.55 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 81 82 | General Facility Operations | Site Safety | Emergency coordinator on the premises or on call | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to have at least one employee either on the facility premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. |  |  | OBSERVATION: An emergency coordinator was not on the premises or available on call. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that at least one employee is either on the premises or on call with the responsibility for coordinating all emergency response measures. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030033 |  |  | Large Quantity Generator: Facility Emergency Equipment | Failure of the facility to maintain the following emergency equipment or equivalents: 1) An internal communications or alarm system; 2) A device, such as a telephone (immediately available at the scene of Operations/ Maintenance ) or a hand-held two-way radio, capable of summoning emergency assistance from local police departments, fire departments, or State or local emergency response teams; 3) Portable fire extinguishers, fire control equipment, spill control equipment, and decontamination equipment; and 4) Water at adequate volume and pressure to supply water hose streams, or foam producing equipment, or automatic sprinklers, or water spray systems. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.32 | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 82 83 | General Facility Operations | Site Safety | Facility equipped with all required emergency equipment | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of the facility to maintain the following emergency equipment or equivalents: 1) An internal communications or alarm system; 2) A device, such as a telephone (immediately available at the scene of Operations/ Maintenance ) or a hand-held two-way radio, capable of summoning emergency assistance from local police departments, fire departments, or State or local emergency response teams; 3) Portable fire extinguishers, fire control equipment, spill control equipment, and decontamination equipment; and 4) Water at adequate volume and pressure to supply water hose streams, or foam producing equipment, or automatic sprinklers, or water spray systems. |  |  | OBSERVATION: The facility has not been equip with [LIST EQUIPMENT]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the facility has been equip with [LIST EQUIPMENT]. to the CUPA within [# days]. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030035 |  |  | Large Quantity Generator: Emergency Equipment Maintenance | Failure to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.33 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 83 84 | General Facility Operations | Site Safety | Tests and maintains all required safety equipment at the facility | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. |  |  | OBSERVATION: [LIST EQUIPMENT] has not been tested and maintained to assure its proper operation in time of emergency. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating [LIST EQUIPMENT] has been properly tested or maintained. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030037 |  |  | Large Quantity Generator: Aisle Space | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless it can be demonstrated to the Department that aisle space is not needed for any of these purposes. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.35 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 84 85 | General Facility Operations | Site Safety | Maintains adequate aisle space | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless it can be demonstrated to the Department that aisle space is not needed for any of these purposes. |  |  | OBSERVATION: The hazardous waste storage area located in the [LOCATION] did not have adequate aisle space allowing for unobstructed movement. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that adequate aisle space has been provided. | [6 empty] | No | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030031 |  |  | Large Quantity Generator: Facility Maintained To Prevent Fire/Explosion/Release | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.31 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 85 86 | General Facility Operations | Site Safety | Maintains and operates the facility to minimize the possibility of fire/explosion/release | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. |  |  | OBSERVATION: [HAZARDOUS WASTE] was observed [DESCRIBE SPILL] in the [LOCATION]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the spill has been properly removed and managed. | [6 empty] | No | Yes
Hazardous Waste Generator | Administration/Documentation | 3010003 |  |  | Universal Waste Handler: USEPA Notification | Failure of a universal waste handler to send written notification of universal waste management to the USEPA Regional Administrator and obtain a federal ID Number prior to accumulating 5,000 kilograms or more of RCRA universal waste. | 22 CCR 23 66273.32(a) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 86 87 | Universal Waste | >5000 Kg | UWH notified the EPA and obtained a federal ID number prior to storing 5,000 kg or more of RCRA UW | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of a universal waste handler to send written notification of universal waste management to the USEPA Regional Administrator and obtain a federal ID Number prior to accumulating 5,000 kilograms or more of RCRA universal waste. |  |  | OBSERVATION: The universal waste handler failed to notify the USEPA and/or obtain a federal ID number prior to storing 5,000 kg or more of RCRA universal waste. [enter specific observations] CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you have notified the federal USEPA and obtained a federal EPA ID number. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010004 |  |  | Universal Waste Handler: Department ID Number | Failure of a universal waste handler to obtain an ID Number from DTSC prior to storing 5,000 kilograms or more of universal waste when a federal ID number is not required. | 22 CCR 23 66273.32(b) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 87 88 | Universal Waste | >5000 Kg | UWH obtained an ID# from DTSC prior to storing >5,000 kg of UW when a fed ID# is not required | 93 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of a universal waste handler to obtain an ID Number from DTSC prior to storing 5,000 kilograms or more of universal waste when a federal ID number is not required. |  |  | OBSERVATION: The universal waste handler failed to obtain an ID number from the DTSC prior to storing 5,000 kg or more of universal waste when a federal ID number is not required. [enter specific observations] CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you have applied to the DTSC for an ID number. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010005 |  |  | Universal Waste Handler: Department Notification | Failure of a universal waste handler of PV modules, electronic devices, CRTs, and/or CRT glass who might accept and accumulate, but not treat, any PV module, electronic device, CRT, and/or CRT glass from an offsite source to submit notification with all required information to DTSC no later than 30 calendar days prior to accepting any above noted waste. | 22 CCR 23 66273.32(c), (e) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 88 89 | Universal Waste | Electronic Devices/CRT/PV Modules | UWH of PV modules/e-devices/CRTs/CRT glass that doesn't treat waste submitted required info to DTSC | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a universal waste handler of PV modules, electronic devices, CRTs, and/or CRT glass who might accept and accumulate, but not treat, any PV module, electronic device, CRT, and/or CRT glass from an offsite source to submit notification with all required information to DTSC no later than 30 calendar days prior to accepting any above noted waste. |  |  | OBSERVATION: Failure of the universal waste handler who accepts and accumulates, but does not treat, any PV modules, electronic device, CRT, and/or CRT glass from an offsite source, to submit notification with all required information to DTSC no later than 30 calendar days prior to accepting any above noted waste. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that notification with all required information has been submitted to the DTSC prior to accepting any wastes noted above. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010020 |  |  | Universal Waste Handler: Annual Report | Failure of a universal waste handler who either: 1) accepts more than 100 kilograms (or 220 pounds) of PV modules or electronic devices, CRTs, and CRT glass calculated collectively, from any offsite sources in a calendar year, or 2) generates 5,000 kilograms (or 11,000 pounds; e.g., about 200 CRTs) or more of PV modules or electronic devices, CRTs, and CRT glass calculated collectively, in a calendar year, to submit to DTSC by February 1 of every year a an annual report that includes all required information. | 22 CCR 23 66273.32(d)(1), (2), (f)(1), (2) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 89 90 | Universal Waste | Electronic Devices/CRT/PV Modules | Accepts 100kg or generates 5000 kg/yr of E-waste/CRTs/PV modules & reports to DTSC Feb 1 annually | 97 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a universal waste handler who either: 1) accepts more than 100 kilograms (or 220 pounds) of PV modules or electronic devices, CRTs, and CRT glass calculated collectively, from any offsite sources in a calendar year, or 2) generates 5,000 kilograms (or 11,000 pounds; e.g., about 200 CRTs) or more of PV modules or electronic devices, CRTs, and CRT glass calculated collectively, in a calendar year, to submit to DTSC by February 1 of every year a an annual report that includes all required information. |  |  | OBSERVATION: The UWH accepts 100 kg of PV modules, electronic devices, CRTs, and CRT glass per year from offsite sources, or generates 5,000 kg or more, and has not submitted the required information to the DTSC by February 1st. CORRECTIVE ACTION: Submit the required information listed above to the DTSC and submit a copy to the CUPA. | OBSERVATION: The UWH generates greater that 5,000 Kg of electronic devices, CRTs, and CRT glass per year and has not submitted the required information to the DTSC by February 1st. CORRECTIVE ACTION: Submit the required information listed above to the DTSC and submit a copy to the CUPA. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010006 |  |  | Universal Waste: Exporting Notification | Failure of the universal waste handler who sends electronic devices, CRTs, and/or CRT glass to any foreign destination to comply with the following: (1) Notify the Department 60 days prior to the intended export before any electronic devices, CRTs, and/or CRT glass are scheduled to leave the United States and cover all export activities extending over the next twelve (12) month or lesser period; (2) Concurrently send a copy of the notification required pursuant to subsection 66273.40(a)(2)(B) of 22 CCR to the CUPA having jurisdiction over the universal waste handler’s facility; (3) sign the export notification; and (4) include all required information in the export notification. | 22 CCR 23 66273.40(a)(2), (3) and (4) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 90 91 | Universal Waste | Exporting Notification | UWH sending devices/CRTs/CRT glass to any foreign destination completed and submitted notification | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the universal waste handler who sends electronic devices, CRTs, and/or CRT glass to any foreign destination to comply with the following: (1) Notify the Department 60 days prior to the intended export before any electronic devices, CRTs, and/or CRT glass are scheduled to leave the United States and cover all export activities extending over the next twelve (12) month or lesser period; (2) Concurrently send a copy of the notification required pursuant to subsection 66273.40(a)(2)(B) of 22 CCR to the CUPA having jurisdiction over the universal waste handler’s facility; (3) sign the export notification; and (4) include all required information in the export notification. |  |  | OBSERVATION: The universal waste handler failed to comply with one or more of the following: (1) Notify the DTSC 60 days prior to the intended export before any electronic devices, CRTs, and/or CRT glass are scheduled to leave the United States and cover all export activities extending over the next twelve (12) month or lesser period; (2) Concurrently send a copy of the notification required pursuant to subsection 66273.40(a)(2)(B) of 22 CCR, to the UPA having jurisdiction over the universal waste handler’s facility; (3) sign the export notification; and (4) include all required information in the export notification. [enter specific observations] CORRECTIVE ACTION: Complete and submit the required notification information listed above to DTSC and to the CUPA. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030008 |  |  | Universal Waste Handler: Labeling Requirements | Failure to label or mark each individual or container or the designated area of universal waste as required. 1. Waste batteries shall be marked with "Universal Waste-Battery(ies)”. 2. Mercury containing equipment shall be marked with "Universal Waste -Mercury-Containing Equipment”. 3. Lamps shall be marked with “Universal Waste-Lamp(s)”. 4. Electronic devices or the container or pallet where the devices are stored shall be marked with “Universal Waste-Electronic Device(s)”. 5. CRTs or the container or pallet where CRTs are stored shall be marked with "Universal Waste-CRT(s)”. 6. Container for CRT glass shall be marked with “Universal Waste-CRT glass”. 7. PV modules shall be marked with "Universal Waste-PV Module(s)". | 22 CCR 23 66273.34 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 91 92 | Universal Waste | UW Management | UWH labeled all universal waste | 31 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to label or mark each individual or container or the designated area of universal waste as required. 1. Waste batteries shall be marked with "Universal Waste-Battery(ies)”. 2. Mercury containing equipment shall be marked with "Universal Waste -Mercury-Containing Equipment”. 3. Lamps shall be marked with “Universal Waste-Lamp(s)”. 4. Electronic devices or the container or pallet where the devices are stored shall be marked with “Universal Waste-Electronic Device(s)”. 5. CRTs or the container or pallet where CRTs are stored shall be marked with "Universal Waste-CRT(s)”. 6. Container for CRT glass shall be marked with “Universal Waste-CRT glass”. 7. PV modules shall be marked with "Universal Waste-PV Module(s)". |  |  | OBSERVATION: Owner/Operator failed to properly label universal waste. CORRECTIVE ACTION: Properly label universal waste [Identify] and submit statement of compliance and/or a photo of the waste labeled properly. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030011 |  |  | Universal Waste Handler: Accumulation Time | Failure to accumulate universal waste for one year or less and to demonstrate the length of time that the universal waste has been accumulated from the date it became a waste or was received. | 22 CCR 23 66273.35 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 92 93 | Universal Waste | UW Management | UWH accumulated universal waste for no longer than 1 year | 57 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to accumulate universal waste for one year or less and to demonstrate the length of time that the universal waste has been accumulated from the date it became a waste or was received. |  |  | OBSERVATION: [UNIVERSAL WASTE] located in the [LOCATION] was observed with an accumulation start date of [DATE]. CORRECTIVE ACTION: Dispose of [UNIVERSAL WASTE] and submit a copy of the manifest/receipt to the CUPA. | OBSERVATION: [UNIVERSAL WASTE] located in the [LOCATION] was observed without an accumulation start date and the UWH was unable to demonstrated that the universal waste has been accumulating less than one year. CORRECTIVE ACTION: Dispose of [UNIVERSAL WASTE] and submit a copy of the manifest/receipt to the CUPA. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030051 |  |  | Universal Waste: Accumulation of Aerosol Cans | Failure to comply with the applicable requirements related to accumulation and containment standards for universal waste aerosol cans. | HSC 6.5 25201.16(f) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 93 94 | Universal Waste | UW Management | UWH meets all accumulation standards for universal waste aerosol cans | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with the applicable requirements related to accumulation and containment standards for universal waste aerosol cans. |  |  | OBSERVATION: [Describe container - not closed, leaking, incompatible with contents, etc.]. [Aerosol cans, or contents removed from aerosol cans etc.] shall be accumulated in a container that is closed, structurally sound and compatible with the contents of the universal waste aerosol can and show no leakage, spillage, or damage that could cause leakage. CORRECTIVE ACTION: Immediately [close container, transfer to compatible container, etc.]. Submit documentation to the CUPA demonstrating what corrective actions were taken. | OBSERVATION: [Describe container, location, and condition of floor]. Containers holding aerosol cans or contents removed from aerosol cans shall be placed on or above a floor that is free of cracks or gaps and is sufficiently impervious and bermed to contain leaks and spills. CORRECTIVE ACTION: Immediately relocate this container to a proper location. Submit documentation to the CUPA demonstrating what corrective actions were taken. | OBSERVATION: [Describe aerosol cans found and note incompatibilities] were found stored in the same container. Incompatible materials shall be kept segregated and managed appropriately in separate containers. CORRECTIVE ACTION: Immediately separate the incompatible aerosol cans and store them in separate containers. Ensure that all aerosol cans are checked for compatibility prior to storage. Submit documentation to the CUPA demonstrating what corrective actions were taken. | OBSERVATION: [Describe container, location, and proximity to heat source]. A container holding flammable wastes shall be kept at a safe distance from heat and open flames. CORRECTIVE ACTION: Immediately relocate this container to a safe distance from [whatever the heat source is]. Submit documentation to the CUPA demonstrating what corrective actions were taken. | OBSERVATION: [Describe container and location] were found not labeled with the type of waste stored. Containers used to store aerosol cans shall be labeled or marked with one of the following phrases: “Universal Waste – Aerosol Cans”, “Waste Aerosol Cans”, or “Used Aerosol Cans”. CORRECTIVE ACTION: Immediately mark these containers and ensure that all containers of aerosol cans are marked in this manner. Submit documentation to the CUPA demonstrating what corrective actions were taken. |  |  | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030050 |  |  | Universal Waste: Handling of Aerosol Cans | Failure of the universal waste handler to manage universal waste aerosol cans in a manner that prevents fire, explosion, and the unauthorized release of any universal waste or component of a universal waste to the environment. | HSC 6.5 25201.16(e) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 94 95 | Universal Waste | UW Management | Universal waste aerosol cans managed to prevent fire, explosion and unauthorized release | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the universal waste handler to manage universal waste aerosol cans in a manner that prevents fire, explosion, and the unauthorized release of any universal waste or component of a universal waste to the environment. |  |  | OBSERVATION: Owner/Operator failed to manage universal waste aerosol cans in a manner that prevents fire, explosion, and the unauthorized release of any universal waste or component of a universal waste to the environment. CORRECTIVE ACTION: Properly manage universal waste aerosol cans in a manner that prevents fire, explosion, and the unauthorized release of any universal waste or component of a universal waste to the environment. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010037 |  |  | Universal Waste Aerosol Can Processing | Failure to notify the CUPA of aerosol can processing procedures prior to commencement of operations | HSC 6.5 25201.16(j) | 2021-08-02 | 2021-12-31 | 2021-08-02 | Revised | 95 96 | Universal Waste | UW Management | Notified UPA of aerosol can processing procedures prior to starting this process | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to notify the CUPA of aerosol can processing procedures prior to commencement of operations |  |  | OBSERVATION: Owner/Operator failed to notify UPA of aerosol can processing procedures prior to starting this process. CORRECTIVE ACTION: Submit required notification to UPA of aerosol can processing procedures. Discontinue processing aerosol cans until this notification is submitted to UPA. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030046 |  |  | Universal Waste Handler: Offsite Shipments | Failure of the universal waste handler to transfer universal waste to another universal waste handler, or appropriate destination facility. Failure to package, label, mark and placard shipments and prepare shipping papers for any universal waste that meets the hazardous materials definition in accordance with DOT 49 CFR parts 171-180. | 22 CCR 23 66273.38; 49 CFR 1 172 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 96 97 | Universal Waste | UW Management | UWH properly prepares, handles and retains shipping papers for all universal waste shipped | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the universal waste handler to transfer universal waste to another universal waste handler, or appropriate destination facility. Failure to package, label, mark and placard shipments and prepare shipping papers for any universal waste that meets the hazardous materials definition in accordance with DOT 49 CFR parts 171-180. |  |  | OBSERVATION: Universal Waste Handler (UWH)failed to properly package, label, mark, placard, or prepare and retain shipping papers for all universal waste being shipped to another universal waste handler, destination facility, or foreign facility. [ENTER SPECIFIC OBSERVATION] CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that all universal waste noted above have been properly packaged, labeled, marked, placarded, or prepared and retain shipping papers. | OBSERVATION: Universal Waste Handler failed to send UW to another Universal Waste Handler or a permitted destination facility as observed by [ENTER OBSERVED SHIPPING/DISPOSAL VIOLATION]. CORRECTIVE ACTION: The UWH shall immediately submit a written statement to the CUPA documenting how the facility will properly manage and recycle all UW generated on site. | [5 empty] | Yes | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050003 |  |  | Universal Waste Handler: Illegal Disposal | Failure of the universal waste handler to prevent improper disposal of universal waste, or to transfer universal waste to the appropriate destination facility. | 22 CCR 23 66273.31(a), 66273.8(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 97 98 | Universal Waste | UW Management | UWH transfers or disposes all universal waste to an appropriate destination facility | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of the universal waste handler to prevent improper disposal of universal waste, or to transfer universal waste to the appropriate destination facility. |  |  | OBSERVATION: The Universal Waste Handler improperly disposed of, or failed to transfer universal waste to an appropriate destination facility. CORRECTIVE ACTION: Ensure that all universal wastes are transferred to an appropriate destination facility and properly disposed. Submit documentation to the CUPA indicating that all universal waste has been transferred to an appropriate destination facility. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Release/Leaks/Spills | 3040004 |  |  | Universal Waste Handler: Release | Failure of the universal waste handler of PV modules electronic devices, CRTs, and CRT glass to prevent the release of the universal waste to the environment under reasonable conditions by the following methods: 1) Immediately clean spills and leaks of universal wastes; and 2) Place all universal waste spills and leaks in containers that are structurally sound and compatible with the universal waste. | 22 CCR 23 66273.33.5, 66273.33.6 | 2021-08-02 | 12/31/2099 | 2021-08-02 | Revised | 98 99 | Universal Waste | UW Management | UWH properly cleaned up and contained spills of PV modules, electronic devices, CRTs and CRT glass | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of the universal waste handler of PV modules electronic devices, CRTs, and CRT glass to prevent the release of the universal waste to the environment under reasonable conditions by the following methods: 1) Immediately clean spills and leaks of universal wastes; and 2) Place all universal waste spills and leaks in containers that are structurally sound and compatible with the universal waste. |  |  | OBSERVATION: Failure of Universal Waste Handler of PV modules, electronic devices, CRTs and/or CRT glass to prevent the release of universal waste to the environment by failing to immediately clean spills and leaks of universal wastes and/or by placing spilled/leaked waste in containers that are not structurally sound and compatible with the waste. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the spilled PV modules, electronic devices, CRTs and/or CRT glass have been properly removed/cleaned up and managed. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Training | 3020003 |  |  | Universal Waste Handler: Employee Training | Failure of universal waste handler to provide initial and/or annual refresher training for employees who manage or handle universal waste and to maintain a written record for three years of personnel who took the initial or annual training. | 22 CCR 23 66273.36 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 99 100 | Universal Waste | Training | UWH complied with all universal waste training requirements | 59 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of universal waste handler to provide initial and/or annual refresher training for employees who manage or handle universal waste and to maintain a written record for three years of personnel who took the initial or annual training. |  |  | OBSERVATION: Owner/Operator failed to provide initial and/or annual refresher training for employees who manage or handle universal waste and to maintain a written record for three years of personnel who took the initial or annual training. CORRECTIVE ACTION: Provide employees with initial or refresher UW training. Submit a evidence of training to the CUPA. | [6 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3010 |  |  | HW-Administration/Documentation - General | Administration/Documentation - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 100 101 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes | Yes
Hazardous Waste Generator | Administration/Documentation | 3015 |  |  | HW-Administration/Documentation - General Local Ordinance | Administration/Documentation - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 101 102 | General Facility Requirements |  | Administration/Documentation - General Local Ordinance | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General Local Ordinance | [9 empty] | Yes | Yes
Hazardous Waste Generator | Training | 3020 |  |  | HW-Training - General | Training - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 102 103 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes | Yes
Hazardous Waste Generator | Training | 3025 |  |  | HW-Training - General Local Ordinance | Training - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 103 104 | General Facility Requirements |  | Training - General Local Ordinance | 34 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General Local Ordinance | [9 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3030 |  |  | HW-Operations/Maintenance - General | Operations/Maintenance - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 104 105 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes | Yes
Hazardous Waste Generator | Operations/Maintenance | 3035 |  |  | HW-Operations/Maintenance - General Local Ordinance | Operations/Maintenance - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 105 106 | General Facility Requirements |  | Operations/Maintenance - General Local Ordinance | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General Local Ordinance | [9 empty] | Yes | Yes
Hazardous Waste Generator | Release/Leaks/Spills | 3040 |  |  | HW-Release/Leaks/Spills - General | Release/Leaks/Spills - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 106 107 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes | Yes
Hazardous Waste Generator | Release/Leaks/Spills | 3045 |  |  | HW-Release/Leaks/Spills - General Local Ordinance | Release/Leaks/Spills - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 107 108 | General Facility Requirements |  | Release/Leaks/Spills - General Local Ordinance | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General Local Ordinance | [9 empty] | Yes | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3050 |  |  | HW-Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 108 109 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes | Yes
Hazardous Waste Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3055 |  |  | HW-Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 109 110 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | [9 empty] | Yes | Yes

## HHW
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | PHHWCF | THHWCF
Household Hazardous Waste Program | Administration/Documentation | 3310001 |  |  | Household Permit by Rule: PHHWCF Operating without a Permit | Failure of the operator of the PHHWCF to submit a Permanent Household Hazardous Waste Collection Facility Permit by Rule Notification to CUPA or authorized agency a minimum of 45 days in advance of the planned commencement of operation. | 22 CCR 20 66270.60(d)(6) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 1 | File Review | PHHWCF | PHHWCF Permit by Rule Notification submitted to CUPA or PA at least 45 days prior to operating. | 95 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the operator of the PHHWCF to submit a Permanent Household Hazardous Waste Collection Facility Permit by Rule Notification to CUPA or authorized agency a minimum of 45 days in advance of the planned commencement of operation. | [9 empty] | yes | no
Household Hazardous Waste Program | Administration/Documentation | 3310002 |  |  | Household Permit by Rule: THHWCF Operating without a Permit | Failure of the operator of the THHWCF to submit a Temporary Household Hazardous Waste Collection Facility Permit by Rule Notification to CUPA or authorized agency a minimum of 45 days in advance of the date the first session of the THHWCF commences operation. | 22 CCR 20 66270.60(d)(5) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 2 | File Review | THHWCF | THHWCF Permit by Rule Notification submitted to CUPA or PA at least 45 days prior to operating. | 95 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the operator of the THHWCF to submit a Temporary Household Hazardous Waste Collection Facility Permit by Rule Notification to CUPA or authorized agency a minimum of 45 days in advance of the date the first session of the THHWCF commences operation. | [9 empty] | no | yes
Household Hazardous Waste Program | Administration/Documentation | 3310007 |  |  | Household Permit by Rule: PHHWCF Financial Assurance | Failure of the owner or operator of PHHWCF to prepare and submit a financial assurance certification of closure for the PHHWCF, with an established mechanism or by self-insuring for public agencies using DTSC Form 1220 (2/96) with original signatures. | 22 CCR 45 67450.30(c) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 3 | File Review | PHHWCF | Financial Assurance Certification for Closure submitted | 55 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the owner or operator of PHHWCF to prepare and submit a financial assurance certification of closure for the PHHWCF, with an established mechanism or by self-insuring for public agencies using DTSC Form 1220 (2/96) with original signatures. | [9 empty] | yes | no
Household Hazardous Waste Program | Administration/Documentation | 3310008 |  |  | Household Permit by Rule: PHHWCF Closure Costs | Failure to prepare, submit, and maintain onsite an estimate of the maximum cost projected of closing the PHHWCF. | 22 CCR 45 67450.30(b)(3); 22 CCR 45 67450.30(b)(4) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 4 | File Review | PHHWCF | A written closure cost estimate was prepared, submitted, and maintained onsite | 79 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure to prepare, submit, and maintain onsite an estimate of the maximum cost projected of closing the PHHWCF. | [9 empty] | yes | no
Household Hazardous Waste Program | Administration/Documentation | 3310009 |  |  | Household Permit by Rule: PHHWCF Annual Closure Cost Adjustment | Failure of the operator to adjust annually the closure cost estimate for inflation within sixty (60) days prior to the anniversary date of the original establishment of the financial mechanism or to revise the closure cost estimate no more than thirty (30) days after a change in the closure plan increases the cost of closure. | 22 CCR 45 67450.30(b)(1), (2) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Existing | 5 | File Review | PHHWCF | Adjusted written closure cost estimate for inflation annually or within 30 days of increase in costs | 100 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Failure of the operator to adjust annually the closure cost estimate for inflation within sixty (60) days prior to the anniversary date of the original establishment of the financial mechanism or to revise the closure cost estimate no more than thirty (30) days after a change in the closure plan increases the cost of closure. | [9 empty] | yes | no
Household Hazardous Waste Program | Administration/Documentation | 3310006 |  |  | Household Permit by Rule: PHHWCF Phase I Completion | Failure of the PHHWCF operator to complete, maintain as part of the operation plan, and file a Phase I assessment within 1 year of commencing operation. | 22 CCR 45 67450.25(a)(5) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 6 | On Site Records | PHHWCF | Phase I assessment submitted within 1 year of commencing operation and part of the operation plan. | 98 | yes | yes | yes | yea | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF operator to complete, maintain as part of the operation plan, and file a Phase I assessment within 1 year of commencing operation. | [9 empty] | yes | no
Household Hazardous Waste Program | Administration/Documentation | 3310003 |  |  | Household Permit by Rule: PHHWCF Reassessment Tank System | Failure of the owner or operator to prepare and maintain for the tank systems: professional engineering certification provided by a manufacturer, an independent professional engineer registered in the State of California or a professional engineer employed by the local government entity and from a different division or agency than the operator. Failure of owner or operator to obtain tank reassessment every five years. | 22 CCR 45 67450.25(a)(2)(G); 22 CCR 15 66265.192(h) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 7 | On Site Records | PHHWCF | Compliant tank system closure plan certified by independent or manufacturer's professional engineer | 99 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the owner or operator to prepare and maintain for the tank systems: professional engineering certification provided by a manufacturer, an independent professional engineer registered in the State of California or a professional engineer employed by the local government entity and from a different division or agency than the operator. Failure of owner or operator to obtain tank reassessment every five years. | [9 empty] | yes | no
Household Hazardous Waste Program | Administration/Documentation | 3310010 |  |  | Household Permit by Rule: PHHWCF Waste Analysis Plan | Failure of the owner or operator to prepare and maintain a written waste analysis plan describing the procedures which the operator or contractor will carry out to characterize unidentified wastes received at the facility including field analysis methods such as Hazardous Category (HAZCAT) analysis. | 22 CCR 45 67450.25(a)(2)(A) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 8 | On Site Records | PHHWCF | A written waste analysis plan has been prepared | 47 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the owner or operator to prepare and maintain a written waste analysis plan describing the procedures which the operator or contractor will carry out to characterize unidentified wastes received at the facility including field analysis methods such as Hazardous Category (HAZCAT) analysis. | [9 empty] | yes | no
Household Hazardous Waste Program | Administration/Documentation | 3310011 |  |  | Household Permit by Rule: THHWCF Operational Plan | Failure of the THHWCF to prepare and maintain an operation plan containing all required information. | 22 CCR 45 67450.4(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 9 | On Site Records | THHWCF | Operation plan at facility, contains all required information and provided to CUPA when requested | 99 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF to prepare and maintain an operation plan containing all required information. | [9 empty] | no | yes
Household Hazardous Waste Program | Administration/Documentation | 3310012 |  |  | Household Permit by Rule: PHHWCF Operational Plan | Failure of the PHHWCF to prepare and maintain an operation plan containing all required information. | 22 CCR 45 67450.25(a)(3) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 10 | On Site Records | PHHWCF | Operation plan at facility, contains all required information and provided to CUPA when requested | 99 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to prepare and maintain an operation plan containing all required information. | [9 empty] | yes | no
Household Hazardous Waste Program | Administration/Documentation | 3310004 |  |  | Household Permit by Rule: 3 year PHHWCF Operational Plan, Waste Records, and Notification Document | Failure of the PHHWCF operator to assure that copies of the operation plan, all records which identify receipts and shipments of hazardous wastes from household and small quantity commercial sources and all notifications pertaining to the PHHWCF Operations/Maintenance are maintained and available upon demand by the CUPA, or authorized agency for a period of at least three years from the commencement of the PHHWCF. | 22 CCR 45 67450.25(a)(3) | 2022-07-01 | 2099-12-31 | 2022-07-01 | Existing | 11 | On Site Records | PHHWCF | Records for proper disposal, operational reports/records and notifications maintained for 3 years | 98 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF operator to assure that copies of the operation plan, all records which identify receipts and shipments of hazardous wastes from household and small quantity commercial sources and all notifications pertaining to the PHHWCF Operations/Maintenance are maintained and available upon demand by the CUPA, or authorized agency for a period of at least three years from the commencement of the PHHWCF. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/MaintenanceAdministration/Documentation | 3310014 |  |  | Household Permit by Rule: 3 year THHWCF Operational Plan, Waste Records, and Notification Document | Failure of the THHWCF operator to assure that copies of the operation plan, all records which identify receipts and shipments of hazardous wastes from household and small quantity commercial sources and all notifications pertaining to the THHWCF Operations/ Maintenance are maintained and available upon demand by the CUPA, or authorized agency for a period of at least three years from the commencement of the THHWCF. | 22 CCR 45 67450.4(h) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 12 | On Site Records | THHWCF | Records for proper disposal, operational reports/records and notifications maintained for 3 years | 98 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF operator to assure that copies of the operation plan, all records which identify receipts and shipments of hazardous wastes from household and small quantity commercial sources and all notifications pertaining to the THHWCF Operations/ Maintenance are maintained and available upon demand by the CUPA, or authorized agency for a period of at least three years from the commencement of the THHWCF. | [9 empty] | no | yes
Household Hazardous Waste Program | Administration/Documentation | 3310013 |  |  | Household Permit by Rule: PHHWCF CESQG Documentation | Failure of the PHHWCF operator to establish a separate record which identifies the name, address, and identification number of the CESQG, the type(s) and quantity(ies) of hazardous wastes accepted from small quantity commercial sources, and the fees paid to the PHHWCF for the management of those wastes. | 22 CCR 45 67450.25(a)(4), 67450.4(g) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 13 | On Site Records | PHHWCF | Records for accepting HW from a small quantity commercial source have been established | 86 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF operator to establish a separate record which identifies the name, address, and identification number of the CESQG, the type(s) and quantity(ies) of hazardous wastes accepted from small quantity commercial sources, and the fees paid to the PHHWCF for the management of those wastes. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/MaintenanceAdministration/Documentation | 3310016 |  |  | Household Permit by Rule: THHWCF CESQG Documentation | Failure of the THHWCF operator to establish a separate record which identifies the name, address, and identification number of the CESQG, the type(s) and quantity(ies) of hazardous wastes accepted from small quantity commercial sources, and the fees paid to the THHWCF for the management of those wastes. | 22 CCR 45 67450.4(g) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 14 | On Site Records | THHWCF | Records for accepting HW from a small quantity commercial source have been established | 86 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF operator to establish a separate record which identifies the name, address, and identification number of the CESQG, the type(s) and quantity(ies) of hazardous wastes accepted from small quantity commercial sources, and the fees paid to the THHWCF for the management of those wastes. | [9 empty] | no | yes
Household Hazardous Waste Program | Administration/Documentation | 3310005 |  |  | Household Permit by Rule: PHHWCF 15 Day Notification of Incident | Failure of the PHHWCF operator to submit a written report to the appropriate CUPA or authorized agency of any incidents of noncompliance with any regulatory requirement that may have occurred within 15 days of such an occurrence. | 22 CCR 45 67450.25(a)(4), 67450.4(i) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 15 | On Site Records | PHHWCF | A written report of any incident of noncompliance was submitted to the CUPA within 15 days | 90 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF operator to submit a written report to the appropriate CUPA or authorized agency of any incidents of noncompliance with any regulatory requirement that may have occurred within 15 days of such an occurrence. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/MaintenanceAdministration/Documentation | 3310015 |  |  | Household Permit by Rule: THHWCF 15 Day Notification of Incident | Failure of the THHWCF operator to submit a written report to the appropriate CUPA or authorized agency of any incidents of noncompliance with any regulatory requirement that may have occurred within 15 days of such an occurrence. | 22 CCR 45 67450.4(i) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 16 | On Site Records | THHWCF | A written report of any incident of noncompliance was submitted to the CUPA within 15 days | 90 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF operator to submit a written report to the appropriate CUPA or authorized agency of any incidents of noncompliance with any regulatory requirement that may have occurred within 15 days of such an occurrence. | [9 empty] | no | yes
Household Hazardous Waste Program | Administration/Documentation | 3310021 |  |  | Transfer of Wastes From One HHW to Another | Failure to maintain shipping papers for the transfer of HHW from one HHWCF to another. | HSC 6.5 25163(f)(2) | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 17 | On Site Records | PHHWCF/THHWCF | Maintains shipping papers for the transfer of HHW from one HHWCF to another | 75 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Failure to maintain shipping papers for the transfer of HHW from one HHWCF to another. | [9 empty] | yes | yes
Household Hazardous Waste Program | Administration/Documentation | 3310020 |  |  | Proxy delivery documentation | Failed to ensure that proxy deliveries of HHW are accompanied by a certification noting the proxy delivery's circumstances and that the proxy delivery person is not doing so for profit. | HSC 6.5 25218.5(a)(1)(A)(ii), 25218.8(b)(3)(A)(ii) | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 18 | On Site Records | PHHWCF/THHWCF | Ensures that proxy deliveries of HHW are accompanied by a certification | 71 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Failed to ensure that proxy deliveries of HHW are accompanied by a certification noting the proxy delivery's circumstances and that the proxy delivery person is not doing so for profit. | [9 empty] | yes | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330001 |  |  | Household Permit by Rule: PHHWCF Adequate Work Environment | Failure of the PHHWCF to operate with a large enough work area to accommodate all necessary personnel, storage, vehicles, and equipment. | 22 CCR 45 67450.25(a)(4), 67450.4(d)(3) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 17 19 | General Operating Requirements | PHHWCF | Operational area sufficient to accommodate all necessary personnel, storage, vehicles and equipment | 99 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to operate with a large enough work area to accommodate all necessary personnel, storage, vehicles, and equipment. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330014 |  |  | Household Permit by Rule: THHWCF Adequate Work Environment | Failure of the THHWCF to operate with a large enough work area to accommodate all necessary personnel, storage, vehicles, and equipment. | 22 CCR 45 67450.4(d)(3) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 18 20 | General Operating Requirements | THHWCF | Operational area sufficient to accommodate all necessary personnel, storage, vehicles and equipment | 99 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF to operate with a large enough work area to accommodate all necessary personnel, storage, vehicles, and equipment. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330002 |  |  | Household Permit by Rule: PHHWCF Barrier Between Operational and Storage Area | Failure of the PHHWCF to have a physical barrier to delineate the handling and storage area. | 22 CCR 45 67450.25(a)(4), 67450.4(d)(5) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 19 21 | General Operating Requirements | PHHWCF | Adequate physical barrier to delineate the handling and storage area established | 80 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to have a physical barrier to delineate the handling and storage area. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330015 |  |  | Household Permit by Rule: THHWCF Barrier Between Operational and Storage Area | Failure of the THHWCF to have a physical barrier to delineate the handling and storage area. | 22 CCR 45 67450.4(d)(5) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 20 22 | General Operating Requirements | THHWCF | Adequate physical barrier to delineate the handling and storage area established | 80 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF to have a physical barrier to delineate the handling and storage area. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330003 |  |  | Household Permit by Rule: PHHWCF Buffer Zone | Failure of the PHHWCF to operate with a significant buffer zone. | 22 CCR 45 67450.25(a)(4), 67450.4(d)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 21 23 | General Operating Requirements | PHHWCF | Operating with a significant buffer zone | 40 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to operate with a significant buffer zone. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330016 |  |  | Household Permit by Rule: THHWCF Buffer Zone | Failure of the THHWCF to operate with a significant buffer zone. | 22 CCR 45 67450.4(d)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 22 24 | General Operating Requirements | THHWCF | Operating with a significant buffer zone | 40 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF to operate with a significant buffer zone. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330004 |  |  | Household Permit by Rule: PHHWCF Bulking of Wastes | Failure of the PHHWCF to meet all requirements when bulking wastes. | 22 CCR 45 67450.25(a), 67450.4(e) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 23 25 | General Operating Requirements | PHHWCF | Requirements for Bulking Wastes are being met | 47 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to meet all requirements when bulking wastes. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330017 |  |  | Household Permit by Rule: THHWCF Bulking of Wastes | Failure of THHWCF to meet all requirements of section 67450.4(e) when bulking wastes. | 22 CCR 45 67450.4(e) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 24 26 | General Operating Requirements | THHWCF | Requirements for Bulking Wastes are being met | 47 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of THHWCF to meet all requirements of section 67450.4(e) when bulking wastes. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330005 |  |  | Household Permit by Rule: PHHWCF Operational Area Boundary Marking | Failure of the PHHWCF to operate in a location that is clearly marked to control public access. | 22 CCR 45 67450.25(a)(4), 67450.4(d)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 25 27 | General Operating Requirements | PHHWCF | Operational Area Boundary has been properly marked | 50 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to operate in a location that is clearly marked to control public access. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330018 |  |  | Household Permit by Rule: THHWCF Operational Area Boundary Marking | Failure of the THHWCF to operate in a location that is clearly marked to control public access. | 22 CCR 45 67450.4(d)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 26 28 | General Operating Requirements | THHWCF | Operational Area Boundary has been properly marked | 50 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF to operate in a location that is clearly marked to control public access. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330006 |  |  | Household Permit by Rule: PHHWCF Operational Area Continuous Base | Failure of the PHHWCF to have a continuous base that is free of cracks or gaps ad is sufficiently impervious to contain leaks, spills, and accumulated precipitation that meets the requirements of section 66264.175(b)(1). | 22 CCR 45 67450.25(a)(4)(A) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 27 29 | General Operating Requirements | PHHWCF | Continuous paved surface is sufficiently impervious to contain leaks, spills and precipitation | 95 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to have a continuous base that is free of cracks or gaps ad is sufficiently impervious to contain leaks, spills, and accumulated precipitation that meets the requirements of section 66264.175(b)(1). | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330019 |  |  | Household Permit by Rule: THHWCF Operational Area Plastic Sheeting | Failure of the THHWCF to have the area paved and covered with a plastic tarp of at least 6 mm thick and ensure all tears and punctures are repaired. | 22 CCR 45 67450.4(d)(4) | 2020-10-01 | 2099-12-31 | 2020-10-01 | Revised | 28 30 | General Operating Requirements | THHWCF | Operational area paved and covered with a plastic tarp at least 6 mm thick, tears/punctures repaired | 100 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF to have the area paved and covered with a plastic tarp of at least 6 mm thick and ensure all tears and punctures are repaired. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330007 |  |  | Household Permit by Rule: PHHWCF Roof or Canopy | Failure of the PHHWCF to have a roof or canopy that covers the handling, sorting, and bulking areas. | 22 CCR 45 67450.25(a)(4), 67450.4(d)(7) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 29 31 | General Operating Requirements | PHHWCF | Roof or canopy that covers the handling, sorting, and bulking areas is provided | 79 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to have a roof or canopy that covers the handling, sorting, and bulking areas. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330020 |  |  | Household Permit by Rule: THHWCF Roof or Canopy | Failure of the THHWCF to have a roof or canopy that covers the handling, sorting, and bulking areas. | 22 CCR 45 67450.4(d)(7) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 30 32 | General Operating Requirements | THHWCF | Roof or canopy that covers the handling, sorting, and bulking areas is provided | 79 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF to have a roof or canopy that covers the handling, sorting, and bulking areas. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330008 |  |  | Household Permit by Rule: PHHWCF Security and Lighting | Failure of the PHHWCF storage area to meet all site security requirements. | 22 CCR 45 67450.25(a)(4), 67450.4(d)(9) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 31 33 | General Operating Requirements | PHHWCF | Storage area meets all site security requirements | 51 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF storage area to meet all site security requirements. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330021 |  |  | Household Permit by Rule: THHWCF Security and Lighting | Failure of the THHWCF storage area to meet all site security requirements. | 22 CCR 45 67450.4(d)(9) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 32 34 | General Operating Requirements | THHWCF | Storage area meets all site security requirements | 51 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF storage area to meet all site security requirements. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330009 |  |  | Household Permit by Rule: PHHWCF Separate Area for Reactive and Ignitable Waste | Failure of the PHHWCF to have a storage area to store reactive and ignitable waste. | 22 CCR 45 67450.25(a)(4), 67450.4(d)(6), 66265.17(a), 66265.17(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 33 35 | General Operating Requirements | PHHWCF | Storage area to store reactive and ignitable waste provided | 59 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to have a storage area to store reactive and ignitable waste. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330022 |  |  | Household Permit by Rule: THHWCF Separate Area for Reactive and Ignitable Waste | Failure of the THHWCF to have a storage area to store reactive and ignitable waste. | 22 CCR 45 67450.4(d)(6) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 34 36 | General Operating Requirements | THHWCF | Storage area to store reactive and ignitable waste provided | 59 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF to have a storage area to store reactive and ignitable waste. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330010 |  |  | Household Permit by Rule: PHHWCF Traffic Control | Failure of the PHHWCF to have traffic control which is one way, directed by staff, and assures all persons remain in their car during waste transfer, unless requested to exit the vehicle to provide access to the waste being delivered. | 22 CCR 45 67450.25(a)(4), 67450.4(d)(10); HSC 6.5 25218.3(e) | 11/01/2017 07/01/2023 | 2099-12-31 | 11/01/2017 07/01/2023 | Revised | 35 37 | General Operating Requirements | PHHWCF | Staff direct one way Maintains traffic controls and assure ensures all persons remain in vehicles except as directed during waste transfer | 138 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to have traffic control which is one way, directed by staff, and assures all persons remain in their car during waste transfer, unless requested to exit the vehicle to provide access to the waste being delivered. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330023 |  |  | Household Permit by Rule: THHWCF Traffic Control | Failure of the THHWCF to have traffic control which is one way, directed by staff, and assures all persons remain in their car during waste transfer, unless requested to exit the vehicle to provide access to the waste being delivered. | 22 CCR 45 67450.4(d)(10); HSC 6.5 25218.3(e) | 11/01/2017 07/01/2023 | 2099-12-31 | 11/01/2017 07/01/2023 | Revised | 36 38 | General Operating Requirements | THHWCF | Staff direct one way Maintains traffic controls and assure ensures all persons remain in vehicles except as directed during waste transfer | 138 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF to have traffic control which is one way, directed by staff, and assures all persons remain in their car during waste transfer, unless requested to exit the vehicle to provide access to the waste being delivered. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330011 |  |  | Household Permit by Rule: PHHWCF "Danger Hazardous Waste Area" Posting | Failure of the PHHWCF to post around the area signs stating "Danger! Hazardous Waste Area - Unauthorized Personnel Keep Out" and are visible at 25 ft. | 22 CCR 45 67450.25(a)(4), 67450.4(d)(8) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 37 39 | General Operating Requirements | PHHWCF | Sign posted w/25 ft visibility saying "Danger! Hazardous Waste Area-Unauthorized Personnel Keep Out" | 100 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to post around the area signs stating "Danger! Hazardous Waste Area - Unauthorized Personnel Keep Out" and are visible at 25 ft. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330024 |  |  | Household Permit by Rule: THHWCF "Danger Hazardous Waste Area" Posting | Failure of the THHWCF to post around the area signs stating "Danger! Hazardous Waste Area - Unauthorized Personnel Keep Out" and are visible at 25 ft. | 22 CCR 45 67450.4(d)(8) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 38 40 | General Operating Requirements | THHWCF | Sign posted w/25 ft visibility saying "Danger! Hazardous Waste Area-Unauthorized Personnel Keep Out" | 100 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF to post around the area signs stating "Danger! Hazardous Waste Area - Unauthorized Personnel Keep Out" and are visible at 25 ft. | [9 empty] | no | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330012 |  |  | Household Permit by Rule: PHHWCF Exceeded Accumulation Time of 1 year | Failure of the PHHWCF to dispose of hazardous waste within one year of accumulation start date. | 22 CCR 45 67450.25(a)(6) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 39 41 | Observations | PHHWCF | Hazardous waste disposed of within one year of accumulation start date | 70 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF to dispose of hazardous waste within one year of accumulation start date. | [9 empty] | yes | no
Household Hazardous Waste Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 3350001 |  |  | Household Permit by Rule: PHHWCF Accepting HW from CEVSQG | Failure of the PHHWCF operator to obtain authorization to accept waste from CEVSQG's and/or failure to keep Household HW separate from the CESQG waste and maintain a separate receiving area or separate operational times for the CESQG and households. | 22 CCR 45 67450.25(a)(3)(B), 67450.4(b)(9) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 40 42 | Observations | PHHWCF | Authorization to take CESQG waste, CESQG waste received/kept separate, or accepted at different time | 100 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the PHHWCF operator to obtain authorization to accept waste from CEVSQG's and/or failure to keep Household HW separate from the CESQG waste and maintain a separate receiving area or separate operational times for the CESQG and households. | [9 empty] | yes | no
Household Hazardous Waste Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 3350003 |  |  | Household Permit by Rule: THHWCF Accepting HW from CEVSQG | Failure of the THHWCF operator to obtain authorization to accept waste from CEVSQG's and/or failure to keep Household HW separate from the CESQG waste and maintain a separate receiving area or separate operational times for the CESQG and households. | 22 CCR 45 67450.4(b)(9) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 41 43 | Observations | THHWCF | Authorization to take CESQG waste, CESQG waste received/kept separate, or accepted at different time | 100 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF operator to obtain authorization to accept waste from CEVSQG's and/or failure to keep Household HW separate from the CESQG waste and maintain a separate receiving area or separate operational times for the CESQG and households. | [9 empty] | no | yes
Household Hazardous Waste Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 3350002 |  |  | Household Permit by Rule: THHWCF Closure and Documentation | Failure of the THHWCF operator to remove and decontaminate structures, equipment, soil and all collected materials and wastes within 144 hours after termination of the session and assure that all contaminated materials and wastes were removed by a registered hazardous waste transporter. | 22 CCR 45 67450.4(f) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 42 44 | Observations | THHWCF | Removed/deconned structures, equipment, soil & collected wastes within 144 hours using reg. hauler | 98 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the THHWCF operator to remove and decontaminate structures, equipment, soil and all collected materials and wastes within 144 hours after termination of the session and assure that all contaminated materials and wastes were removed by a registered hazardous waste transporter. | [9 empty] | no | yes
Household Hazardous Waste Program | Administration/Documentation | 3310017 |  |  | Materials Exchange Program: Quality Assurance Program/Plan | Failure of a HHW program to have a complete quality assurance program which sets guidelines for participating container screening, acceptance, and evaluation, as well as when containers no longer meet protocols and becomes a waste. | HSC 6.5 25218.11.5 | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 43 45 | Materials Exchange Program | PHHWCF | Quality Assurance Program has been completed by HHW as required for Materials Exchange Program | 94 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of a HHW program to have a complete quality assurance program which sets guidelines for participating container screening, acceptance, and evaluation, as well as when containers no longer meet protocols and becomes a waste. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330025 |  |  | Materials Exchange Program: Notification to user | Materials exchange program is not informing customers to use materials in a manner consistent with their original use. | HSC 25218.12(a)(2) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 44 46 | Materials Exchange Program | PHHWCF | Customers are being informed to use materials in a manner consistent with original use | 86 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Materials exchange program is not informing customers to use materials in a manner consistent with their original use. | [9 empty] | yes | no
Household Hazardous Waste Program | Administration/Documentation | 3310018 |  |  | Materials Exchange Program: Information from re-distributors | Materials exchange program failed to collect required information from commercial entities who will re-distribute materials received from the program. | HSC 25218.12(b)(1) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 45 47 | Materials Exchange Program | PHHWCF | Required information has been collected from commercial entities that redistribute materials | 93 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Materials exchange program failed to collect required information from commercial entities who will re-distribute materials received from the program. | [9 empty] | yes | no
Household Hazardous Waste Program | Administration/Documentation | 3310019 |  |  | Materials Exchange Program: Annual report from re-distributors | Materials exchange program failed to collect required annual report from commercial entities who accepted materials for the purpose of redistribution. | HSC 25218.12(b)(2) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 46 48 | Materials Exchange Program | PHHWCF | Annual report collected from commercial entities that redistribute materials | 76 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Materials exchange program failed to collect required annual report from commercial entities who accepted materials for the purpose of redistribution. | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330026 |  |  | Materials Exchange Program: Participation of non-compliant re-distributors | Materials exchange program failed to stop supplying materials to commercial entities who accepted materials for the purpose of redistribution but who have not provided required information or annual report. | HSC 25218.12(b)(3) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 47 49 | Materials Exchange Program | PHHWCF | Stopped supplying materials to commercial entities who failed to provide info for annual report | 95 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Materials exchange program failed to stop supplying materials to commercial entities who accepted materials for the purpose of redistribution but who have not provided required information or annual report | [9 empty] | yes | no
Household Hazardous Waste Program | Operations/Maintenance | 3330013 |  |  | Household Permit by Rule: Recycle-Only Permit Exemption Requirements | Failure of the operator of a recycle-only household hazardous waste collection facility not operating under a hazardous waste facilities permit to comply with notification and operation requirements. | HSC 6.5 25218.2, 25218.8 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 48 50 | Notification and Operation | Recycle-Only HHW | Recycle-only HHW collection facility complied with notification and operation requirements | 90 | yes | yes | yes | yes | yes | yes | yes | Class 2 | yes |  | 30 | Failure of the operator of a recycle-only household hazardous waste collection facility not operating under a hazardous waste facilities permit to comply with notification and operation requirements. | [9 empty] | yes | yes
Household Hazardous Waste Program | Administration/Documentation | 3310 |  |  | HHW-Administration/Documentation - General | Administration/Documentation - General | 22 CCR Multiple Chapters Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 49 51 | General Facility Requirements |  | Administration/Documentation - General | 38 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Administration/Documentation - General | [9 empty] | yes | yes
Household Hazardous Waste Program | Administration/Documentation | 3315 |  |  | HHW-Administration/Documentation - General Local Ordinance | Administration/Documentation - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 50 52 | General Facility Requirements |  | Administration/Documentation - General Local Ordinance | 54 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Administration/Documentation - General Local Ordinance | [9 empty] | yes | yes
Household Hazardous Waste Program | Training | 3320 |  |  | HHW-Training - General | Training - General | 22 CCR Multiple Chapters Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 51 53 | General Facility Requirements |  | Training - General | 18 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Training - General | [9 empty] | yes | yes
Household Hazardous Waste Program | Training | 3325 |  |  | HHW-Training - General Local Ordinance | Training - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 52 54 | General Facility Requirements |  | Training - General Local Ordinance | 34 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Training - General Local Ordinance | [9 empty] | yes | yes
Household Hazardous Waste Program | Operations/Maintenance | 3330 |  |  | HHW-Operations/Maintenance - General | Operations/Maintenance - General | 22 CCR Multiple Chapters Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 53 55 | General Facility Requirements |  | Operations/Maintenance - General | 32 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Operations/Maintenance - General | [9 empty] | yes | yes
Household Hazardous Waste Program | Operations/Maintenance | 3335 |  |  | HHW-Operations/Maintenance - General Local Ordinance | Operations/Maintenance - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 54 56 | General Facility Requirements |  | Operations/Maintenance - General Local Ordinance | 48 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Operations/Maintenance - General Local Ordinance | [9 empty] | yes | yes
Household Hazardous Waste Program | Release/Leaks/Spills | 3340 |  |  | HHW-Release/Leaks/Spills - General | Release/Leaks/Spills - General | 22 CCR Multiple Chapters Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 55 57 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes | Yes
Household Hazardous Waste Program | Release/Leaks/Spills | 3345 |  |  | HHW-Release/Leaks/Spills - General Local Ordinance | Release/Leaks/Spills - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 56 58 | General Facility Requirements |  | Release/Leaks/Spills - General Local Ordinance | 46 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Release/Leaks/Spills - General Local Ordinance | [9 empty] | yes | yes
Household Hazardous Waste Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 3350 |  |  | HHW-Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 22 CCR Multiple Chapters Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 57 59 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | yes | yes
Household Hazardous Waste Program | Abandonment/Illegal Disposal/Unauthorized Treatment | 3355 |  |  | HHW-Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 58 60 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | 77 | yes | yes | yes | yes | yes | yes | yes | Minor | yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | [9 empty] | yes | yes

## TP
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | TP full list | TP CA | TP CECL | TP CEL | TP CESQT | TP CESW | TP PBR
Tiered Permitting | Abandonment/Illegal Disposal/Unauthorized Treatment | 3250005 |  |  | Treatment: Unauthorized Treatment | Failure of a storage facility, treatment facility, transfer facility, resource recovery facility, or disposal site to accept, treat, store, or dispose of a hazardous waste at the facility, area, or site, without to obtain a hazardous waste facilities permit, or other grant of authorization, prior to accepting, treating, storing, or disposing of a hazardous waste at the facility, area, or site. from the department, or a permit-by-rule, conditional authorization, or conditional exemption permit from the CUPA | HSC 6.5 25201(a) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 1 | File Review | All Tiers | Obtained a permit to treat hazardous waste | 42 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure of a storage facility, treatment facility, transfer facility, resource recovery facility, or disposal site to accept, treat, store, or dispose of a hazardous waste at the facility, area, or site, without to obtain a hazardous waste facilities permit, or other grant of authorization, prior to accepting, treating, storing, or disposing of a hazardous waste at the facility, area, or site. from the department, or a permit-by-rule, conditional authorization, or conditional exemption permit from the CUPA |  |  | OBSERVATION: Owner/Operator failed to obtain aA permit or grant of authorization to treat HW has not been obtained. [ENTER SPECIFIC HAZARDOUS WASTE TREATMENT ACTIVITY OBSERVED] CORRECTIVE ACTION: Immediately submit all documentation necessary to obtain a permit or grant of authorization to treat HW by permit-by-rule, conditional authorization, or conditional exemption for this facility to the CUPA. | OBSERVATION: The owner or operator failed to obtain a permit to treat HW. No owner or operator of a storage facility, treatment facility, transfer facility, resource recovery facility, or disposal site shall accept, treat, store, or dispose of HW at the facility, area, or site, unless the owner or operator holds a HW facilities permit or other grant of authorization from the DTSC to use and operate the facility, area, or site, or the owner or operator is operating under a permit-by-rule pursuant to the DTSC's regulations, or a grant of conditional authorization or conditional exemption pursuant to this chapter. CORRECTIVE ACTIONS: Immediately obtain a permit to treat HW by permit-by-rule, conditional authorization, or conditional exemption for this facility issued from the CUPA. | [5 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Administration/Documentation | 3210043 |  |  | General: Electronic data | Failure to report program data electronically. | HSC 6.11 25404(e)(4) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 2 | File Review | All Tiers | Program data reported in CERS | 29 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to report program data electronically. |  |  | OBSERVATION: Generator failed to report program data electronically. CORRECTIVE ACTION: Complete all required electronic reporting in CERS. [Specify] | [6 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Administration/Documentation | 3210004 |  |  | Conditionally Exempt: Treatment Notification | Failure to electronically submit the signature page for the onsite treatment notification. | HSC 6.5 25201.5(d)(7) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 3 | File Review | CE | Onsite CE HW Treatment Notification Information submitted electronically | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to electronically submit the signature page for the onsite treatment notification. |  |  | OBSERVATION: Owner/Operator did not submit Onsite HW Treatment notification information to the CUPA sixty (60) days prior to beginning the first treatment. CORRECTIVE ACTION: Submit the required Onsite HW Treatment notification to the CUPA. | OBSERVATION: A notification for treating HW onsite has not been submitted to the CUPA. No person may treat HW onsite without submitting notification information sixty (60) days prior to beginning the first treatment of hazardous waste. CORRECTIVE ACTION: Immediately submit the required hazardous waste treatment notification to the CUPA for review. | OBSERVATION: Notification information for treating HW onsite has not been submitted to the CERS. No person may treat HW onsite without submitting notification information sixty (60) days prior to beginning the first treatment of waste. CORRECTIVE ACTION: Immediately submit the required notification information to the CERS for review by the CUPA. |  |  |  |  | yes | No | Yes | Yes | Yes | Yes | No
Tiered Permitting | Administration/Documentation | 3210046 |  |  | Conditionally Exempt Treatment: Generator and Unit Information | Failure to identify the following information in CERS: all generator information, all Conditionally Exempt treatment units, accurately list number of tanks and containers in each unit, and plot plan/map that shows unit locations are properly Identified. | HSC 6.5 25201.5(d)(7) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 4 | File Review | CE | Generator and treatment unit information, and unit location map submitted in CERS | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to identify the following information in CERS: all generator information, all Conditionally Exempt treatment units, accurately list number of tanks and containers in each unit, and plot plan/map that shows unit locations are properly Identified. |  |  | OBSERVATION: Owner/Operator failed to identify the following information in CERS: all generator information, all Conditional Exempt treatment units, accurately list number of tanks and containers in each unit, and/or submit plot plan/map that shows unit locations. CORRECTIVE ACTION: Correctly report in CERS the items noted above as incomplete or incorrect. | [6 empty] | Yes | No | Yes | Yes | Yes | Yes | No
Tiered Permitting | Administration/Documentation | 3210009 |  |  | Conditionally Exempt: Tiered Permit Unit Amendment Notification | Failure to electronically submit to the CUPA an amended notification within 30 days of any change in operation which necessitates modifying any of the information submitted in the notification. | HSC 6.5 25201.5(i) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 5 | File Review | CE | Amended Onsite CE HW Treatment Notification Information submitted electronically | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit to the CUPA an amended notification within 30 days of any change in operation which necessitates modifying any of the information submitted in the notification. |  |  | OBSERVATION: Owner/Operator did not submit amended Onsite HW Treatment notification information to the CUPA within 30 days of a change in operation. CORRECTIVE ACTION: Submit the amended notification information to the CUPA. | OBSERVATION: An amended notification for treating HW onsite has not been submitted to the CUPA. A generator shall submit amended notification information within 30 days of any change in operation which necessitates modifying any of the information submitted in the initial notification. CORRECTIVE ACTION: Immediately submit the required amended notification information to the CUPA for review. | OBSERVATION: Amended notification information for treating HW onsite has not been submitted to the CERS. A generator shall submit amended notification information within 30 days of any change in operation which necessitates modifying any of the information submitted in the initial notification. CORRECTIVE ACTION: Immediately submit the required amended notification information to the CERS for review by the CUPA. |  |  |  |  | Yes | No | Yes | Yes | Yes | Yes | No
Tiered Permitting | Administration/Documentation | 3210003 |  |  | Conditional Authorization: Treatment Notification | Failure to electronically submit the signature page for the onsite treatment notification. | HSC 6.5 25200.3(e) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 6 | File Review | CA | Onsite CA HW Treatment Notification Information submitted electronically | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to electronically submit the signature page for the onsite treatment notification. |  |  | OBSERVATION: Owner/Operator did not submit Onsite Hazardous Waste Treatment notification to the CUPA sixty (60) days prior to beginning the first treatment of hazardous waste. CORRECTIVE ACTION: Submit the required Onsite Hazardous Waste Treatment notification to the CUPA. | OBSERVATION: A notification for treating hazardous waste onsite has not been submitted to the CUPA. No person may treat hazardous waste onsite without submitting notification sixty (60) days prior to beginning the first treatment of hazardous waste. CORRECTIVE ACTION: Immediately submit the required hazardous waste treatment notification to the CUPA for review. | OBSERVATION: Notification information for treating hazardous waste onsite has not been submitted to CERS. No person may treat hazardous waste onsite without submitting notification sixty (60) days prior to beginning the first treatment of hazardous waste. CORRECTIVE ACTION: Immediately submit the required hazardous waste treatment notification to CERS for review by the CUPA. |  |  |  |  | Yes | Yes | No | No | No | No | No
Tiered Permitting | Administration/Documentation | 3210045 |  |  | Conditional Authorization Treatment: Generator and Unit Information | Failure to identify the following information in CERS: all generator information, all Conditional Authorization treatment units, accurately list number of tanks and containers in each unit, and plot plan/map that shows unit locations are properly Identified. | HSC 6.5 25200.3(e)(3) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 7 | File Review | CA | Generator and treatment unit information, and unit location map submitted in CERS | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to identify the following information in CERS: all generator information, all Conditional Authorization treatment units, accurately list number of tanks and containers in each unit, and plot plan/map that shows unit locations are properly Identified. |  |  | OBSERVATION: Owner/Operator failed to identify the following information in CERS: all generator information, all Conditional Authorization treatment units, accurately list number of tanks and containers in each unit, and/or submit plot plan/map that shows unit locations. CORRECTIVE ACTION: Correctly report in CERS the items noted above as incomplete or incorrect. | [6 empty] | Yes | Yes | No | No | No | No | No
Tiered Permitting | Administration/Documentation | 3210008 |  |  | Conditionally Authorization: Tiered Permit Unit Amendment Notification | Failure to electronically submit to the CUPA an amended notification within 30 days of any change in operation which necessitates modifying any of the information submitted in the notification. | HSC 6.5 25200.3(k) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 8 | File Review | CA | Amended Onsite CA HW Treatment Notification Information submitted electronically | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit to the CUPA an amended notification within 30 days of any change in operation which necessitates modifying any of the information submitted in the notification. |  |  | OBSERVATION: Owner/Operator did not submit amended Onsite HW Treatment notification information to the CUPA within 30 days of a change in operation. CORRECTIVE ACTION: Submit the amended notification information to the CUPA. | OBSERVATION: An amended notification for treating HW onsite has not been submitted to the CUPA. A generator shall submit amended notification information within 30 days of any change in operation which necessitates modifying any of the information submitted in the initial notification. CORRECTIVE ACTION: Immediately submit the required amended notification information to the CUPA for review. | OBSERVATION: Amended notification information for treating HW onsite has not been submitted to the CERS. A generator shall submit amended notification information within 30 days of any change in operation which necessitates modifying any of the information submitted in the initial notification. CORRECTIVE ACTION: Immediately submit the required amended notification information to the CERS for review by the CUPA. |  |  |  |  | Yes | Yes | No | No | No | No | No
Tiered Permitting | Administration/Documentation | 3210025 |  |  | Conditional Authorization: Financial Assurance Documentation | Failure to prepare, failure to prepare correctly, and/or failure to submit to the UPA, the Certification of Financial Assurance, a written estimate of the cost of closing each unit, or an approved financial assurance mechanism, if applicable. | 22 CCR 45 67450.13(a)(1), (b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 9 | File Review | CA | Completed and submitted a Cert of Financial Assurance, Closure Cost Estimate, & Fin Assurance Mech | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare, failure to prepare correctly, and/or failure to submit to the UPA, the Certification of Financial Assurance, a written estimate of the cost of closing each unit, or an approved financial assurance mechanism, if applicable. |  |  | OBSERVATION: Owner/Operator did not prepare, did not prepare correctly, and/or did not submit to the UPA, the Certification of Financial Assurance, a written estimate of closure costs, or an approved financial assurance mechanism, if applicable. CORRECTIVE ACTION: Correctly prepare and submit to the UPA, the Certification of Financial Assurance, written estimate of closure costs, and an approved financial assurance mechanism. | OBSERVATION: A written estimate of closure costs for the fixed treatment unit(s) has not been submitted to the CUPA. A owner/operator shall prepare a written estimate of the cost of closing each unit. CORRECTIVE ACTION: Submit the written estimate of closure costs for financial assurance for each unit to the CUPA. | OBSERVATION: A written estimate of closure costs for the fixed treatment unit(s) has not been submitted to the CERS. A owner/operator shall prepare a written estimate of the cost of closing each unit. CORRECTIVE ACTION: Submit the written estimate of closure costs for financial assurance for each unit to the CERS. |  |  |  |  | Yes | Yes | No | No | No | No | No
Tiered Permitting | Administration/Documentation | 3210027 |  |  | Conditional Authorization: Closure Cost Estimate - Inflation Adjustment | Failure to adjust Closure Cost Estimate for inflation by March 1st. | 22 CCR 45 67450.13(a)(2) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 10 | File Review | CA | Inflation adjustment to the Closure Cost Estimate was completed by March 1 of each year | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to adjust Closure Cost Estimate for inflation by March 1st. |  |  | OBSERVATION: Owner/Operator did not adjust for inflation by March 1 of each year. CORRECTIVE ACTION: Ensure that the inflation adjustment to the closure cost estimate is completed by March 1 of each year. Submit copy of closure cost adjustment to CERS. | OBSERVATION: An adjustment for the closure cost estimate was not completed by March 1 of each year. The Owner/Operator or Generator shall adjust the closure cost estimate for inflation by March 1 of each year. CORRECTIVE ACTION: Ensure that the closure cost estimate is adjusted for inflation by March 1 of each year. | OBSERVATION: An adjustment for the written closure cost estimate was not submitted to the CERS by March 1 of each year. The Owner/Operator or Generator shall adjust the closure cost estimate for inflation by March 1 of each year. CORRECTIVE ACTION: Submit the adjusted written closure cost estimate to the CERS. |  |  |  |  | Yes | Yes | No | No | No | No | No
Tiered Permitting | Administration/Documentation | 3210029 |  |  | Conditional Authorization: Closure Cost Estimate Adjustment After Changes/Maintain Latest Estimate | Failure to update the closure cost estimate whenever a change occurs that increases the cost of closure, and/or failure to maintain a copy of the latest closure cost estimate at the facility during the operating life of the facility. | 22 CCR 45 67450.13(a)(4) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 11 | File Review | CA | Closure Cost Estimate was revised upon increase in closure cost & latest estimate maintained | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update the closure cost estimate whenever a change occurs that increases the cost of closure, and/or failure to maintain a copy of the latest closure cost estimate at the facility during the operating life of the facility. |  |  | OBSERVATION: Owner/Operator did not revise the closure cost estimate when a change occurred that increased the cost of closure, and/or did not maintain a copy of the latest closure cost estimate at the facility. CORRECTIVE ACTION: Update closure cost estimate to address increased costs and submit to CERS, and maintain copy of latest closure cost estimate at the facility for the operating life of the facility. Ensure that the closure cost estimate is revised whenever changes occur that increase the cost of closure. | OBSERVATION: A revised written closure cost estimate for changes in the Closure Plan and/or a change occurs that increases the cost of closure was not found in the records at the facility. The Owner/Operator shall maintain the latest written closure cost estimate at the facility. CORRECTIVE ACTION: Ensure that the latest written closure cost estimate is maintained at the facility whenever a change in the Closure Plan and/or an increase in the cost of closure occurs. | OBSERVATION: A revised written closure cost estimate was not submitted to the CERS. The written closure cost estimate shall be revised whenever a Closure Plan and/or cost increase for closure occurs. CORRECTIVE ACTION: Submit the revised written closure cost estimate to the CERS. |  |  |  |  | Yes | Yes | No | No | No | No | No
Tiered Permitting | Administration/Documentation | 3210024 |  |  | Conditional Authorization: Phase I Requirements | Failure to complete and/or submit a Phase I Checklist to DTSC within one year of commencing operations, and after release of hazardous waste or constituents from any solid or hazardous waste management unit. | HSC 6.5 25200.14(b)(1) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 12 | File Review | CA | Phase 1 Environmental Assessment Checklist submitted | 52 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete and/or submit a Phase I Checklist to DTSC within one year of commencing operations, and after release of hazardous waste or constituents from any solid or hazardous waste management unit. |  |  | OBSERVATION: Owner/Operator failed to complete and/or submit a Phase I Environmental Assessment Checklist to DTSC within one year of commencing operations, or after release of hazardous waste or constituents from any solid or hazardous waste management unit. CORRECTIVE ACTION: Submit the required Phase I Environmental Assessment Checklist to DTSC and the UPA. | OBSERVATION: A Tiered Permitting Phase I Environmental Assessment Checklist (DTSC Form 1151) has not been submitted to the CUPA. An Owner/Operator/Generator is required to complete and file a phase I environmental assessment with the CUPA one year from the date that the facility or generator becomes authorized to operate. CORRECTIVE ACTION: Immediately submit the required Tiered Permitting Phase I Environmental Assessment Checklist to the CUPA. | [5 empty] | Yes | Yes | No | No | No | No | No
Tiered Permitting | Administration/Documentation | 3210002 |  |  | Permit by Rule: Treatment Notification | Failure to electronically submit the signature page for the onsite treatment notification. | 22 CCR 45 67450.2(b)(2) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 13 | File Review | PBR | Onsite PBR HW Treatment Notification Information submitted electronically | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to electronically submit the signature page for the onsite treatment notification. |  |  | OBSERVATION: Owner/Operator did not submit Onsite Hazardous Waste Treatment Notification to the CUPA sixty (60) days prior to beginning the first treatment. CORRECTIVE ACTION: Submit the required Onsite Hazardous Waste Treatment Notification to the CUPA. | OBSERVATION: A notification for treating hazardous waste onsite has not been submitted to the CUPA. No person may treat hazardous waste onsite without submitting notification sixty (60) days prior to beginning the first treatment of hazardous waste. CORRECTIVE ACTION: Immediately submit the required Hazardous Waste Treatment notification to the CUPA for review and authorization to operate. | OBSERVATION: Notification information for treating hazardous waste onsite has not been submitted to CERS. No person may treat hazardous waste onsite without submitting notification sixty (60) days prior to beginning the first treatment of hazardous waste. CORRECTIVE ACTION: Immediately submit the required Hazardous Waste Treatment notification to CERS for review by the CUPA. |  |  |  |  | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210044 |  |  | Permit-by-Rule Treatment: Generator and Unit Information | Failure to identify the following information in CERS: all generator information, all Permit-by-rule treatment units, accurately list number of tanks and containers in each unit, and plot plan/map that shows unit locations are properly Identified. | 22 CCR 45 67450.2(b)(3)(B) and (G) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 14 | File Review | PBR | Generator and treatment unit information, and unit location map submitted in CERS | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to identify the following information in CERS: all generator information, all Permit-by-rule treatment units, accurately list number of tanks and containers in each unit, and plot plan/map that shows unit locations are properly Identified. |  |  | OBSERVATION: Owner/Operator failed to identify one or more of the following in CERS: all generator information, all Permit-by-rule treatment units, accurately list number of tanks and containers in each unit, and/or plot plan/map that shows unit locations are properly Identified. CORRECTIVE ACTION: Correctly report in CERS the items noted above as incomplete or incorrect. | [6 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting Program | Administration/Documentation | 3210053 |  |  | Permit By Rule: Tiered Permit Annual Notification | Failure to electronically submit to the CUPA an annual Tiered Permit notification. | 22 CCR 45 67450.3(c)(1) | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 15 | File Review | PBR | Annual Tiered Permit notification electronically submitted to the CUPA | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit to the CUPA an annual Tiered Permit notification. |  |  | OBSERVATION: Owner/Operator failed to electronically submit to the CUPA an annual Tiered Permit notification. CORRECTIVE ACTION: Electronically submit the annual Tiered Permit notification in CERS. | [6 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210007 |  |  | Permit by Rule: Tiered Permit Unit Amendment Notification | Failure to electronically submit to the CUPA an amended notification within 30 days of any change in operation which necessitates modifying any of the information submitted in the most recent notification. | 22 CCR 45 67450.3(c)(2) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 15 16 | File Review | PBR | Amended Onsite PBR HW Treatment Notification Information submitted electronically | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to electronically submit to the CUPA an amended notification within 30 days of any change in operation which necessitates modifying any of the information submitted in the most recent notification. |  |  | OBSERVATION: Owner/Operator did not submit amended Onsite HW Treatment notification information to the CUPA within 30 days of a change in operation. CORRECTIVE ACTION: Submit the amended notification information to the CUPA. | OBSERVATION: An amended notification for treating HW onsite has not been submitted to the CUPA. A generator shall submit amended notification information within 30 days of any change in operation which necessitates modifying any of the information submitted in the initial notification. CORRECTIVE ACTION: Immediately submit the required amended notification information to the CUPA for review. | OBSERVATION: Amended notification information for treating HW onsite has not been submitted to the CERS. A generator shall submit amended notification information within 30 days of any change in operation which necessitates modifying any of the information submitted in the initial notification. CORRECTIVE ACTION: Immediately submit the required amended notification information to the CERS for review by the CUPA. |  |  |  |  | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210026 |  |  | Permit by Rule: Financial Assurance Documentation | Failure to prepare, failure to prepare correctly, and/or failure to submit to the UPA, the Certification of Financial Assurance, a written estimate of the cost of closing each unit, or an approved financial assurance mechanism, if applicable. | 22 CCR 45 67450.13(a)(1), (b) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 16 17 | File Review | PBR | Completed and submitted a Cert of Financial Assurance, Closure Cost Estimate, & Fin Assurance Mech | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare, failure to prepare correctly, and/or failure to submit to the UPA, the Certification of Financial Assurance, a written estimate of the cost of closing each unit, or an approved financial assurance mechanism, if applicable. |  |  | OBSERVATION: Owner/Operator did not prepare, did not prepare correctly, and/or did not submit to the UPA, the Certification of Financial Assurance, a written estimate of closure costs, or an approved financial assurance mechanism, if applicable. CORRECTIVE ACTION: Correctly prepare and submit to the UPA, the Certification of Financial Assurance, written estimate of closure costs, and an approved financial assurance mechanism. | OBSERVATION: A written estimate of closure costs for the fixed treatment unit(s) has not been submitted to the CUPA. A owner/operator shall prepare a written estimate of the cost of closing each unit. CORRECTIVE ACTION: Submit the written estimate of closure costs for financial assurance for each unit to the CUPA. | OBSERVATION: A written estimate of closure costs for the fixed treatment unit(s) has not been submitted to the CERS. A owner/operator shall prepare a written estimate of the cost of closing each unit. CORRECTIVE ACTION: Submit the written estimate of closure costs for financial assurance for each unit to the CERS. |  |  |  |  | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210028 |  |  | Permit by Rule: Closure Cost Estimate - Inflation Adjustment | Failure to adjust Closure Cost Estimate for inflation by March 1st | 22 CCR 45 67450.13(a)(2) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 17 18 | File Review | PBR | Inflation adjustment to the Closure Cost Estimate was completed by March 1 of each year | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to adjust Closure Cost Estimate for inflation by March 1st. |  |  | OBSERVATION: Owner/Operator did not adjust for inflation by March 1 of each year. CORRECTIVE ACTION: Ensure that the inflation adjustment to the closure cost estimate is completed by March 1 of each year. Submit copy of closure cost adjustment to CERS. | OBSERVATION: An adjustment for the closure cost estimate was not completed by March 1 of each year. The Owner/Operator or Generator shall adjust the closure cost estimate for inflation by March 1 of each year. CORRECTIVE ACTION: Ensure that the closure cost estimate is adjusted for inflation by March 1 of each year. | OBSERVATION: An adjustment for the written closure cost estimate was not submitted to the CERS by March 1 of each year. The Owner/Operator or Generator shall adjust the closure cost estimate for inflation by March 1 of each year. CORRECTIVE ACTION: Submit the adjusted written closure cost estimate to the CERS. |  |  |  |  | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210030 |  |  | Permit by Rule: Closure Cost Estimate Adjustment After Changes/Maintain Latest Estimate | Failure to update the closure cost estimate whenever a change occurs that increases the cost of closure, and/or failure to maintain a copy of the latest closure cost estimate at the facility during the operating life of the facility. | 22 CCR 45 67450.13(a)(3) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 18 19 | File Review | PBR | Closure Cost Estimate was revised upon increase in closure cost & latest estimate maintained | 92 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to update the closure cost estimate whenever a change occurs that increases the cost of closure, and/or failure to maintain a copy of the latest closure cost estimate at the facility during the operating life of the facility. |  |  | OBSERVATION: Owner/Operator did not revise the closure cost estimate when a change occurred that increased the cost of closure, and/or did not maintain a copy of the latest closure cost estimate at the facility. CORRECTIVE ACTION: Update closure cost estimate to address increased costs and submit to CERS, and maintain copy of latest closure cost estimate at the facility for the operating life of the facility. Ensure that the closure cost estimate is revised whenever changes occur that increase the cost of closure. | OBSERVATION: A revised closure cost estimate for changes in the Closure Plan and/or a change occurs that increases the cost of closure was not found in the records at the facility. The Owner/Operator shall maintain the latest closure cost estimate at the facility. CORRECTIVE ACTION: Ensure that the latest closure cost estimate is maintained at the facility whenever a change in the Closure Plan and/or an increase in the cost of closure occurs. | OBSERVATION: A revised written closure cost estimate was not submitted to the CERS. The written closure cost estimate shall be revised whenever a Closure Plan and/or cost increase for closure occurs. CORRECTIVE ACTION: Submit the revised written closure cost estimate to the CERS. |  |  |  |  | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210022 |  |  | Permit by Rule: Phase 1 Requirements | Failure to complete and/or submit a Phase I Checklist to DTSC within one year of commencing operations, and after release of hazardous waste or constituents from any solid or hazardous waste management unit. | 22 CCR 45 67450.3, 67450.7, HSC 6.5 25200.14(b)(1) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 19 20 | File Review | PBR | Phase 1 Environmental Assessment Checklist submitted | 52 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to complete and/or submit a Phase I Checklist to DTSC within one year of commencing operations, and after release of hazardous waste or constituents from any solid or hazardous waste management unit. |  |  | OBSERVATION: Owner/Operator failed to complete and/or submit a Phase I Environmental Assessment Checklist to DTSC within one year of commencing operations, or after release of hazardous waste or constituents from any solid or hazardous waste management unit. CORRECTIVE ACTION: Submit the required Phase 1 Environmental Assessment Checklist to DTSC and to the UPA. | OBSERVATION: The Owner/Operator failed to complete a corrective action program at the facility. An Owner/Operator shall complete a corrective action program at the facility that consists of a phase 1 environmental assessment and subsequent corrective action as necessary to protect human health and the environment for all releases of hazardous waste or constituents from any solid or hazardous waste management unit a the facility, regardless of the time at which waste was placed in the unit. A phase 1 environmental assessment shall be conducted and a Phase 1 Environmental Assessment Checklist shall be submitted within one year of the initial notification. CORRECTIVE ACTIONS: Submit a copy of the Phase 1 Environmental Assessment Checklist to the CUPA within one year of the initial notification. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Release/Leaks/Spills | 3240002 |  |  | PBR Treatment: Notification of Emergency/Incident within 15 Days | Failure to notify the Department of a release, fire, and / or explosion within 15 days and include the following: 1) Name, address, and telephone number of the owner or operator; 2) Name, address, and telephone number of the facility; 3) Date, time, and type of incident (e.g., fire, explosion); 4) Name and quantity of material(s) involved; 5) The extent of injuries, if any; 6) An assessment of actual or potential hazards to human health or the environment, where this is applicable; and 7) Estimated quantity and disposition of recovered material that resulted from the incident. | 22 CCR 15 66265.77(a), 66265.56(j); 22 CCR 45 67450.3(c)(9)(D) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 20 21 | File Review | PBR | A written incident report for release, fire and/or explosion was submitted | 74 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to notify the Department of a release, fire, and / or explosion within 15 days and include the following: 1) Name, address, and telephone number of the owner or operator; 2) Name, address, and telephone number of the facility; 3) Date, time, and type of incident (e.g., fire, explosion); 4) Name and quantity of material(s) involved; 5) The extent of injuries, if any; 6) An assessment of actual or potential hazards to human health or the environment, where this is applicable; and 7) Estimated quantity and disposition of recovered material that resulted from the incident. |  |  | OBSERVATION: Owner/Operator did not submit a written incident report to the CUPA within 15 days of the incident. CORRECTIVE ACTION: Submit the written incident report to the CUPA. | OBSERVATION: A written incident report for a release, fire, and/or explosion has not been submitted to the CUPA. Within 15 days after the incident, the owner/operator shall submit a written report on the incident. CORRECTIVE ACTION: Immediately submit a written incident report to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210039 |  |  | Permit by Rule: Annual Report | Failure of the owner or operator of a fixed treatment unit (FTU), upon request by the CUPA or authorized agency, to prepare, and submit to CUPA a complete annual report detailing treatment activities conducted during the calendar year preceding the request. | 22 CCR 45 67450.3(c)(10) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 21 22 | File Review | PBR | PBR annual Report submitted, when requested. | 44 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator of a fixed treatment unit (FTU), upon request by the CUPA or authorized agency, to prepare, and submit to CUPA a complete annual report detailing treatment activities conducted during the calendar year preceding the request. |  |  | OBSERVATION: Owner/Operator did not submit an Annual Report. CORRECTIVE ACTION: Submit the required Annual Report to the CUPA. | OBSERVATION: An Annual Report for each fixed treatment unit (FTU) which performed treatment during the calendar year has not been submitted to the CUPA. The Owner/Operator of a FTU shall submit an Annual Report which includes all of the required information listed in this section. CORRECTIVE ACTION: Immediately submit the required Annual Report information to the CUPA. | OBSERVATION: Annual Report information was not submitted to the CERS. The Owner/Operator of a FTU shall submit an Annual Report which includes all of the required information listed in this section. CORRECTIVE ACTION: Immediately submit the required Annual Report information to the CERS. |  |  |  |  | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210014 |  |  | Treatment: New Tank P.E. Assessment | Failure to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service. The written assessment shall state that, the new hazardous waste tank system has sufficient structural integrity, is acceptable for the transferring, storing and treating of hazardous waste, and that the tanks and containment system including the foundation, structural support, seams, connections, and pressure controls (if applicable) are suitably designed to meet the regulation. The tank assessment shall be valid for 5 years. | 22 CCR 45 67450.3(c)(9)(F); 22 CCR 15 66265.192(a), 66265.192(h) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 22 23 | On Site Records | All Tiers | New tank assessment completed prior to placing system into service and was reviewed/certified by PE | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service. The written assessment shall state that, the new hazardous waste tank system has sufficient structural integrity, is acceptable for the transferring, storing and treating of hazardous waste, and that the tanks and containment system including the foundation, structural support, seams, connections, and pressure controls (if applicable) are suitably designed to meet the regulation. The tank assessment shall be valid for 5 years. |  |  | OBSERVATION: Owner/Operator failed to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service, and/or the tank assessment is not complete. CORRECTIVE ACTION: Complete written tank assessment on tank system prior to placing the tank system into service, or complete now if system is already in service. Assessment must be reviewed and certified by an independent, qualified, professional engineer. | [6 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Administration/Documentation | 3210042 |  |  | Treatment: P.E. Assessment/Reassessment of the TP Tank systems | Failure of the generator to obtain assessment or reassessment every five (5) years or the remaining service life of the tank system, as stated in the engineer's assessment, whichever is less. This assessment applies to onground or aboveground tank systems containing only non-RCRA hazardous wastes generated onsite, and tank systems authorized under Permit-by-Rule, Conditional Authorization, and Conditional Exemption or for a small quantity generator onground or aboveground tank systems containing RCRA hazardous wastes generated onsite. | 22 CCR 67450.3(c)(9)(F); 22 CCR 15 66265.192(h) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 23 24 | On Site Records | All Tiers | P.E. assessment and/or reassessment of the hazardous waste tank system completed | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the generator to obtain assessment or reassessment every five (5) years or the remaining service life of the tank system, as stated in the engineer's assessment, whichever is less. This assessment applies to onground or aboveground tank systems containing only non-RCRA hazardous wastes generated onsite, and tank systems authorized under Permit-by-Rule, Conditional Authorization, and Conditional Exemption or for a small quantity generator onground or aboveground tank systems containing RCRA hazardous wastes generated onsite. |  |  | OBSERVATION: Owner/Operator failed to obtain assessment or reassessment every five (5) years or the remaining service life of the hazardous waste treatment tank system, as stated in the engineer's assessment, whichever is less. CORRECTIVE ACTION: Obtain assessment or reassessment of the hazardous waste treatment tank system pursuant to 22 CCR 66265.192, completed by a professional engineer. | [6 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Administration/Documentation | 3210012 |  |  | Treatment: New Tank Assessment Standards | Failure to include all required information in the new tank system assessment. | 22 CCR 45 67450.3(c)(9)(F); 22 CCR 15 66265.192(k) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 24 25 | On Site Records | All Tiers | HW treatment tank assessment completed and includes all required information. | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to include all required information in the new tank system assessment. |  |  | OBSERVATION: The hazardous waste tank system assessment was not complete and/or kept on file at the facility. CORRECTIVE ACTION: Immediately revise the hazardous waste tank system assessment to include all of the required information as listed in CCR 66265.192(k) and keep on file at the facility and submit a copy to the CUPA. | OBSERVATION: The Owner/Operator failed to prepare a complete hazardous waste tank system assessment that includes all of the required information listed in this section. The hazardous waste tank system assessment shall also be kept on file at the facility. CORRECTIVE ACTION: Immediately prepare/revise the hazardous waste tank system to include all of the required information according to this section. Provide a copy of the revised HW tank system assessment to the CUPA and maintain a copy on file at the facility. | OBSERVATION: The Owner/Operator failed to prepare a complete hazardous waste tank system assessment that includes all of the required information listed in this section. The hazardous waste tank system assessment shall also be kept on file at the facility. CORRECTIVE ACTION: Immediately prepare/revise the hazardous waste tank system assessment to include all of the required information according to this section. Submit a copy of the revised hazardous waste tank system assessment to CERS and maintain a copy on file at the facility. |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Administration/Documentation | 3210013 |  |  | Treatment: Annual P.E. assessment of Hazardous Waste Tank Systems without Secondary Containment | Failure of the generator conducting CE, CA, or PBR treatment activity to annually obtain and maintain a current P.E. assessment of the existing Hazardous Waste tank systems which lack secondary containment meeting the requirements of section 66265.193. The P.E. assessment shall determine that the tank system is adequately designed and has sufficient structural strength and compatibility with the waste(s) to be transferred, stored or treated to ensure that it will not collapse, rupture, or fail. At a minimum, this assessment shall include all elements of the tank integrity assessment. | 22 CCR 15 66265.191(a), 66265.191(b), 66265.191(c), 66265.191(e) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 25 26 | On Site Records | All Tiers | Existing HW tank system without secondary containment has been assessed and certified annually | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the generator conducting CE, CA, or PBR treatment activity to annually obtain and maintain a current P.E. assessment of the existing Hazardous Waste tank systems which lacks secondary containment meeting the requirements of section 66265.193. The P.E. assessment shall determine that the tank system is adequately designed and has sufficient structural strength and compatibility with the waste(s) to be transferred, stored or treated to ensure that it will not collapse, rupture, or fail. At a minimum, this assessment shall include all elements of the tank integrity assessment. |  |  | OBSERVATION: A hazardous waste tank system assessment was not kept on file at the facility. The hazardous waste tank system assessment was not reviewed and certified by an independent, qualified, professional engineer, registered in California annually. CORRECTIVE ACTION: Provide a copy of the certified hazardous waste tank system assessment to the CUPA and maintain a copy at the facility. Submit a copy of the certified waste tank assessment to the CUPA. | OBSERVATION: The Owner/Operator failed to obtain a certified hazardous waste tank system assessment. The Owner/Operator shall obtain and keep on file at the facility a written assessment reviewed and certified by an independent, qualified, professional engineer, registered in California annually. CORRECTIVE ACTION: Immediately obtain a certified hazardous waste tank assessment that includes all of the required information in this section. Provide a copy of the certified hazardous waste tank system assessment to the CUPA and maintain a copy at the facility. | OBSERVATION: The Owner/Operator failed to obtain a certified hazardous waste tank system assessment. The Owner/Operator shall obtain and keep on file at the facility a written assessment reviewed and certified by an independent, qualified, professional engineer, registered in California annually. CORRECTIVE ACTION: Immediately obtain a certified hazardous waste tank assessment that includes all of the required information in this section. Submit a copy of the certified hazardous waste tank system assessment to CERS and maintain a copy at the facility. |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Administration/Documentation | 3210015 |  |  | Treatment: Existing Tank P.E. Assessment | Failure to include all required information in the tank system assessment. | 22 CCR 15 66265.191(g); 22 CCR 45 67450.3(c)(9)(F) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 26 27 | On Site Records | All Tiers | Existing HW tank system assessment is complete | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to include all required information in the tank system assessment. |  |  | OBSERVATION: An existing hazardous waste tank assessment did not include all of the required information according to this section. CORRECTIVE ACTION: Immediately revise the hazardous waste tank system assessment to include all of the required information as listed in this section. Submit a copy of the complete hazardous waste tank assessment to the CUPA. | OBSERVATION: The Owner/Operator failed to prepare a complete hazardous waste tank system assessment. The hazardous waste tank system assessment shall include all of the information listed in this section. CORRECTIVE ACTION: Immediately prepare/revise the hazardous waste tank system to include all of the required information according to this section. Provide a copy of the revised hazardous waste tank system assessment to the CUPA. | OBSERVATION: The Owner/Operator failed to prepare a complete hazardous waste tank system assessment. The hazardous waste tank assessment shall include all of the information listed in this section. CORRECTIVE ACTION: Immediately prepare/revise the hazardous waste tank system assessment to include all of the required information according to this section. Submit a copy of the revised hazardous waste tank system assessment to CERS. |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Administration/Documentation | 3210016 |  |  | Treatment: Hazardous Waste Tank System Replacement | Failure to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components. | 22 CCR 15 66265.192(m); 22 CCR 45 67450.3(c)(9)(F) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 27 28 | On Site Records | All Tiers | Obtained approval before replacement of identical/equivalent tank system parts not in 66265.192(l) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components. |  |  | OBSERVATION: Owner/Operator failed to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). CORRECTIVE ACTION: Provide CUPA with documentation on the tank system parts or components that have been replaced. CUPA will then determine if a new written hazardous waste tank system assessment for the tank system is required. | OBSERVATION: The Owner/Operator failed to submit the required information in writing to the CUPA for making a determination for approval prior to the replacement of parts/components for the HW tank system. CORRECTIVE ACTIONS: Immediately submit the required information in writing according to this section for approval by the CUPA. | [5 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Administration/Documentation | 3210038 |  |  | Conditionally Exempt: Operating Instructions and Waste Treatment Record Retention | Failure of the generator to prepare and maintain onsite, for a period of three years, the following: (1) adequate records to demonstrate compliance with all applicable pretreatment standards and discharge requirements issued by the agency operating the POTW; (2) records of the dates, concentrations, amounts, and types of waste treated; and (3) written operating instructions. | HSC 6.5 25201.5(d)(3), 25201.5(d)(5), 25201.5(d)(6) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 28 29 | On Site Records | CE | Records for conducting CE HW treatment are maintained onsite for three years | 76 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the generator to prepare and maintain onsite, for a period of three years, the following: (1) adequate records to demonstrate compliance with all applicable pretreatment standards and discharge requirements issued by the agency operating the POTW; (2) records of the dates, concentrations, amounts, and types of waste treated; and (3) written operating instructions. |  |  | OBSERVATION: Records for conducting hazardous waste treatment were not maintained onsite for three years. CORRECTIVE ACTION: Begin maintaining records for hazardous waste treatment and ensure that they are kept onsite for three years. Submit copies of these records to the CUPA. | OSERVATION: The Owner/Operator failed to maintain records for hazardous waste treatment for three years. The generator shall prepare and maintain written operating instructions, a record of the dates, amounts, types of hazardous waste treated, a written inspection schedule and a log of inspections conducted onsite for a period of three years. The generator shall also maintain adequate records to demonstrate compliance with all applicable pretreatment standards and industrial waste discharge requirements issued by the POTW. CORRECTIVE ACTIONS: Ensure that written operating instructions, records of the dates, amounts, types of hazardous waste treated, a written inspection schedule and a log of inspections conducted are maintained onsite for a period of three years. Records must be maintained to adequately demonstrate compliance with all applicable pretreatment standards and industrial waste discharge requirements issued by the POTW. Submit supporting documentation that verifies compliance with these requirements to the CUPA. | [5 empty] | Yes | No | Yes | Yes | Yes | Yes | No
Tiered Permitting | Operations/Maintenance | 3230031 |  |  | Conditionally Exempt: Hazardous Waste Treatment System Inspection and Log | Failure to prepare, implement, and maintain onsite, for three years at the facility, a treatment system inspection program and log of inspections conducted. | HSC 6.5 25201.5(d)(4), 25201.5(d)(5) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 29 30 | On Site Records | CE | Records for scheduling and logging inspections are maintained onsite for three years(CE) | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare, implement, and maintain onsite, for three years at the facility, a treatment system inspection program and log of inspections conducted. |  |  | OBSERVATION: Records for scheduling and logging inspections for the hazardous waste treatment system were not maintained onsite for three years. CORRECTIVE ACTION: Begin maintaining records for scheduling and logging inspections for the hazardous waste treatment system and ensure that they are kept onsite for three years. Submit copies of these records and inspections to the CUPA. | OBSERVATION: The Owner/Operator failed to maintain records for inspecting the hazardous waste treatment system for three years. The generator shall prepare and maintain a written inspection schedule and log of the inspections conducted for the hazardous waste treatment system onsite for three years. CORRECTIVE ACTIONS: Ensure that a written inspection schedule is prepared and a log of the inspections conducted are maintained onsite for three years for the hazardous waste treatment system. Submit supporting documentation that verifies compliance with these requirements to the CUPA. | [5 empty] | Yes | No | Yes | Yes | Yes | Yes | No
Tiered Permitting | Administration/Documentation | 3210037 |  |  | Conditional Authorization: Operating Instructions and Waste Treatment Record Retention | Failure of the generator to prepare and maintain onsite, for a period of five years, adequate records to demonstrate that requirements and conditions of the grant of conditional authorization are met. | HSC 6.5 25200.3(c)(6), 25200.3(c)(7) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 30 31 | On Site Records | CA | Records for conducting CA HW treatment are maintained onsite for five years | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the generator to prepare and maintain onsite, for a period of five years, adequate records to demonstrate that requirements and conditions of the grant of conditional authorization are met. |  |  | OBSERVATION: Records for conducting hazardous waste treatment were not maintained onsite for five years. CORRECTIVE ACTION: Begin maintaining records for hazardous waste treatment and ensure that they are kept onsite for five years. Submit copies of these records to the CUPA. | OSERVATION: The Owner/Operator failed to maintain records for hazardous waste treatment for five years. The generator shall prepare and maintain written operating instructions. The operating instructions shall include, but are not limited to, how to operate the treatment unit and carry out hazardous waste treatment, how to recognize potential and actual process upsets and respond to them, when to implement the contingency plan, how to determine if the treatment has been efficacious, and how to address the residuals of waste treatment. A record of the dates, concentrations, amounts, and types of waste treated and records to demonstrate compliance with all applicable pretreatment standards and industrial waste discharge requirements issued by the POTW shall be maintained onsite for a period of five years. CORRECTIVE ACTIONS: Ensure that written operating instructions have the required content, records of the dates, concentrations, amounts, types of hazardous waste treated and records to adequately demonstrate compliance with all applicable pretreatment standards and industrial waste discharge requirements issued by the POTW are maintained onsite for five years. Submit supporting documentation that verifies compliance with these requirements to the CUPA. | [5 empty] | Yes | Yes | No | No | No | No | No
Tiered Permitting | Operations/Maintenance | 3230011 |  |  | Conditional Authorization: Hazardous Waste Treatment System Inspection and Log | Failure to prepare and maintain onsite for five years, a treatment system inspection program and the log of inspections conducted. | HSC 6.5 25200.3(c)(5), 25200.3(c)(7) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 31 32 | On Site Records | CA | Records for scheduling and logging inspections are maintained onsite for five years(CA) | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare and maintain onsite for five years, a treatment system inspection program and the log of inspections conducted. |  |  | OBSERVATION: Records for scheduling and logging inspections for the hazardous waste treatment system were not maintained onsite for five years. CORRECTIVE ACTION: Begin maintaining records for scheduling and logging inspections for the hazardous waste treatment system and ensure that they are kept onsite for five years. Submit copies of these records to the CUPA. | OBSERVATION: The Owner/Operator failed to maintain records for inspecting the hazardous waste treatment system for five years. The generator shall prepare and maintain a written inspection schedule and log of the inspections conducted for the hazardous waste treatment system onsite for five years. CORRECTIVE ACTIONS: Ensure that a written inspection schedule is prepared and a log of the inspections conducted are maintained onsite for five years for the hazardous waste treatment system. Submit supporting documentation that verifies compliance with these requirements to the CUPA. | [5 empty] | Yes | Yes | No | No | No | No | No
Tiered Permitting | Operations/Maintenance | 3230085 |  |  | Permit-by-Rule: Hazardous Waste Treatment System Inspection and Log | Failure to prepare a treatment system inspection program and the log of inspections conducted, and maintain onsite for three years. | 22 CCR 45 67450.3(c)(8)(B); 67450.3(c)(9)(A) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 32 33 | On Site Records | PBR | Treatment system inspection program prepared and log of inspections maintained | 78 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prepare a treatment system inspection program and the log of inspections conducted, and maintain onsite for three years. |  |  | OBSERVATION: Generator failed to provide a treatment system inspection program and a log of inspections conducted for the past three years. CORRECTIVE ACTIONS: Complete and provide to CUPA a treatment system inspection program and a log of inspections conducted for the past three years. | [6 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210010 |  |  | Permit by Rule: Documentation | Failure to maintain the required documents, including waste analysis plan, contingency plan, training documents, Phase I Environmental Assessment, written inspections schedules, etc. at the facility where the FTU is operating and upon request make these documents available to the authorized agency, DTSC, the CUPA, or EPA, or local government agency. | 22 CCR 45 67450.3(c)(8) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 33 34 | On Site Records | PBR | Documents for operating a FTU are maintained onsite | 51 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain the required documents, including waste analysis plan, contingency plan, training documents, Phase I Environmental Assessment, written inspections schedules, etc. at the facility where the FTU is operating and upon request make these documents available to the authorized agency, DTSC, the CUPA, or EPA, or local government agency. |  |  | OBSERVATION: Documents for operating a FTU were not maintained onsite, including, but not limited to, waste analysis plan, contingency plan, training documents, Phase I Environmental Assessment, written inspections schedules, etc. CORRECTIVE ACTION: Submit copies of the documents for operating a FTU to the CUPA and maintain onsite. | OBSERVATION: The Owner/Operator failed to maintain the required documents for operating a FTU at the facility where the FTU is operating. Documents that shall be kept at the facility include: a written waste analysis plan, a written inspection schedule, training documents, a contingency plan, a copy of the most recent notification and a copy of the most recent acknowledgement received from the CUPA, a copy of any local Air District permit and other permits required for the operation of the FTU, A copy of the closure plan, a copy of documents related to the environmental investigation of any cleanup, abatement or other necessary remedial action taken, and documentation of any convictions, judgments, settlements, or orders resulting from any action by any local, State, or federal environmental or public health enforcement agency concerning the operation of the facility within the last three years. CORRECTIVE ACTIONS: Immediately prepare and maintain the required documents listed in this section at the facility where the FTU is operating. Submit any/all of the required documents to the CUPA for review. | OBSERVATION: The Owner/Operator failed to maintain the required documents for operating a FTU at the facility where the FTU is operating. Documents that shall be kept at the facility include: a written waste analysis plan, a written inspection schedule, training documents, a contingency plan, a copy of the most recent notification and a copy of the most recent acknowledgement received from the CUPA, a copy of any local Air District permit and other permits required for the operation of the FTU, A copy of the closure plan, a copy of documents related to the environmental investigation of any cleanup, abatement or other necessary remedial action taken, and documentation of any convictions, judgments, settlements, or orders resulting from any action by any local, State, or federal environmental or public health enforcement agency concerning the operation of the facility within the last three years. CORRECTIVE ACTIONS: Immediately prepare and maintain the required documents listed in this section at the facility where the FTU is operating. Submit the treatment notification, local agency notification, and prior enforcement history documents to the CERS for review. |  |  |  |  | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210011 |  |  | Permit by Rule: Cyanide Treatment Records Retention | Failure to maintain the required documents at the facility for a minimum of three years from the last date of any activity and made available to authorized representatives of the Department, the CUPA, or the U.S. EPA. | 22 CCR 45 67450.11(d)(7)(E) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 34 35 | On Site Records | PBR | Records for cyanide treatment were maintained at the facility for three years | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain the required documents at the facility for a minimum of three years from the last date of any activity and made available to authorized representatives of the Department, the CUPA, or the U.S. EPA. |  |  | OBSERVATION: Records for cyanide treatment were not maintained a the facility for three years. CORRECTIVE ACTIONS: Begin maintaining records for the cyanide treatment system and ensure that they are kept at the facility for three years. Submit copies of these records to the CUPA. | OBSERVATION: The Owner/Operator failed to maintain cyanide treatment records at the facility for three years. Owners or Operators shall ensure that the following records are maintained at the facility for a minimum of three years from the last date of any activity: written approval from the agency operating the POTW receiving the facility's discharges, a written method documented in the waste analysis plan for ensuring that the concentration of total cyanide does not exceed 5000 milligrams per liter in the aqueous waste resulting from mixing, and documentation that the residual solids generated by treatment have been sent offsite for metals recovery or reclamation, or determined to be not amendable for recycling. CORRECTIVE ACTIONS: Ensure that the cyanide treatment records, as listed in this section, are maintained at the facility for a minimum of three years. Submit copies of supporting documentation that demonstrates compliance with this requirement to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230080 |  |  | Conditionally Exempt: Hazardous Waste Treatment Process Combinations | Failure of the generator treating hazardous wastes to comply with the requirements of the conditional exemption applicable to the treatment process. | 22 CCR 45 67450.11(a); HSC 6.5 25201.5(a), 25201.5(c) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 35 36 | General Operating Requirements | CE | Meeting Conditionally Exempt hazardous waste treatment requirements | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the generator treating hazardous wastes to comply with the requirements of the conditional exemption applicable to the treatment process. |  |  | OBSERVATION: The owner/operator has failed to meet all of the operating requirements for the Conditionally Exempt hazardous waste treatment activities on site. CORRECTIVE ACTION: Submit photo and written documentation which demonstrates that the facility has complied with all Conditionally Exempt treatment requirements. | [6 empty] | Yes | No | Yes | Yes | Yes | Yes | No
Tiered Permitting | Administration/Documentation | 3210049 |  |  | Conditionally Exempt Authorization Treatment: Waste Generated onsite | Failure to treat only hazardous waste that is generated onsite. | HSC 6.5 25201.5(d)(1), 25189 | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 36 37 | General Operating Requirements | CE | Only treating hazardous waste generated onsite | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to treat only hazardous waste that is generated onsite. |  |  | OBSERVATION: Owner/Operator treated hazardous waste that was not generated onsite. CORRECTIVE ACTION: Discontinue practice of treating hazardous waste that was not generated onsite. | [6 empty] | Yes | No | Yes | Yes | Yes | Yes | No
Tiered Permitting Program | Administration/Documentation | 3210051 |  |  | Conditional Exempt : Discharge and Treatment Residual Records | Failure of the generator to maintain adequate records to demonstrate that they are in compliance with all applicable pretreatment standards and waste discharge requirements and treatment residuals managed and disposed in accordance with applicable federal, state, and local requirements. | HSC 6.5 25201.5(d)(6) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 37 38 | General Operating Requirements | CE | Adequate records kept demonstrating effluent or treatment residuals are discharged compliantly | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the generator to maintain adequate records to demonstrate that they are in compliance with all applicable pretreatment standards and waste discharge requirements and treatment residuals managed and disposed in accordance with applicable federal, state, and local requirements. |  |  | OBSERVATION: Owner/Operator failed to maintain adequate records to demonstrate that they are in compliance with all applicable pretreatment standards and waste discharge requirements and treatment residuals managed and disposed in accordance with applicable federal, state, and local requirements. CORRRECTIVE ACTION: Maintain adequate records to demonstrate compliance with applicable pretreatment standards and waste discharge requirements and that treatment residuals have been managed and disposed in accordance with all applicable requirements. | [6 empty] | Yes | No | Yes | Yes | Yes | Yes | No
Tiered Permitting | Operations/Maintenance | 3230084 |  |  | Conditionally Exempt Small Quantity Treatment (CESQT): Monthly volume | Failure to comply with total monthly treatment limitation of 55 gallon or 500 lbs when the hazardous waste is not extremely hazardous waste and hazardous waste permit is not required for any other activity at that facility. | HSC 6.5 25201.5(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 38 39 | General Operating Requirements | CE | Facility has not treated more than 55 gal/500 lbs of hazardous waste in a month | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with total monthly treatment limitation of 55 gallon or 500 lbs when the hazardous waste is not extremely hazardous waste and hazardous waste permit is not required for any other activity at that facility. |  |  | OBSERVATION: Owner/Operator treated hazardous waste in excess of the 55 gal/500 lb limit allowed in a month. CORRECTIVE ACTION: Discontinue treating hazardous waste in excess of allowed monthly volume limit. | [6 empty] | Yes | No | Yes | Yes | Yes | Yes | No
Tiered Permitting | Operations/Maintenance | 3230018 |  |  | Conditionally Exempt: Laundry Facility | Failure of a facility laundering reusable soiled textile materials to meet the requirements of the conditional exemption applicable to the process. | HSC 6.5 25144.6(c) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 39 40 | General Operating Requirements | CE | Requirements for laundering reusable soiled textile materials are being met | 75 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of a facility laundering reusable soiled textile materials to meet the requirements of the conditional exemption applicable to the process. |  |  | OBSERVATION: The laundry facility did not meet the requirements of the conditional exemption applicable to the process. CORRECTIVE ACTION: Maintain compliance with the requirements of the conditional exemption applicable to a commercial laundry found in H&SC 25144.6. | OBSERVATION: The Owner/Operator of this laundry facility failed to meet one or more of the following requirements for laundering reusable soiled textile materials which have become soiled with hazardous waste during commercial or industrial use: The materials are not otherwise regulated by the EPA; the materials are not used to clean up or control a spill that is required to be reported to any state or federal agency; no hazardous waste has been added after the materials' original use; no free liquids are released during transportation or storage; records maintained of the date, type, and quantities of the materials collected and laundered; a contingency plan is prepared and employees are trained in the execution of the plan; management procedures are in place to ensure materials are properly managed; the waste washwater conveyances and containers are impervious, and are visually inspected at least twice a year; the sludge from washing process is managed properly; training program in place that ensures facility personnel safely and properly handle wastes; written operating instructions prepared; written inspection schedule prepared and log of inspections maintained; records maintained to demonstrate compliance with all pretreatment standards and industrial waste discharge requirements of POTW; all closure requirements have been met; written notification of closure provided in person or by certified mail to the CUPA, the waste is managed in accordance with all applicable generator requirements for hazardous waste; permit fees have been paid; notice provided to CUPA not less than 60 days before commencing treatment of hazardous waste. CORRECTIVE ACTIONS: Ensure that compliance is maintained with all of the requirements listed. Provide supporting documentation that demonstrates compliance with these requirements to the CUPA. | [5 empty] | Yes | No | Yes | Yes | Yes | Yes | No | 1857
Tiered Permitting | Administration/Documentation | 3210050 |  |  | Conditionally Exempt: Closure Documentation | Failure of the generator to remove or decontaminate all waste residues, containment system components, soils, and other structures or equipment contaminated with hazardous waste, and provide written notification of all closure activities at the closure of the treatment unit. | HSC 6.5 25201.5(d)(8) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 40 41 | General Operating Requirements | CE | All contaminated system components and soils removed or decontaminated and notification provided | 96 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the generator to remove or decontaminate all waste residues, containment system components, soils, and other structures or equipment contaminated with hazardous waste, and provide written notification of all closure activities at the closure of the treatment unit. |  |  | OBSERVATION: Owner/Operator failed to remove or decontaminate all waste residues, containment system components, soils, and other structures or equipment contaminated with hazardous waste, and provide written notification of all closure activities at the closure of the treatment unit. CORRECTIVE ACTION: Remove or decontaminate all waste residues, containment system components, soils, and other structures or equipment contaminated with hazardous waste, and provide written notification of all closure activities at the closure of the treatment unit. | [6 empty] | Yes | No | Yes | Yes | Yes | Yes | No
Tiered Permitting | Operations/Maintenance | 3230079 |  |  | Conditional Authorized: Hazardous Waste Treatment Process Combinations | Failure of the generator treating hazardous wastes under grant of conditional authorization to comply with the requirements applicable to the treatment process. | HSC 6.5 25200.3(a), 25200.3(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 41 42 | General Operating Requirements | CA | Meeting Conditionally Authorized hazardous waste treatment requirements | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the generator treating hazardous wastes under grant of conditional authorization to comply with the requirements applicable to the treatment process. |  |  | OBSERVATION: The owner/operator has failed to meet all of the operating requirements for the Conditionally Authorized hazardous waste treatment activities on site. CORRECTIVE ACTION: Submit photo and written documentation showing that the facility has complied with all Conditionally Authorized treatment requirements. | [6 empty] | yes | Yes | No | No | No | No | No
Tiered Permitting | Administration/Documentation | 3210048 |  |  | Conditional Authorization Treatment: Waste Generated onsite | Failure to treat only hazardous waste that is generated onsite. | HSC 6.5 25200.3(c)(8), 25189 | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 42 43 | General Operating Requirements | CA | Only treating hazardous waste generated onsite | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to treat only hazardous waste that is generated onsite. |  |  | OBSERVATION: Owner/Operator treated hazardous waste that was not generated onsite. CORRECTIVE ACTION: Discontinue practice of treating hazardous waste that was not generated onsite. | [6 empty] | Yes | Yes | No | No | No | No | No
Tiered Permitting | Operations/Maintenance | 3230083 |  |  | Conditional Authorization Treatment: Monthly volume | Treated hazardous waste in excess of 5,000 gallons/unit or 45,000 pounds in any calendar month, whichever is less, unless the wastes are: • Dilute aqueous waste which are hazardous solely due to the presence of inorganic constituents; • Dilute aqueous waste which are hazardous solely due to the presence of organic constituents; • Neutralization of acidic or alkaline wastes that are hazardous only due to corrosivity or toxicity that results only from the acidic or alkaline material, in elementary neutralization units, if the wastes contain less than 10 percent acid or base constituents by weight; If the waste contains more than 10 percent acid or base constituents by weight, the volume treated in a single batch at any one time shall not exceed 500 gallons. • Treatment of oil mixed with water and oil/water separation sludges, using any of the approved treatment technologies. | HSC 6.5 25200.3(b)(1) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 43 44 | General Operating Requirements | CA | Allowed monthly treatment volume has not been exceeded | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Treated hazardous waste in excess of 5,000 gallons/unit or 45,000 pounds in any calendar month, whichever is less, unless the wastes are: • Dilute aqueous waste which are hazardous solely due to the presence of inorganic constituents; • Dilute aqueous waste which are hazardous solely due to the presence of organic constituents; • Neutralization of acidic or alkaline wastes that are hazardous only due to corrosivity or toxicity that results only from the acidic or alkaline material, in elementary neutralization units, if the wastes contain less than 10 percent acid or base constituents by weight; If the waste contains more than 10 percent acid or base constituents by weight, the volume treated in a single batch at any one time shall not exceed 500 gallons. • Treatment of oil mixed with water and oil/water separation sludges, using any of the following treatment technologies listed. |  |  | OBSERVATION: Owner/Operator treated hazardous waste in excess of the allowed monthly treatment limit. CORRECTIVE ACTION: Discontinue treating hazardous waste in excess of allowed monthly volume limit. | [6 empty] | Yes | Yes | No | No | No | No | No
Tiered Permitting Program | Administration/Documentation | 3210052 |  |  | Conditional Authorization: Discharge and Treatment Residual records | Failure to maintain adequate records to demonstrate compliance with all applicable pretreatment standards and with all applicable industrial waste discharge requirements issued by the agency operating the publicly owned treatment works into which the wastes are discharged. | HSC 6.5 25200.3(c)(7) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 44 45 | General Operating Requirements | CA | Adequate records kept demonstrating effluent or treatment residuals are discharged compliantly | 94 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain adequate records to demonstrate compliance with all applicable pretreatment standards and with all applicable industrial waste discharge requirements issued by the agency operating the publicly owned treatment works into which the wastes are discharged. |  |  | OBSERVATION: Owner/Operator failed to maintain adequate records to demonstrate that they are in compliance with all applicable pretreatment standards and waste discharge requirements. CORRRECTIVE ACTION: Maintain adequate records to demonstrate compliance with applicable pretreatment standards and waste discharge requirements. | [6 empty] | Yes | Yes | No | No | No | No | No
Tiered Permitting | Operations/Maintenance | 3230082 |  |  | CA Treatment: Secondary Containment for Treatment in Containers | Failure to provide secondary containment for treatment in containers. | HSC 6.5 25200.3(c)(4), 66264.175(a); 66264.175(b) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 45 46 | General Operating Requirements | CA | Provided secondary containment for treatment in containers. | 59 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide secondary containment for treatment in containers. |  |  | OBSERVATION: The facility owner/operator has failed to meet the secondary containment requirements for Conditionally Authorized treatment of hazardous waste in containers. CORRECTIVE ACTION: Submit photo and written documentation to the CUPA that demonstrates the facility owner/operator has met the Conditionally Authorized container treatment secondary containment requirements. | [6 empty] | Yes | Yes | No | No | No | No | No
Tiered Permitting | Abandonment/Illegal Disposal/Unauthorized Treatment | 3250001 |  |  | Conditional Authorization: Closure and Documentation | Failure of the generator to remove or decontaminate all containment system components and structures or equipment contaminated with hazardous waste and soils and provide written notification of all closure activities at the closure of the treatment unit. | HSC 6.5 25200.3(g) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 46 47 | General Operating Requirements | CA | The HW treatment unit was closed properly and the CUPA was notified | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure of the generator to remove or decontaminate all containment system components and structures or equipment contaminated with hazardous waste and soils and provide written notification of all closure activities at the closure of the treatment unit. |  |  | OBSERVATION: The HW treatment unit was not closed properly and/or the CUPA was not notified that the HW treatment unit is closed. CORRECTIVE ACTION: Ensure that compliance with the requirements have been met to properly close the HW treatment unit and/or notify the CUPA that the HW treatment unit has been closed. | OBSERVATION: The generator failed to properly close the HW treatment unit and/or notify the CUPA when the HW treatment unit had ceased operation. The generator shall upon terminating operation of any treatment process or unit conditionally authorized pursuant to this section, the generator conducting treatment pursuant to this section, shall remove or decontaminate all waste residues, containment system components, soils and structures or equipment contaminated with HW from the unit. The removal of the unit from service shall be conducted in a manner that does both of the following: minimizes the need for further maintenance, eliminates the escape of HW, HW constituents, leachate, contaminated runoff, or waste decomposition products to the environment after the treatment process is no longer in operation. Any generator conducting treatment pursuant to this section who permanently ceases operation of a treatment process or unit that is conditionally authorized pursuant to this section shall, upon completion of all activities required under this subdivision, provide written notification, in person or by certified mail, with return receipt requested to the department and to one of the following: The CUPA, if the generator is under the jurisdiction of a CUPA, if the generator is not under the jurisdiction of a CUPA, the notification shall be submitted to the officer or agency authorized, pursuant to subdivision (f) or section 25404.3, to implement and enforce the requirements of this chapter listed in paragraph (1) of subdivision (c) of section 25404. CORRECTIVE ACTIONS: Immediately ensure that the HW treatment unit is closed properly according to the listed requirements and/or Immediately notify the CUPA upon the completion of all activities as listed. Provide supporting documentation that demonstrates compliance with these requirements to the CUPA. | [5 empty] | Yes | Yes | No | No | No | No | No
Tiered Permitting | Administration/Documentation | 3210047 |  |  | Permit-by-Rule Treatment: Waste Generated onsite | Failure to treat only hazardous waste that is generated onsite. | 22 CCR 45 67450.3(c)(6); HSC 6.5 25189 | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 47 48 | General Operating Requirements | PBR | Only treating hazardous waste generated onsite | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to treat only hazardous waste that is generated onsite. |  |  | OBSERVATION: Owner/Operator treated hazardous waste that was not generated onsite. CORRECTIVE ACTION: Discontinue practice of treating hazardous waste that was not generated onsite. | [6 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230074 |  |  | Permit-by-Rule Treatment: Secondary Containment | Failure to meet required secondary containment requirements for hazardous waste tank systems or components. | 22 CCR 45 67450.3(c)(9)(F); 22 CCR 15 66265.193 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 48 49 | General Operating Requirements | PBR | HW tank systems secondary containment meets requirements | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet required secondary containment requirements for hazardous waste tank systems or components. |  |  | OBSERVATION: The HW tank secondary containment system does not meet requirements. CORRECTIVE ACTION: A secondary containment system for the HW tank is required to be installed and/or the secondary containment system is not designed to meet the requirements of this section. Submit documentation to the CUPA of the secondary containment system you are going to use for approval. | OBSERVATION: The Owner/Operator failed to meet the requirements for designing, installing and operating a secondary containment system for the HW tank system. An Owner/Operator shall design, install and operate a secondary containment system to prevent any migration of wastes or accumulated liquid out of the system to the soil, ground water, or surface water at any time during the use of the HW tank system. CORRECTIVE ACTION: A plan for designing, installing and/or modifying to meet the requirements and operating a HW tank secondary containment system must be submitted to the CUPA for review. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230081 |  |  | PBR Treatment: Secondary Containment for Treatment in Containers | Failure to provide secondary containment for treatment in containers and/or to obtain P.E. certification that containment is suitably designed to achieve the requirements. | 22 CCR 45, 67450.3(c)(12); 66264.175 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 49 50 | General Operating Requirements | PBR | Provided secondary containment for treatment in containers. | 59 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide secondary containment for treatment in containers and/or to obtain P.E. certification that containment is suitably designed to achieve the requirements. |  |  | OBSERVATION: The facility owner/operator has failed to meet the secondary containment requirements for Permit by Rule treatment of hazardous waste in containers and/or to obtain P.E. certification that containment is suitably designed to achieve the requirements. CORRECTIVE ACTION: Submit photo and written documentation to the CUPA that shows the facility owner/operator has met the Permit by Rule container treatment secondary containment requirements, and a P.E. certification that containment is suitably designed to achieve the requirements. | [6 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230087 |  |  | Permit-by-Rule: Written Waste Analysis Plan and Documentation | Failure of an owner or operator to obtain a detailed chemical and physical analysis of a representative sample of the waste, which includes all information necessary to manage waste in accordance with the requirements, and to meet LDR requirements; Failure to analyze wastes according to the frequency specified in the plan and to retain waste analysis documentation for three years. | 22 CCR 15 66265.13(a), 66265.13(b); 22 CCR 45 67450.3(c)(8)(A), 67450.3(c)(9)(A) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 50 51 | General Operating Requirements | PBR | Written waste analysis plan complied with and records maintained for 3 years | 76 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of an owner or operator to obtain a detailed chemical and physical analysis of a representative sample of the waste, which includes all information necessary to manage waste in accordance with the requirements, and to meet LDR requirements; Failure to analyze wastes according to the frequency specified in the plan and to retain waste analysis documentation for three years. |  |  | OBSERVATION: Owner/Operator failed to complete a waste analysis plan or has an incomplete waste analysis plan, or failed to implement the waste analysis plan and properly maintain records to document implementation of the waste analysis plan. CORRECTIVE ACTION: Complete or revise waste analysis plan to comply with the requirements of CCR 66265.13, and/or implement waste analysis plan and properly maintain records to document that you are implementing the waste analysis plan. Submit copy of plan and records demonstrating implementation. | [6 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230047 |  |  | Permit by Rule: Discharge and Treatment Residuals | Failure of the owner or operator discharging any effluent or treatment residuals to meet the applicable discharge requirements. | 22 CCR 45 67450.3(c)(5) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 51 52 | General Operating Requirements | PBR | Effluent or treatment residuals are discharged compliantly | 58 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator discharging any effluent or treatment residuals to meet the applicable discharge requirements. |  |  | OBSERVATION: The requirements for discharging effluent or treatment residuals has not been met. CORRECTIVE ACTION: Ensure that compliance with the requirements have been met to discharge the effluent or treatment residuals. | OBSERVATION: The owner or operator of the treatment unit failed to meet the requirements for discharging effluent or treatment residuals. The owner or operator of a treatment unit deemed to hold a permit by rule shall discharge any effluent or treatment residual as follows: to a publicly-owned treatment works (POTW) in accordance with all applicable industrial waste discharge requirements issued by the agency operating the POTW. HW shall not be discharged to a POTW unless the POTW is authorized to receive the HW and the discharge of the HW is specifically approved in writing by the agency operating the POTW. The treatment unit owner or operator shall inform the agency operating the POTW of the time, volume, content characteristics and point of the discharge or in accordance with waste discharge requirements issued by a Regional Water Quality Control Board or a National Pollutant Discharge Elimination System (NPDES) permit or to a treatment, storage, or disposal facility authorized to receive the waste or in accordance with any other applicable state law allowing alternative disposition of the effluent or treatment residual. CORRECTIVE ACTIONS: Ensure that the HW treatment unit meets all of the requirements listed. Provide supporting documentation that demonstrates compliance with the requirements to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230086 |  |  | Permit-by-Rule: Closure Plan and Closure Notification | Failure to prepare a written closure plan, to notify CUPA 15 days prior to the completion of closure, or to submit to CUPA a closure certification signed by the owner or operator and an independent P.E.. | 22 CCR 45 67450.3(c)(11)(D), 67450.3(c)(11)(F), 67450.3(c)(11)(G), 67450.3(c)(8)(G) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 52 53 | General Operating Requirements | PBR | Closure plan completed, CUPA notified within 15 days of closure and submitted owner/PE certification | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a written closure plan, to notify CUPA 15 days prior to the completion of closure, or to submit to CUPA a closure certification signed by the owner or operator and an independent P.E.. |  |  | OBSERVATION: Owner/operator failed to prepare, or submit to CUPA when requested, a written closure plan, to notify CUPA 15 days prior to the completion of closure, or to submit to CUPA a closure certification signed by the owner or operator and an Independent P.E. CORRECTIVE ACTION: Complete and submit to CUPA a copy of closure plan or closure certification signed by owner or operator and independent, professional engineer registered in California. | [6 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230044 |  |  | Permit by Rule: Cyanide Process Solution Addition to Aqueous Waste | Failure of the owner or operator to meet the applicable requirements while adding spent cyanide-containing process solutions to the aqueous waste for the purpose of reducing cyanide processing hazards. | 22 CCR 45 67450.11(d)(7)(A), 67450.11(d)(7)(B), 67450.11(d)(7)(C), 67450.11(d)(7)(D) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 53 54 | General Operating Requirements | PBR | Processing hazards reduced by properly adding cyanide-process solutions to aqueous wastes | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator to meet the applicable requirements while adding spent cyanide-containing process solutions to the aqueous waste for the purpose of reducing cyanide processing hazards. |  |  | OBSERVATION: Owner/Operator failed to meet the requirements while adding spent cyanide-containing process solutions to the aqueous waste for the purpose of reducing cyanide processing hazards. CORRECTIVE ACTION: Ensure that compliance with the requirements have been met when adding spent cyanide-containing process solutions to the aqueous waste for the purpose of reducing cyanide processing hazards. Submit documentation to CUPA that states how this is achieved. | OBSERVATION: The Generator failed to meet all of the requirements for treating spent cyanide-containing process solution. The Generator shall: treat HW that is generated onsite, the treatment of the waste is not regulated under RCRA, the waste is not reactive pursuant to section 66261.23 or extremely hazardous pursuant to sections 66261.107 or 66261.110, the HW is hazardous because it contains cyanide or a combination of cyanide and metals, the treatment is conducted solely for the purpose of treating cyanide-containing wastes. The only treatment technologies used are the ones listed in this section for the waste stream(s) eligible to be treated, the treatment is only conducted for the purpose of treating eligible constituent(s), all treatment is conducted in tanks or containers and all discharges to air comply with federal, state, and local air pollution control requirements. Spent cyanide-containing process solutions may be treated by slow addition to the aqueous waste generated by rinsing work pieces and fixtures holding work pieces that were processed in cyanide-containing solutions and by rinsing containers, pumps, hoses, and other equipment used to transfer cyanide solutions onsite for the purpose of reducing cyanide processing hazards, provided that the owner or operator is in compliance with the following requirements: Solutions resulting from the mixing authorized shall be further treated by processes listed below and in accordance with the other provisions of this subsection. The only treatment processes that can be used are: oxidation by addition of hypochlorite, oxidation by addition of peroxide or ozone, with or without the use of ultraviolet light, alkaline chlorination, electrochemical oxidation, and ion exchange or reverse osmosis. Owners or operators managing cyanide-containing spent process solutions shall ensure that the concentration of cyanide in solutions treated with the processes listed above shall not exceed 5000 milligrams per liter or parts per million (ppm) of total cyanide, residual solids generated by any treatment process allowed in section 67450.11, such as filter cakes and sludges from clarifiers, are either recycled by a facility that recovers metals from the residual solids, or are partially reclaimed for further processing by another metal recovery facility or determined not amenable for recycling due to technological or economic reasons. A justification statement is prepared when any residual solids are not recycled as listed above in a calendar year. Owners or operators shall complete this justification statement by January 30, for any shipment of residual solids not recycled in the previous calendar year. The justification statement shall include all of the following: chemical composition of the residual solids, including but not limited to, the concentration and type of the metals present, cyanide concentration, and water content; and the total weight or volume of the residual solid not recycled during the previous calendar year, the chemical composition of the spent process solutions, including but not limited to, the concentration and type of metals present, and cyanide concentration; and the total weight or volume of the spent process solution treated during the previous calendar year, current year cost estimates expressed in dollars per pound or dollars per gallon for the following HW management options, including transportation: offsite disposal of the residual solids including treatment, offsite recycling of the residual solids, offsite treatment of process solutions and onsite treatment of process solutions. A basis for the decision to not recycle the residual solids as either: technological and provide the chemical, physical, hazardous characteristics, or other properties that affect recycling the residual solids or economic and provide a comparison of the HW management costs including, but not limited to, all costs listed in subparagraph (7)(C)1 and (7)(C)2 for both managing the residual solids and managing the spent process solutions. The justification statement may include any other information that influenced or formed the basis of the generator's decision to not recycle the residual solids. This supplemental information may include the availability of suitable processing technology and facilities or the marketability of the residual solid or its reclaimed components. CORRECTIVE ACTIONS: Ensure that the HW treatment unit meets all of the requirements listed. Provide supporting documentation that demonstrates compliance with the requirements to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230045 |  |  | Permit by Rule: Treatment of Cyanide Waste Solutions | Failure of the generator to meet the specified requirement while treating cyanide waste solutions under Permit by Rule. | 22 CCR 45 67450.11(d)(1),(2),(3) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 54 55 | General Operating Requirements | PBR | Cyanide-containing aqueous wastes are treated | 45 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the generator to meet the specified requirement while treating cyanide waste solutions under Permit by Rule. |  |  | OBSERVATION: Owner/Operator failed to meet the requirements for treating cyanide-containing aqueous wastes. CORRECTIVE ACTION: Ensure that compliance with the requirements have been met to or treating cyanide-containing aqueous wastes. Submit documentation to CUPA that states how this is achieved. | OBSERVATION: The Generator failed to meet all of the requirements for treating cyanide-containing aqueous wastes. The Generator shall: treat HW that is generated onsite, the treatment of the waste is not regulated under RCRA, the waste is not reactive pursuant to section 66261.23 or extremely hazardous pursuant to sections 66261.107 or 66261.110, the HW is hazardous because it contains cyanide or a combination of cyanide and metals, the treatment is conducted solely for the purpose of treating cyanide-containing wastes. The only treatment technologies used are the ones listed in this section for the waste stream(s) eligible to be treated, the treatment is only conducted for the purpose of treating eligible constituent(s), all treatment is conducted in tanks or containers and all discharges to air comply with federal, state, and local air pollution control requirements. Cyanide-containing wastes eligible for treatment are: aqueous wastes generated by rinsing work pieces and fixtures holding work pieces that were processed in cyanide-containing solutions, aqueous wastes generated by reverse osmosis or the regeneration of demineralizer (ion exchange) columns that were used for recycling of wastewaters at facilities that maintain zero discharge of wastewaters derived from the treatment of cyanide-containing aqueous waste, aqueous wastes generated by rinsing containers, pumps, hoses, and other equipment used to transfer cyanide solutions onsite, aqueous wastes generated by the following onsite recycling activities: rinsing spent anode bags prior to onsite reuse or rinsing empty containers prior to onsite use, aqueous wastes generated by onsite laboratories conducting analyses and testing, spent process solutions managed in accordance with the requirements of subsection (d)(6) and spent process solutions managed in accordance with the requirements of subsection (d)(7). The following processes may be used to treat the wastes: oxidation by addition of hypochlorite, oxidation by addition of peroxide or ozone, with or without the use of ultraviolet light, alkaline chlorination, electrochemical oxidation, and ion exchange or reverse osmosis. CORRECTIVE ACTIONS: Ensure that the HW treatment unit meets all of the requirements listed. Provide supporting documentation that demonstrates compliance with the requirements to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Training | 3220002 |  |  | Permit by Rule: Cyanide Treatment Training | Failure to provide initial and annual training to employees, who handle cyanide process solutions, cyanide-containing rinse waters, or manage cyanide-containing aqueous waste, on how to reduce wastes in the production area, including, but not limited to, procedures to: 1. reduce drag-out of plating baths, 2. minimize contaminants in process baths, 3. extend process bath life, 4. minimize chemical spills and splashes from process and rinse solutions handling practices, and 5. respond to chemical spills to reduce waste and minimize releases from process and rinse solutions handling practices. | 22 CCR 45 67450.11(d)(4)(D) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 55 56 | General Operating Requirements | PBR | Training for cyanide treatment has been provided | 49 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide initial and annual training to employees, who handle cyanide process solutions, cyanide-containing rinse waters, or manage cyanide-containing aqueous waste, on how to reduce wastes in the production area, including, but not limited to, procedures to: 1. reduce drag-out of plating baths, 2. minimize contaminants in process baths, 3. extend process bath life, 4. minimize chemical spills and splashes from process and rinse solutions handling practices, and 5. respond to chemical spills to reduce waste and minimize releases from process and rinse solutions handling practices. |  |  | OBSERVATION: Training for reducing wastes in the production area for cyanide treatment was not provided to employees. CORRECTIVE ACTION: Ensure that employees who handle/manage cyanide wastes are provided training. Submit employee training documentation including outline and roster to the CUPA. | OBSERVATION: The Owner/Operator of the FTU is not in compliance with providing initial and annual training to employees who handle/manage cyanide treatment processes. The Owner/Operator of the FTU must be in compliance with providing initial and annual training to employees who handle cyanide process solutions, cyanide-containing rinse waters, or manage cyanide-containing aqueous waste, on how to reduce wastes in the production area, including, but not limited to, procedures to: reduce drag-out of plating baths, minimize contaminants in process baths, extend process bath life, minimize chemical spills and splashes from process and rinse solutions handling practices, and respond to chemical spills to reduce waste and minimize releases from process and rinse solutions handling practices. CORRECTIVE ACTIONS: Ensure that employees who handle/manage cyanide treatment processes are provided initial and annual training that is in compliance with the requirements of this section. Submit supporting documentation that demonstrates compliance with these requirements to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230049 |  |  | Permit by Rule: Treatment of Aqueous Waste Containing Chromium VI | Failure of the generator to meet the Permit by Rule requirements for the treatment of Chromium VI waste, including automatically controlled addition of both pH and the reducing agents. | 22 CCR 45 67450.11(a)(1) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 56 57 | General Operating Requirements | PBR | Aqueous wastes containing hexavalent chromium are properly treated | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the generator to meet the Permit by Rule requirements for the treatment of Chromium VI waste, including automatically controlled addition of both pH and the reducing agents. |  |  | OBSERVATION: Owner/Operator failed to meet the Permit by Rule requirements for the treatment of Chromium VI waste, including automatically controlled addition of both pH and the reducing agents. CORRECTIVE ACTION: Immediately comply with Permit by Rule requirements for the treatment of Chromium VI waste, including automatically controlled addition of both pH and the reducing agents. Submit documentation to the CUPA to indicate what actions have been taken to comply with this requirement. | OBSERVATION: The Generator failed to meet all of the requirements for treating aqueous wastes which contain hexavalent chromium, which is greater than or equal to 750 ppm. The Generator shall follow these requirements: Treat HW that is generated onsite, the total volume of HW treated in the unit, in any calendar month, shall not be less than 55 gallons, the treatment of the waste is not regulated under RCRA, the waste is not reactive pursuant to section 66261.23 or extremely hazardous pursuant to sections 66261.107 or 66261.110, the waste to be treated is a HW only because it contains one or more constituents listed in this section. The only treatment technologies used are the ones listed in this section for the waste stream(s) eligible to be treated, the treatment is only conducted for the purpose of treating eligible constituent(s), all treatment is conducted in tanks or containers and all discharges to air comply with federal, state, and local air pollution control requirements. The treatment technologies that can be used are: reduction of hexavalent chromium to trivalent chromium with sodium bisulfite, sodium metabisulfite, sodium thiosulfate, ferrous sulfate, ferrous sulfide or sulfur dioxide, provided both pH and addition of the reducing agent are automatically controlled. CORRECTIVE ACTIONS: Ensure that the HW treatment unit meets all of the requirements listed. Provide supporting documentation that demonstrates compliance with the requirements to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230072 |  |  | Treatment: Precaution Requirement for Reactive and Ignitable Waste | Failure to take precautions to prevent accidental ignition or reaction of ignitable or reactive waste. This waste shall be separated and protected from sources of ignition or reaction including but not limited to: Open flames, smoking, cutting and welding, hot surfaces, frictional heat, sparks (static, electrical, or mechanical), spontaneous ignition (e.g., from heat-producing chemical reactions), and radiant heat. While ignitable or reactive waste is being handled, the owner or operator shall confine smoking and open flame to specially designated locations. “No Smoking” signs shall be conspicuously placed wherever there is a hazard from ignitable or reactive waste. | 22 CCR 15 66265.17(a), 67450.3(c)(9)(A) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 57 58 | Observations | All Tiers | Ignitable or reactive HW containers are protected from sources of ignition or reaction | 86 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure to take precautions to prevent accidental ignition or reaction of ignitable or reactive waste. This waste shall be separated and protected from sources of ignition or reaction including but not limited to: Open flames, smoking, cutting and welding, hot surfaces, frictional heat, sparks (static, electrical, or mechanical), spontaneous ignition (e.g., from heat-producing chemical reactions), and radiant heat. While ignitable or reactive waste is being handled, the owner or operator shall confine smoking and open flame to specially designated locations. “No Smoking” signs shall be conspicuously placed wherever there is a hazard from ignitable or reactive waste. |  |  | OBSERVATION: The ignitable or reactive HW containers stored at this facility were not protected from sources of ignition or reaction. CORRECTIVE ACTION: Immediately ensure that all ignitable or reactive HW containers are protected from sources of ignition or reaction. Provide photos and other supporting documentation that demonstrate compliance with this requirement to the CUPA. | OBSERVATION: The owner or operator failed to protect ignitable or reactive HW containers from sources of ignition or reaction. The owner or operator shall take precautions to prevent accidental ignition or reaction of ignitable or reactive waste. This waste shall be separated and protected from sources of ignition or reaction including but not limited to: open flames, smoking, cutting and welding, hot surfaces, frictional heat, sparks (static, electrical, or mechanical), spontaneous ignition (e.g., from heat-producing chemical reactions), and radiant heat. While ignitable or reactive waste is being handled, the owner or operator shall confine smoking and open flame to specially designated locations. "No Smoking" signs shall be conspicuously placed wherever there is a hazard from ignitable or reactive waste. CORRECTIVE ACTIONS: Immediately take precautions to prevent the accidental ignition or reaction of the HW being stored at this facility. Provide supporting documentation that demonstrates compliance with this requirement to the CUPA. | [5 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Operations/Maintenance | 3230088 |  |  | Conditional Authorization Treatment: Security | Failure to provide a posted sign stating "Danger Hazardous Waste Area - Keep Out" and to provide one of the following means of security to the active hazardous waste portion of the facility: 1) A 24-hour surveillance system (e.g., television monitoring or surveillance by guards or facility personnel) which continuously monitors and controls entry; or 2) A) An artificial or natural barrier (e.g., a fence in good repair or a fence combined with a cliff), which completely surrounds area; and B) A means to control entry, at all times, through the gates or other entrances (e.g., an attendant, television monitors, locked entrance, or controlled roadway access to the facility). | 22 CCR 15 66265.14; HSC 6.5 25200.3(c)(1) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 58 59 | Observations | CA | The facility has adequate security-Sign posted and surveillance, barrier or entry control provided | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to provide a posted sign stating "Danger Hazardous Waste Area - Keep Out" and to provide one of the following means of security to the active hazardous waste portion of the facility: 1) A 24-hour surveillance system (e.g., television monitoring or surveillance by guards or facility personnel) which continuously monitors and controls entry; or 2) A) An artificial or natural barrier (e.g., a fence in good repair or a fence combined with a cliff), which completely surrounds area; and B) A means to control entry, at all times, through the gates or other entrances (e.g., an attendant, television monitors, locked entrance, or controlled roadway access to the facility). |  |  | OBSERVATION: Owner/Operator failed to provide a posted sign stating "Danger Hazardous Waste Area - Keep Out", and a surveillance system or a barrier and a means to control entry. CORRECTIVE ACTION: Provide required sign and surveillance system or a barrier and a means to control entry. | [6 empty] | Yes | Yes | No | No | No | No | No
Tiered Permitting | Operations/Maintenance | 3230069 |  |  | Treatment: PBR Hazardous Waste Tanks | Failure to comply with general tank operating requirements: a) Hazardous wastes or treatment reagents shall not be placed in a tank system if they could cause the tank, its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail. b) The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: 1) Spill prevention controls (e.g., check valves, dry discount couplings); 2) Overfill prevention controls (e.g., level sensing devices, high level alarms, automatic feed cutoff, or bypass to a standby tank); and 3) Maintenance of sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. | 22 CCR 45 67450.3(c)(9)(F); 22 CCR 15 66265.194 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 59 60 | Observations | PBR | Tanks are compatible with hazardous waste and have spill/overflow prevention provided | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with general tank operating requirements: a) Hazardous wastes or treatment reagents shall not be placed in a tank system if they could cause the tank, its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail. b) The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: 1) Spill prevention controls (e.g., check valves, dry discount couplings); 2) Overfill prevention controls (e.g., level sensing devices, high level alarms, automatic feed cutoff, or bypass to a standby tank); and 3) Maintenance of sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. |  |  | OBSERVATION: Appropriate controls and practices are not in place to prevent spills and overflows from the [HAZARDOUS WASTE] tank or secondary containment system. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank or secondary containment system meets all requirements identified above. | OBSERVATION: The owner or operator failed to operate a HW tank system properly. HW or treatment reagents shall not be placed in a tank system if they could cause the tank, its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail. The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: spill prevention controls (e.g., check valves, dry discount couplings), overfill prevention controls (e.g., level sensing devices, high level alarms, automatic feed cutoff, or bypass to a standby tank), and maintenance or sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. The owner or operator shall comply with the requirements of section 66265.196 if a leak or spill occurs in the tank system. Transfer, treatment or storage of HW in tanks shall comply with section 66265.17(b). CORRECTIVE ACTIONS: Immediately operate the HW tank system at this facility according to the requirements listed. Provide supporting documentation that demonstrates compliance with these requirements to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Abandonment/Illegal Disposal/Unauthorized Treatment | 3250004 |  |  | Treatment: PBR Tank Closure and Documentation | Failure of owner or operator to properly close a hazardous waste tank system ensuring the minimization of further maintenance and that all other requirements have been met. | 22 CCR 45 67450.3(c)(11); 22 CCR 15 66265.111, 114, 197 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 60 61 | Observations | PBR | The HW tank system was properly closed | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 30 | Failure of owner or operator to properly close a hazardous waste tank system ensuring the minimization of further maintenance and that all other requirements have been met. |  |  | OBSERVATION: The HW tank system was not closed properly in accordance with the requirements. CORRECTIVE ACTIONS: Immediately close the HW tank system according to the requirements listed. Provide photos and other supporting documentation that demonstrate compliance with this requirement to the CUPA. | OBSERVATION: The generator failed to properly close the HW tank system according to the closure performance standard, the disposal or decontamination of equipment, structures, soils, and closure and post closure-care. The generator shall upon terminating operation of any HW tank system, remove or decontaminate all waste residues, containment system components, soils and structures or equipment contaminated with HW from the tank system. The removal of the HW tank system from service shall be conducted in a manner that does both of the following: minimizes the need for further maintenance, eliminates the escape of HW, HW constituents, leachate, contaminated runoff, or waste decomposition products to the ground or surface waters or to the atmosphere after the treatment process is no longer in operation. During the partial and final closure periods, all contaminated equipment, structures and soil shall be properly disposed of, or decontaminated by removing all HW and residues. If the owner or operator demonstrates that not all contaminated soils can be practicably removed or decontaminated as required, then the owner or operator shall close the tank system and perform post-closure care in accordance with the closure and post-closure care requirements that apply to landfills (section 66265.310). CORRECTIVE ACTIONS: Immediately ensure that the HW tank system is closed properly according to the listed requirements. Provide supporting documentation that demonstrates compliance with these requirements to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230075 |  |  | Permit-by-Rule Treatment: Security | Failure of owner or operator to provide posted sign stating "Danger Hazardous Waste Area - Keep Out" and to provide one of the following means of security to the active hazardous waste portion of the facility: 1) A 24-hour surveillance system (e.g., television monitoring or surveillance by guards or facility personnel) which continuously monitors and controls entry; or 2) A) An artificial or natural barrier (e.g., a fence in good repair or a fence combined with a cliff), which completely surrounds area; and B) A means to control entry, at all times, through the gates or other entrances (e.g., an attendant, television monitors, locked entrance, or controlled roadway access to the facility). | 22 CCR 45 67450.3 (c)(9)(A); 22 CCR 15 66265.14 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 61 62 | Observations | PBR | The facility has adequate security-sign posted and surveillance, barrier or entry control provided | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of owner or operator to provide a posted sign stating "Danger Hazardous Waste Area - Keep Out" and to provide one of the following means of security to the active hazardous waste portion of the facility: 1) A 24-hour surveillance system (e.g., television monitoring or surveillance by guards or facility personnel) which continuously monitors and controls entry; or 2) A) An artificial or natural barrier (e.g., a fence in good repair or a fence combined with a cliff), which completely surrounds area; and B) A means to control entry, at all times, through the gates or other entrances (e.g., an attendant, television monitors, locked entrance, or controlled roadway access to the facility). |  |  | OBSERVATION: The HW facility does not have adequate security, including a posted sign stating "Danger Hazardous Waste Area - Keep Out", and to provide one of the following means of security to the active hazardous waste portion of the facility: 1) A 24-hour surveillance system (e.g., television monitoring or surveillance by guards or facility personnel) which continuously monitors and controls entry; or 2) A) An artificial or natural barrier (e.g., a fence in good repair or a fence combined with a cliff), which completely surrounds area; and B) A means to control entry, at all times, through the gates or other entrances (e.g., an attendant, television monitors, locked entrance, or controlled roadway access to the facility). CORRECTIVE ACTION: Immediately ensure that security for this facility meets the requirements noted above. Provide photos and other supporting documentation that demonstrate compliance with this requirement to the CUPA. | OBSERVATION: The owner or operator failed to provide security for this facility. The owner or operator shall prevent the unknowing entry, and minimize the possibility for the unauthorized entry, of persons or livestock onto the active portion of the facility, unless the owner or operator can demonstrate to the department that physical contact with the waste, structures, or equipment within the active portion of the facility will not injure unknowing or unauthorized persons or livestock which may enter the active portion of the facility, disturbance of the waste or equipment, by the unknowing or unauthorized entry of persons or livestock onto the active portion of a facility will not cause a violation of the requirements of this chapter. Unless the owner or operator has made a successful demonstration under subsection (a)(1) and (2) of this section, a facility shall have : a 24-hour surveillance system (e.g., television monitoring or surveillance by guards or facility personnel) which continuously monitors and controls entry onto the active portion of the facility or an artificial or natural barrier (e.g., a fence in good repair or a fence combined with a cliff), which completely surrounds the active portion of the facility and a means to control entry, at all times, through the gates or other entrances to the active portion of the facility (e.g., an attendant, television monitors, locked entrance, or controlled roadway access to the facility). The requirements of this section shall be satisfied if the facility or plant within which the active portion is located itself has a surveillance system, or a barrier and a means to control entry which complies with the requirements. Unless the owner or operator has made a successful demonstration, a sign with the legend "Danger Hazardous Waste Area - Unauthorized Personnel Keep Out," shall be posted at each entrance to the active portion of a facility, and at other locations, in sufficient numbers to be seen from any approach to this active portion. The legend shall be written in English, Spanish and in any other language predominant in the area surrounding the facility, and shall be legible from a distance of at least 25 feet. Existing signs with a legend other than "Danger Hazardous Waste Area - Unauthorized Personnel Keep Out" may be used if the legend on the sign indicates that only the authorized personnel are allowed to enter the active portion, and that entry onto the active portion can be dangerous. CORRECTIVE ACTIONS: Immediately ensure that the security for this facility meets the requirements listed. Provide supporting documentation that demonstrates compliance with this requirement to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230048 |  |  | Permit by Rule: FTU Markings | Failure to permanently mark the exterior of each FTU with the name of the person which owns or operates the FTU, facility identification number and an individual serial number. | 22 CCR 45 67450.3(c)(7) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Revised | 62 63 | Observations | PBR | The exterior of the treatment unit is marked with name of owner/operator, Fac ID#, & unit serial # | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to permanently mark the exterior of each FTU with the name of the person which owns or operates the FTU, facility identification number and an individual serial number. |  |  | OBSERVATION: Owner/operator has failed to permanently mark the exterior of the treatment unit with the name of the owner or operator, the Facility ID #, or the unit serial #. CORRECTIVE ACTION: Properly mark the exterior of the treatment unit with the name or owner or operator, Facility ID #, and unit serial #. Provide photos and other supporting documentation that demonstrate compliance with this requirement to the CUPA. | OBSERVATION: The owner or operator failed to permanently mark the exterior of the treatment unit. The owner or operator of a treatment unit deemed to hold a permit by rule shall permanently mark the exterior of each treatment unit with the name of the person which owns or operates the treatment unit, facility identification number and an individual serial number. CORRECTIVE ACTIONS: Ensure that the HW treatment unit meets all of the requirements listed. Provide supporting documentation that demonstrates compliance with the requirements to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Operations/Maintenance | 3230046 |  |  | Permit by Rule: Cyanide Treatment Waste Reduction | Failure of the owners or operators treating cyanide waste solutions to implement best management practices (BMP) to reduce waste generation, and minimize or eliminate releases to work areas and the environment. | 22 CCR 45 67450.11(d)(4)(A), (B), (C) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 63 64 | Observations | PBR | Implementing BMPs to reduce Cyanide-containing waste generated and minimize releases | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the owners or operators treating cyanide waste solutions to implement best management practices (BMP) to reduce waste generation, and minimize or eliminate releases to work areas and the environment. |  |  | OBSERVATION: Owner/Operator treating cyanide waste solutions failed to implement best management practices to reduce waste generation, and minimize or eliminate releases to work areas and the environment. CORRECTIVE ACTION: For the treatment of cyanide waste solutions you must ensure to implement best management practices to reduce waste generation, and minimize or eliminate releases to work areas and the environment. Provide documentation that demonstrates compliance with this requirement to the CUPA. | OBSERVATION: The owners or operators of the treatment unit failed to reduce the generation of cyanide-containing wastes. The owners or operators of all sites or facilities subject to subsection (d) shall implement the following to reduce waste generation and minimize or eliminate releases to work areas and the environment: use holding racks and/or drain boards between all process and rinse tanks to contain plating drag-out, rinse solution drag-out, and return drag-out solutions to process tanks, use countercurrent rinsing to reduce water use and wastewater generation when multiple sequential rinse tanks are used, at a minimum, every four (4) years, review the use of cyanide-containing process baths to determine if a non-cyanide alternative with equivalent results is available as part of: the Source Reduction Evaluation Review and Plan pursuant to HSC section 25244.19, an Environmental Management System or an environmental performance evaluation plan. Provide initial and annual training to employees, who handle cyanide process solutions, cyanide -containing rinse waters, or manage cyanide-containing aqueous waste, on how to reduce wastes in the production area, including, but not limited to, procedures to: reduce drag-out of plating baths, minimize contaminants in process baths, extend process bath life, minimize chemical spills and splashes from process and rinse solutions handling practices, and respond to chemical spills to reduce waste and minimize releases from process and rinse solutions handling practices. CORRECTIVE ACTIONS: Ensure that the HW treatment unit meets all of the requirements listed. Provide supporting documentation that demonstrates compliance with the requirements to the CUPA. | [5 empty] | Yes | No | No | No | No | No | Yes
Tiered Permitting | Administration/Documentation | 3210 |  |  | Tiered Permitting - Administration/Documentation - General | Administration/Documentation - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 64 65 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Administration/Documentation | 3215 |  |  | Tiered Permitting - Administration/Documentation - General Local Ordinance | Administration/Documentation - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 65 66 | General Facility Requirements |  | Administration/Documentation - General Local Ordinance | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Training | 3220 |  |  | Tiered Permitting - Training - General | Training - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 66 67 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Training | 3225 |  |  | Tiered Permitting - Training - General Local Ordinance | Training - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 67 68 | General Facility Requirements |  | Training - General Local Ordinance | 34 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Operations/Maintenance | 3230 |  |  | Tiered Permitting - Operations/Maintenance - General | Operations/Maintenance - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 68 69 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Operations/Maintenance | 3235 |  |  | Tiered Permitting - Operations/Maintenance - General Local Ordinance | Operations/Maintenance - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 69 70 | General Facility Requirements |  | Operations/Maintenance - General Local Ordinance | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Release/Leaks/Spills | 3240 |  |  | Tiered Permitting - Release/Leaks/Spills - General | Release/Leaks/Spills - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 70 71 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Release/Leaks/Spills | 3245 |  |  | Tiered Permitting - Release/Leaks/Spills - General Local Ordinance | Release/Leaks/Spills - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 71 72 | General Facility Requirements |  | Release/Leaks/Spills - General Local Ordinance | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Abandonment/Illegal Disposal/Unauthorized Treatment | 3250 |  |  | Tiered Permitting - Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 72 73 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Tiered Permitting | Abandonment/Illegal Disposal/Unauthorized Treatment | 3255 |  |  | Tiered Permitting - Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 73 74 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## RCRA
Violation Program | Violation Category | Violation Type Number | UST Performance Measure | RCRA Violation Type | Name | Description | Citations | Begin Date | End Date | Updated On | Comments | Checklist Item Order | Inspection Checklist Heading _Optional_ | Inspection Checklist Sub_Heading _Optional_ | Inspection Checklist Item Text _What Appears on the Checklist_ | Length of Checklist Item Text | Display NVO Checkbox? | Display OUT of Compliance Checkbox? | Display NA Checkbox? | Display UD Checkbox? | Display COS Checkbox? | Display Repeat Checkbox? | Display Degree of Violation Drop_Down | Default Degree of Violation | Required Item? | Points _Optional_ | Comply By Days _Optional_ | Violation Descriptive Text | TCR Designation | Violation Corrective Text _Optional_ | Inspector Comment 1 _Optional_ | Inspector Comment 2 _Optional_ | Inspector Comment 3 _Optional_ | Inspector Comment 4 _Optional_ | Inspector Comment 5 _Optional_ | Inspector Comment 6 _Optional | Inspector Comment 7 _Optional | RCRA LQG
RCRA Large Quantity Generator | Administration/Documentation | 3110001 |  | 262.A | RCRA: EPA ID Number | Failure to obtain an Identification Number prior to treating, storing, disposing of, transporting or offering for transportation any hazardous waste. | 22 CCR 12 66262.12 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 1 | Recordkeeping/ Documentation | ID Number | Obtained an Identification Number (unless exempted HSC 25143.13) | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain an Identification Number prior to treating, storing, disposing of, transporting or offering for transportation any hazardous waste. |  |  | OBSERVATION: The generator has not obtained an Identification Number to manage hazardous waste. A hazardous waste generator shall not treat, store, dispose of, transport or offer for transportation, hazardous waste without obtaining an Identification Number. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you have obtained an Identification Number. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130018 |  | 262.C | RCRA: Contingency Plan | Failure to prepare and implement a written Contingency Plan to minimize hazards to human health or the environment from fires, explosions, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.51 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 2 | Recordkeeping/ Documentation | Contingency Plan | Contingency Plan prepared and implemented | 41 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare and implement a written Contingency Plan to minimize hazards to human health or the environment from fires, explosions, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water. |  |  | OBSERVATION: Facility failed to prepare an Contingency Plan. The owner or operator shall prepare an Emergency Response Plan designed to minimize hazards to human health or the environment from fires, explosions, or any unplanned release of hazardous waste to air, soil, or surface water. CORRECTIVE ACTION: Immediately prepare an Contingency Plan and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110012 |  | 262.D | RCRA: Contingency Plan Copies | Failure to maintain a copy of the contingency plan and all its revisions at the facility and to submit a copy to all local police departments, fire departments, hospitals, and State and local emergency response teams that may be called upon to provide emergency services. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.53 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 3 | Recordkeeping/ Documentation | Contingency Plan | Contingency Plan and all revisions maintained at the facility | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to maintain a copy of the contingency plan and all its revisions at the facility and to submit a copy to all local police departments, fire departments, hospitals, and State and local emergency response teams that may be called upon to provide emergency services. |  |  | OBSERVATION: A copy of the Contingency Plan is not maintained at the facility. CORRECTIVE ACTION: Locate a copy of the Contingency Plan, maintain it at the facility, and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110011 |  | 262.C | RCRA: Contingency Plan Emergency Action Plan | Failure to include all of the following in the Contingency Plan: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. (If the owner or operator has already prepared a Spill Prevention, Control, and Countermeasures (SPCC) Plan or some other emergency or contingency plan, the owner or operator need only amend that plan to incorporate hazardous waste management provisions.) | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.52 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 4 | Recordkeeping/ Documentation | Contingency Plan | Contingency plan contains all required content | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to include all of the following in the Contingency Plan: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. (If the owner or operator has already prepared a Spill Prevention, Control, and Countermeasures (SPCC) Plan or some other emergency or contingency plan, the owner or operator need only amend that plan to incorporate hazardous waste management provisions.) |  |  | OBSERVATION: The Contingency Plan does not contain one or more of the following: description of actions personnel will take in response to a release or emergency, arrangements with local authorities, list of emergency coordinators including name, addresses & phone numbers, list of emergency equipment and their physical description, location and capabilities, evacuation plan, and OES phone number. CORRECTIVE ACTION: Revise the Contingency Plan to include all the content required by 22 CCR 15 66265.52 and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Training | 3120001 |  | 262.A | RCRA: Employee Hazardous Waste Training | Failure to provide employees with hazardous waste training program of class room instructions or on-the-job training within the first six months after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. Training records on current personnel shall be kept until closure of the facility and for former employees the record shall be kept for at least three years from the date the employee last worked at the facility. The records shall include the following: the job title for each position at the facility related to hazardous waste management, and the name of the employee filling each job; a written job description for each position, duties of facility personnel assigned to each position, and a written description of the type and amount of both introductory and continuing training that will be given to each person filling a position. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.16 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 5 | Recordkeeping/ Documentation | Training | Trained facility personnel annually and maintained required documentation until closure | 87 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to provide employees with hazardous waste training program of class room instructions or on-the-job training within the first six months after the date of their employment or assignment to a facility, or to a new position at a facility and annually thereafter. Training records on current personnel shall be kept until closure of the facility and for former employees the record shall be kept for at least three years from the date the employee last worked at the facility. The records shall include the following: the job title for each position at the facility related to hazardous waste management, and the name of the employee filling each job; a written job description for each position, duties of facility personnel assigned to each position, and a written description of the type and amount of both introductory and continuing training that will be given to each person filling a position. |  |  | OBSERVATION: As demonstrated by the hazardous waste violations observed at the time of inspection, personnel are not adequately trained to perform their duties in a way that ensures the facility's compliance with the requirements of this chapter, and/or proper training documentation has not been maintained. CORRECTIVE ACTION: Conduct training with applicable personnel and document it according to the requirements of 22 CCR 15 66265.16(d). Submit a copy of the documentation to the CUPA. | OBSERVATION: Documented training of personnel was not available at the time of inspection. CORRECTIVE ACTION: Locate training documentation or conduct training with applicable personnel and document it. Submit a copy of the training documentation to the CUPA. | [5 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110002 |  | 262.B | RCRA: Preparation of the Hazardous Waste Manifest | Failure to prepare a Uniform Hazardous Waste Manifest and, if necessary, a Continuation Sheet, before the transport of a hazardous waste off-site for transfer, treatment, storage, or disposal. | 22 CCR 12 66262.20 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 6 | Recordkeeping/ Documentation | Manifest | Prepared a Uniform Hazardous Waste Manifests for transportation of hazardous waste | 82 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to prepare a Uniform Hazardous Waste Manifest and, if necessary, a Continuation Sheet, before the transport of a hazardous waste off-site for transfer, treatment, storage, or disposal. |  |  | OBSERVATION: [LIST WASTE] was transported by [LIST TRANSPORTER] to [LIST LOCATION] and a Uniform Hazardous Waste Manifest was not prepared. CORRECTIVE ACTION: For future shipments of the above noted waste, prepare a Uniform Hazardous Waste Manifest prior to being transported to, or offered for transportation to, an off-site facility. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110003 |  | 262.B | RCRA: Hazardous Waste Manifest Completeness | Failure to properly complete the Uniform Hazardous Waste Manifest. | 22 CCR 12 66262.23(a) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 7 | Recordkeeping/ Documentation | Manifest | Properly completed all Uniform Hazardous Waste Manifests | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to properly complete the Uniform Hazardous Waste Manifest. |  |  | OBSERVATION: The Uniform Hazardous Waste Manifest [MANIFEST #] does not contain [LIST MISSING REQUIREMENTS]. CORRECTIVE ACTION: Contact the DTSC to make necessary corrections to the manifests and submit a copy to the CUPA. | OBSERVATION: The Uniform Hazardous Waste Manifest [MANIFEST #] contained the following errors: [LIST ERRORS]. CORRECTIVE ACTION: Contact the DTSC to make necessary corrections to the manifests and submit a copy to the CUPA. | [5 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110004 |  | 262.D | RCRA: Hazardous Waste Manifest Exception Requirement | Failure to complete the Uniform Hazardous Waste Manifest exception requirements. | 22 CCR 12 66262.42 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 8 | Recordkeeping/ Documentation | Manifest | Completed all Uniform Hazardous Waste Manifest exception reporting requirements | 79 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to complete the Uniform Hazardous Waste Manifest exception requirements. |  |  | Observation: The generator failed to determine the status of a uniform hazardous waste manifested shipment within 35 days from the date the waste was shipped. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the generator has determined the status of the hazardous waste manifest shipment for [LIST MANIFESTS]. | OBSERVATION: The generator failed to file an exception report with the DTSC after not receiving a destination facility signed copy of the uniform hazardous waste manifest within 45 days of the waste shipment date. CORRECTIVE ACTION: Either locate a copy of the missing manifests or prepare and submit an exception report to DTSC (DTSC Report Repository; Generator Information Services Section; P.O. Box 806; Sacramento, CA 95812-0806). Submit copies to the CUPA. | [5 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110005 |  | 262.D | RCRA: Hazardous Waste Disposal Documentation | Failure to keep a copy of each properly signed manifest for at least three years from the date the waste was accepted by the initial transporter. The manifest signed at the time the waste was accepted for transport shall be kept until receiving a signed copy from the designated facility which received the waste. | 22 CCR 12 66262.40(a) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 9 | Recordkeeping/ Documentation | Manifest | Signed copy of Uniform Hazardous Waste Manifest kept for 3 years | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to keep a copy of each properly signed manifest for at least three years from the date the waste was accepted by the initial transporter. The manifest signed at the time the waste was accepted for transport shall be kept until receiving a signed copy from the designated facility which received the waste. |  |  | OBSERVATION: Uniform Hazardous Waste Manifests for [LIST HAZARDOUS WASTES] were not available at the time of inspection. CORRECTIVE ACTION: Locate a copy of all manifests for [LIST HAZARDOUS WASTES] and submit copies to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110006 |  | 262.D | RCRA: Hazardous Waste Manifest Not Sent to DTSC | Failure to send a legible copy of each hazardous waste manifest that originated in paper form to the Department within 30 days of each shipment of hazardous waste. | 22 CCR 12 66262.23(a)(4); HSC 25160(b)(1)(C) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 10 | Recordkeeping/ Documentation | Manifest | Sent a legible copy of each Uniform Hazardous Waste Manifest to the DTSC within 30 days of shipment | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to send a legible copy of each hazardous waste manifest that originated in paper form to the Department within 30 days of each shipment of hazardous waste. |  |  | OBSERVATION: The generator has not sent a legible copy of each Uniform Hazardous Waste Manifest, that originated in paper form, to the DTSC within 30 days of shipment. CORRECTIVE ACTION: Send a copy of all hazardous waste manifests that originated in paper form to the DTSC and submit a statement to the CUPA demonstrating compliance. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110017 |  |  | Consolidated Manifest | Failure of a generator of hazardous waste that meets the conditions to be transported on a consolidated manifest to comply with one or more of the required consolidated manifesting procedures and retain copies of receipts for three years. | HSC 6.5 25160.2 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 11 | Recordkeeping/ Documentation | Manifest | All consolidated manifest requirements are met | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of a generator of hazardous waste that meets the conditions to be transported on a consolidated manifest to comply with one or more of the required consolidated manifesting procedures and retain copies of receipts for three years. |  |  | OBSERVATION: Owner/Operator failed to comply with one or more consolidated manifesting requirements. CORRECTIVE ACTION: Ensure that all wastes transported on a consolidated manifest meet all consolidated manifest requirements, and maintain copies of manifests for three years. | OBSERVATION: Consolidated manifest receipts for [LIST HAZARDOUS WASTES] were observed missing the following required information [insert missing required regulatory component]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating how all consolidated manifest receipts will be properly completed in the future. | [5 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110018 |  |  | Used Oil Certification Form | Failure to record in an operating log and retain for three years the following information for each shipment of recycled or exempted oil: 1) The name and address of the used oil recycling facility or generator claiming the oil meets the requirements of HSC 6.5 25250.1. 2) The name and address of the facility receiving the shipment. 3) The quantity of oil delivered. 4) The date of shipment or delivery. 5) A cross-reference to the records and documentation required under HSC 6.5 25250.1. | HSC 6.5 25250.1(c), 25250.18(a), 25250.19(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 12 | Recordkeeping/ Documentation | Manifest | Exempt used oil management operating log records are retained for 3 years | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to record in an operating log and retain for three years the following information for each shipment of recycled or exempted oil: 1) The name and address of the used oil recycling facility or generator claiming the oil meets the requirements of HSC 6.5 25250.1. 2) The name and address of the facility receiving the shipment. 3) The quantity of oil delivered. 4) The date of shipment or delivery. 5) A cross-reference to the records and documentation required under HSC 6.5 25250.1. |  |  | OBSERVATION: The generator failed to retain an operating log recording the management of exempt used oil. CORRECTIVE ACTION: Submit documentation to the CUPA that shows the generator has implemented an adequate operating log recording the management of exempt used oil. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110019 |  |  | Lead Battery Disposal Documentation | Failure to retain for at least three years a legible copy of each manifest or bill of lading which identifies spent lead-acid storage batteries shipped to a person who stores the batteries or who uses, reuses, recycles or reclaims the batteries or their components. | 22 CCR 16 66266.81(a)(4)(B) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 13 | Recordkeeping/ Documentation | Manifest | Owner/Operator retained copy of manifest or bill of lading for spent lead acid batteries for 3 years | 100 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to retain for at least three years a legible copy of each manifest or bill of lading which identifies spent lead-acid storage batteries shipped to a person who stores the batteries or who uses, reuses, recycles or reclaims the batteries or their components. |  |  | OBSERVATION: Manifests or bills of lading for spent lead acid batteries recording the shipments off site were not retained at the facility for the past three years. CORRECTIVE ACTION: Obtain copies of all bills of lading for lead-acid batteries recording shipments off site over the past three years. Submit copies of the bills of lading for the past year to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130001 |  | 262.A | RCRA: Hazardous Waste Determination | Failure to determine if wastes generated are hazardous waste by using generator knowledge or applying testing method. | 22 CCR 12 66262.11 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 14 | Recordkeeping/ Documentation | Waste Determination | Determined if waste generated is hazardous waste | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to determine if wastes generated are hazardous waste by using generator knowledge or applying testing method. |  |  | OBSERVATION: Owner/Operator failed to determine if the waste generated {describe waste} is a hazardous waste. CORRECTIVE ACTION: Submit documentation to the CUPA indicating you have determined that the waste in question is hazardous or not and how this determination was made. i.e. Generator knowledge, lab analysis, etc. If determined to be hazardous waste then you must manage it as such. Specify how it is being managed in response documentation. | OBSERVATION: Finely divided metal generated from [DESCRIBE PROCESS] are being [RECYCLED AS SCRAP METAL/ DISPOSED OF TO THE TRASH]. Finely divided metal less than 100 microns in size does not meet the definition of scrap metal. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the finely divided metal has been properly characterized to determine if it is a hazardous waste. If determined to be hazardous submit manifests/receipts documenting proper disposal and a statement demonstrating how you will manage it in the future. | [5 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130028 |  |  | Maintaining records of waste determination for three years | Failure to keep records of any test results, waste analyses, or other determinations made in accordance with section 66262.11 for at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. | 22 CCR 12 66262.40(c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 15 | Recordkeeping/ Documentation | Waste Determination | Kept records of any test results, waste analyses, or other determinations | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to keep records of any test results, waste analyses, or other determinations made in accordance with section 66262.11 for at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. |  |  | Observation: The hazardous waste determination documentation for [LIST WASTE] was not available at the time of inspection for the previous 3 years from the date the waste stream was last managed on site or sent off site for treatment. ORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [WASTE] has been properly characterized to determine if it is a hazardous waste. If determined to be hazardous submit a manifest/receipt documenting proper disposal and a statement demonstrating how you will manage it in the future. | OBSERVATION: The [WASTE] located in the [LOCATION] was observed being [DESCRIBE: HOW DISPOSED OF / HOW TREATED AND DISPOSED OF / ACCUMULATED] and a proper waste determination has not been made. CORRECTIVE ACTION: Immediately cease [DESCRIBE: HOW DISPOSED OF / HOW TREATED AND DISPOSED OF] of [WASTE]. Submit documentation to the CUPA demonstrating that the [WASTE] has been properly characterized to determine if it is a hazardous waste. If determined to be hazardous submit a manifest/receipt documenting proper disposal and a statement demonstrating how you will manage it in the future. Keep the test results, waste analyses, or other determinations at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. | [5 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130002 |  | 262.C | RCRA: Land Disposal Restriction | Failure to determine whether waste is restricted from land disposal. | 22 CCR 12 66262.34(a)(4); 22 CCR 18 66268.7(a) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 16 | Recordkeeping/ Documentation | Waste Determination | Determined land disposal restrictions for hazardous waste | 57 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to determine whether waste is restricted from land disposal. |  |  | OBSERVATION: Land Disposal Restriction (LDR) documentation for [HAZARDOUS WASTE] was not available at the time of inspection. CORRECTIVE ACTION: Submit LDR documentation for [HAZARDOUS WASTE] to the CUPA. Retain the documentation at least three years from the date that the waste was last sent to on-site or off-site treatment, storage, or disposal. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110020 |  |  | General: Electronic data | Failure to report program data electronically. | HSC 6.11 25404(e)(4) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 17 | Recordkeeping/ Documentation | Reporting | Program data reported electronically when required | 50 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to report program data electronically. |  |  | OBSERVATION: Owner/Operator failed to report program data electronically into CERS. CORRECTIVE ACTION: Complete all required reporting into CERS. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110021 |  |  | Excluded Recyclable Materials Report | Failure of any person who recycles more than 100 kilograms per month of recyclable material under a claim that the material qualifies for exclusion or exemption, to submit recyclable materials report every two years. | HSC 6.5 25143.10 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 18 | Recordkeeping/ Documentation | Reporting | Submitted Recyclable Materials Report every two years | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of any person who recycles more than 100 kilograms per month of recyclable material under a claim that the material qualifies for exclusion or exemption, to submit recyclable materials report every two years. |  |  | OBSERVATION: The generator was observed recycling more than 100 kilograms per month of hazardous waste and has not submitted the Recyclable Materials Report in CERS or has failed to submit it every two years. CORRECTIVE ACTION: Complete the recyclable materials report for the most recent reporting period and submit a copy in CERS. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110022 |  |  | Remote Consolidation: Notification | Failure to annually submit notification of generator’s intent to remotely consolidate hazardous waste. | HSC 6.5 25110.10(d) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 19 | Recordkeeping/ Documentation | Reporting | Remote Waste Consolidation Site Annual Notification submitted | 62 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failed to submit Remote Waste Consolidation Site Annual Notification. |  |  | OBSERVATION: The generator consolidates hazardous waste from a remote site and has not submitted the Remote Waste Consolidation Site Annual Notification to the CUPA. CORRECTIVE ACTION: Complete and submit the Remote Waste Consolidation Site Annual Notification to the CUPA through CERS. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110008 |  | 262.D | Source Reduction Report | Failure of a generator to conduct, when required, a source reduction evaluation review and plan every four years, and/or failure of the review and plan to contain all required information. | 22 CCR 31 67100.7, 67100.8 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 20 | Recordkeeping/ Documentation | Reporting | Prepared a hazardous waste management performance report every four years | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a generator to conduct, when required, a source reduction evaluation review and plan every four years, and/or failure of the review and plan to contain all required information. |  |  | OBSERVATION: A hazardous waste management performance report has not been prepared within the past four years. CORRECTIVE ACTION: Prepare a hazardous waste management report that includes all the required information and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110009 |  | 262.D | Summary Progress Report | Failure of a large quantity generator to prepare a summary progress report every four years, using DTSC’s Form # 1262 (3/99) titled "Summary Progress Report". | 22 CCR 31 67100.9 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 21 | Recordkeeping/ Documentation | Reporting | Prepared a summary progress report and submitted it to the DTSC every four years | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a large quantity generator to prepare a summary progress report every four years, using DTSC’s Form # 1262 (3/99) titled "Summary Progress Report". |  |  | OBSERVATION: The generator failed to prepare a summary progress report and has not submitted it to the DTSC every four years. CORRECTIVE ACTION: Prepare a summary progress report and submit a copy to the DTSC and the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110010 |  | 262.D | Source Reduction Plan | Failure to adequately complete, and maintain for review, all requirements of the source reduction evaluation review and plan (SB-14). | 22 CCR 31 67100.3, 67100.4, 67100.5; HSC 6.5 25244.19, 25244.21 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 22 | Recordkeeping/ Documentation | Reporting | Completed all source reduction evaluation review and plan requirements | 70 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to adequately complete, and maintain for review, all requirements of the source reduction evaluation review and plan (SB-14). |  |  | OBSERVATION: A source reduction evaluation review and plan with all the required information has not been completed and maintained for review. CORRECTIVE ACTION: Complete a source reduction report with all the required information and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110007 |  | 262.D | RCRA: Biennial Report | Failure of a large quantity RCRA generator to prepare the Biennial report (Form 8700), and submit to DTSC by March 1st on even numbered years ; and maintain it onsite for three years. | 22 CCR 15 66262.40(b), 66262.41 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 23 | Recordkeeping/ Documentation | Reporting | Prepared a Biennial Report, submitted to DTSC, and kept for 3 years | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of a large quantity RCRA generator to prepare the Biennial report (Form 8700), and submit to DTSC by March 1st on even numbered years ; and maintain it onsite for three years. |  |  | OBSERVATION: The [NOTE WHICH YEARS] Biennial report was not properly prepared or retained. A copy of the Biennial report shall be kept for three years. CORRECTIVE ACTION: Immediately locate a copy of the [note which years] Biennial report and maintain it for three years. | OBSERVATION: The [NOTE WHICH YEARS] Biennial report was not prepared and submitted to DTSC. A generator who ships any hazardous waste offsite to a TSDF within the United States shall prepare and submit a Biennial Report, U.S. EPA Form 8700, to the DTSC by March 1 of each even-numbered year, and shall cover generator activities during the previous calendar year. CORRECTIVE ACTION: Immediately prepare a report for the [note year] calendar year and submit it to the DTSC. Ensure that this report is done in a timely manner. | [5 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150001 |  | 262.A | RCRA: Hazardous Waste Not Transported by Registered Hauler | Failure to use a DTSC registered hazardous waste transporter to transport hazardous waste or transporting hazardous waste without being a DTSC registered hazardous waste transporter. | HSC 6.5 25163(a) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 24 | Hazardous Waste Management | Disposal | Registered hazardous waste transporter used to transport hazardous waste | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to use a DTSC registered hazardous waste transporter to transport hazardous waste or transporting hazardous waste without being a DTSC registered hazardous waste transporter. |  |  | OBSERVATION: Owner/Operator failed to use a DTSC registered hazardous waste transporter to transport hazardous waste or transporting hazardous waste without being a DTSC registered hazardous waste transporter. CORRECTIVE ACTION: Ensure that you use a DTSC registered hazardous waste transporter to transport hazardous waste in the future. Submit a statement to the CUPA stating hazardous wastes will be transported by a registered transporter in the future. | [6 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150003 |  |  | Improper Disposal of Hazardous Waste | Failure to dispose of hazardous waste at a facility which has a permit from DTSC or disposing of hazardous waste at any point which is not authorized. | HSC 6.5 25189.5(a), 25201(a) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 25 | Hazardous Waste Management | Disposal | Disposed of hazardous waste at an authorized location | 53 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to dispose of hazardous waste at a facility which has a permit from DTSC or disposing of hazardous waste at any point which is not authorized. |  |  | OBSERVATION: Owner/Operator failed to dispose of hazardous waste at a facility which has a permit from DTSC or disposed of hazardous waste at a point which is not authorized pursuant to HSC chapter 6.5. CORRECTIVE ACTION: Immediately discontinue disposing of hazardous waste at any facility not permitted by DTSC or to any point which is not authorized pursuant to HSC chapter 6.5. Submit a statement to the CUPA indicating improperly disposed of hazardous waste has been properly managed, and that all hazardous wastes will only be disposed at facilities permitted by DTSC in the future. | [6 empty] | Yes
RCRA Large Quantity Generator | Release/Leaks/Spills | 3140002 |  |  | Quarantine Order | No person shall remove, transfer, or dispose of the hazardous waste until permission for removal, transfer, or disposal is given by an authorized agent. | HSC 6.5 25187.6 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 26 | Hazardous Waste Management | Disposal | Quarantined HW not removed, transferred, or disposed without permission by authorized agent | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 1 | Yes |  | 14 30 | Failure to obtain permission from an authorized agent or court to remove, transfer, or dispose of hazardous waste that is under quarantined. |  |  | OBSERVATION: Quarantined HW was removed, transferred, or disposed of without permission by authorized agent. CORRECTIVE ACTION: Submit a statement to the CUPA demonstrating that you have read the quarantine notice and trained all applicable employees on the requirements. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130004 |  | 262.C | RCRA: Hazardous Waste Accumulation Time Exceeded | Failure to send hazardous waste offsite for treatment, storage, or disposal within 90 days for a generator who generates 1000 kilograms or more of RCRA hazardous waste or one kilogram of acute hazardous waste per month. | 22 CCR 12 66262.34(a) (c); HSC 6.5 25123.3(b)(1) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 27 | Hazardous Waste Management | Accumulation Time Limits | Disposed of hazardous waste within 90 days of accumulation start date | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to send hazardous waste offsite for treatment, storage, or disposal within 90 days for a generator who generates 1000 kilograms or more of RCRA hazardous waste or one kilogram of acute hazardous waste per month. |  |  | OBSERVATION: Owner/Operator failed to send hazardous waste offsite for treatment, storage, or disposal within 90 days of accumulation start date. CORRECTIVE ACTION: Dispose of hazardous waste and submit a copy of the manifest/receipt to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130023 |  | 262.C | RCRA: Hazardous Waste Generator: Satellite Accumulation | Failure to meet the following conditions of satellite accumulation regulations: • Accumulate up to 55 gallons of hazardous waste or one quart of acute hazardous waste at or near the initial point of accumulation which was under the control of the operator. • Total time hazardous waste can be accumulated onsite in any generator accumulation area is either one year from the initial date of accumulation, or 90 days from the date on which the quantity limitation of 55 gallons of hazardous waste or one quart of acutely hazardous waste is reached, whichever comes first. • The generator complies with sections 66265.171, 66264.172, and 66265.173(a). • The container must be clearly marked with the initial date that hazardous waste is first placed in the container and labelled with the words “Hazardous Waste” including specified information. • Container must be labelled with the date the satellite accumulation limit is reached and moved within three days after reaching the 55 gallon (or one quart) limit to a central accumulation area. • 55 gallons (or one quart of acute hazardous waste) of waste per process may be accumulated. | 22 CCR 12 66262.34(e) | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 28 | Hazardous Waste Management | Accumulation Time Limits | Met all requirements for hazardous waste satellite accumulation | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to meet the following conditions of satellite accumulation regulations: • Accumulate up to 55 gallons of hazardous waste or one quart of acute hazardous waste at or near the initial point of accumulation which was under the control of the operator. • Total time hazardous waste can be accumulated onsite in any generator accumulation area is either one year from the initial date of accumulation, or 90 days from the date on which the quantity limitation of 55 gallons of hazardous waste or one quart of acutely hazardous waste is reached, whichever comes first. • The generator complies with sections 66265.171, 66264.172, and 66265.173(a). • The container must be clearly marked with the initial date that hazardous waste is first placed in the container and labelled with the words “Hazardous Waste” including specified information. • Container must be labelled with the date the satellite accumulation limit is reached and moved within three days after reaching the 55 gallon (or one quart) limit to a central accumulation area. • 55 gallons (or one quart of acute hazardous waste) of waste per process may be accumulated. |  |  | OBSERVATION: Failure of the Owner/Operator to comply with one or more satellite accumulation requirements [Describe as needed]. CORRECTIVE ACTION: Ensure that all hazardous wastes being accumulated pursuant to satellite accumulation meet all applicable requirements and submit documentation of compliance to the CUPA. {Describe specific corrections as needed} | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130003 |  | 262.C | RCRA: Hazardous Waste Labeling Standards | Failure to properly label hazardous waste accumulation containers with the following requirements: "Hazardous Waste", name and address of the generator, physical and chemical characteristics of the Hazardous Waste, and starting accumulation date. | 22 CCR 12 66262.34(f) | 2011-07-01 | 2099-12-31 | 2012-04-24 13:48 | Existing | 29 | Hazardous Waste Management | Container Management | Labeled all containers or portable tanks containing hazardous waste | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly label hazardous waste accumulation containers with the following requirements: "Hazardous Waste", name and address of the generator, physical and chemical characteristics of the Hazardous Waste, and starting accumulation date. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed without a hazardous waste label. CORRECTIVE ACTION: Submit a photo to the CUPA demonstrating that the container listed above has been properly labeled. | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed without the following information on the label: [LIST MISSING INFORMATION]. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that the container listed above has been properly labeled. | [5 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130005 |  | 262.C | RCRA: Container in Poor Condition or Damaged | Failure to accumulate hazardous waste in a container that is in good condition. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.171 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 30 | Hazardous Waste Management | Container Management | Accumulated hazardous waste in containers that are in good condition | 68 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to accumulate hazardous waste in a container that is in good condition. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed [DESCRIBE CONDITION]. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is in good condition or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130006 |  | 262.C | RCRA: Hazardous Waste Container Incompatible with Material Stored | Failure to accumulate or store hazardous waste in a container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored, so that the ability of the container to contain the waste is not impaired. | 22 CCR 12 66262.34(a); 22 CCR 15 66265.172 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 31 | Hazardous Waste Management | Container Management | Hazardous waste accumulated in lined and/or compatible containers | 65 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to accumulate or store hazardous waste in a container made of or lined with materials which will not react with, and are otherwise compatible with, the hazardous waste to be stored, so that the ability of the container to contain the waste is not impaired. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed in an [UNLINED / INCOMPATIBLE] container. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating the waste listed above has been transferred into a container that is compatible with the hazardous waste or submit a manifest/receipt demonstrating the waste has been properly disposed of by a registered hazardous waste transporter. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130007 |  | 262.C | RCRA: Open Hazardous Waste Container | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.173 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 32 | Hazardous Waste Management | Container Management | Containers of hazardous waste closed except when adding or removing waste | 73 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the following container management requirements: (a) A container holding hazardous waste must always be closed during storage, except when it is necessary to add or remove waste. (b) A container holding hazardous waste must not be opened, handled, or stored in a manner which may rupture the container or cause it to leak. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed open. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that the container listed above has been properly closed. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130008 |  | 262.C | RCRA: Weekly Hazardous Waste Storage Areas Inspection | Failure to inspect weekly areas where hazardous waste containers are stored. The owner or operator must look for leaking containers and for deterioration of containers caused by corrosion or other factors. | 22 CCR 12 66262.34(a); 22 CCR 15 66265.174 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 33 | Hazardous Waste Management | Container Management | Inspects all hazardous waste containers at least weekly | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to inspect weekly areas where hazardous waste containers are stored. The owner or operator must look for leaking containers and for deterioration of containers caused by corrosion or other factors. |  |  | OBSERVATION: [DESCRIBE CONTAINER] of [HAZARDOUS WASTE] located in the [LOCATION] was observed [LEAKING / DETERIORATING]. CORRECTIVE ACTION: Submit a copy of the inspection log to the CUPA demonstrating that the hazardous waste storage area is being inspected weekly. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130009 |  | 262.C | RCRA: Reactive and Ignitable Waste 50 ft from Property Line | Failure to keep reactive and ignitable waste at least 15 meters (50 feet) from the facility's property line. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.176 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 34 | Hazardous Waste Management | Container Management | Reactive and ignitable waste containers located at least 50 ft from property line | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to keep reactive and ignitable waste at least 15 meters (50 feet) from the facility's property line. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [HAZARDOUS WASTES] located in the [LOCATION] were observed closer than 50 feet from the property line. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that all containers holding ignitable or reactive waste are stored at least 50 feet from the property line. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130010 |  | 262.C | RCRA: Incompatible Waste Storage | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.17(b), 66265.177 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 35 | Hazardous Waste Management | Container Management | Incompatible waste in containers managed properly to prevent a reaction | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to separate incompatible wastes from the same container, nearby containers, or unwashed containers which previously contained incompatible waste or materials. |  |  | OBSERVATION: [DESCRIBE CONTAINERS] of [LIST HAZARDOUS WASTES] located in the [LOCATION] are not compatible and were observed stored in a manner that could result a reaction. CORRECTIVE ACTION: Transfer or separate the containers of incompatible wastes noted above to other compatible containers or by separating containers to prevent a reaction and submit photos to the CUPA demonstrating compliance. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130025 |  | 262.C | RCRA: Air Emissions for Waste in Containers | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.178 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 36 | Hazardous Waste Management | Container Management | Complied with air emission requirements for HW in containers | 60 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. |  |  | OBSERVATION: The facility Owner/Operator failed to meet air emission requirements for hazardous waste containers as observed by [ENTER SPECIFIC OBSERVATIONS]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the air emission requirements specified in articles 27, 28, and 28.5 of chapter 15 have been met. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130024 |  | 262.C | RCRA: Hazardous Waste Generator: Empty Containers >5 Gallons | Failure to manage empty containers greater than 5 gallons in capacity that previously held a hazardous material/waste including but not limited to the following: (1) By reclaiming its scrap value onsite or shipping the container or inner liner to a person who reclaims its scrap value; or (2) By reconditioning or remanufacturing the container or inner liner onsite for subsequent reuse, or shipping the container or inner liner to a person who reconditions or remanufactures the container or inner liner; or (3) By shipping the container or inner liner to a supplier or to another intermediate collection location for accumulation prior to managing the container or inner liner pursuant to subsections (e)(2) or (e)(3) of 22 CCR 11 66261.7; or (4) By shipping the container or inner liner back to the supplier for the purpose of being refilled; and (5) A container or an inner liner removed from a container shall be marked with the date it has been emptied and shall be managed within one year of being emptied. | 22 CCR 11 66261.7 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 37 | Hazardous Waste Management | Container Management | Empty containers > 5 gallons properly managed | 45 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to manage empty containers greater than 5 gallons in capacity that previously held a hazardous material/waste including but not limited to the following: (1) By reclaiming its scrap value onsite or shipping the container or inner liner to a person who reclaims its scrap value; or (2) By reconditioning or remanufacturing the container or inner liner onsite for subsequent reuse, or shipping the container or inner liner to a person who reconditions or remanufactures the container or inner liner; or (3) By shipping the container or inner liner to a supplier or to another intermediate collection location for accumulation prior to managing the container or inner liner pursuant to subsections (e)(2) or (e)(3) of 22 CCR 11 66261.7; or (4) By shipping the container or inner liner back to the supplier for the purpose of being refilled; and (5) A container or an inner liner removed from a container shall be marked with the date it has been emptied and shall be managed within one year of being emptied. |  |  | OBSERVATION: Owner/Operator failed to properly manage empty containers greater than 5 gallons in capacity that previously held a hazardous material/waste. {describe specific violation as needed} CORRECTIVE ACTION: Submit photos/documentation to the UPA demonstrating that the empty containers have been marked with the date they were emptied and are being properly managed pursuant to 22 CCR 11 66261.7. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130022 |  | 262.C | RCRA: Hazardous Waste Generator: Hazardous Waste Tank Label | Failure to label stationary hazardous waste tanks as "hazardous waste" and mark with an accumulation start date. | 22 CCR 12 66262.34(f) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 38 | Hazardous Waste Management | Tank Management | Stationary tanks marked as "Hazardous Waste" and marked with accumulation start date | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to label stationary hazardous waste tanks as "hazardous waste" and mark with an accumulation start date. |  |  | OBSERVATION: The [HAZARDOUS WASTE] tank was observed without a label. CORRECTIVE ACTION: Submit a photo to the CUPA demonstrating that the [HAZARDOUS WASTE] tank has been properly labeled. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110013 |  | 262.C | RCRA: New Hazardous Waste Tank System P.E. Certification | Failure to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service. The written assessment shall state that, the new hazardous waste tank system has sufficient structural integrity, is acceptable for the transferring, storing and treating of hazardous waste, and that the tanks and containment system including the foundation, structural support, seams, connections, and pressure controls (if applicable) are suitably designed to meet the regulation. | 22 CCR 15 66265.192(a) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 39 | Hazardous Waste Management | Tank Management | Written hazardous waste tank system assessment by P.E. completed | 64 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to obtain and maintain a written assessment reviewed and certified by an independent, qualified, professional engineer prior to placing the tank system in service. The written assessment shall state that, the new hazardous waste tank system has sufficient structural integrity, is acceptable for the transferring, storing and treating of hazardous waste, and that the tanks and containment system including the foundation, structural support, seams, connections, and pressure controls (if applicable) are suitably designed to meet the regulation. |  |  | OBSERVATION: A written hazardous waste tank assessment has not been obtained for the [HAZARDOUS WASTE] tank system. CORRECTIVE ACTION: Obtain a written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192 and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110014 |  | 262.C | RCRA: New Tank Assessment Standards | Failure to include all required information in the new tank system assessment. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.192(k) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 40 | Hazardous Waste Management | Tank Management | Written hazardous waste tank system assessment meets all requirements | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to include all required information in the new tank system assessment. |  |  | OBSERVATION: The written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system did not include the following: [LIST] CORRECTIVE ACTION: Revise the written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192(k) and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110023 |  |  | Reassessment for Hazardous Waste Tank System P.E. Certification | Failure of generator to obtain assessment or reassessment every five (5) years or the remaining service life of the tank system, as stated in the engineer's assessment, whichever is less. This assessment applies to onground or aboveground tank systems containing only non-RCRA hazardous wastes generated onsite, or for a small quantity generator onground or aboveground tank systems containing RCRA hazardous wastes generated onsite. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.192(h) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 41 | Hazardous Waste Management | Tank Management | Written hazardous waste tank system assessment/reassessment by P.E. completed | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of generator to obtain assessment or reassessment every five (5) years or the remaining service life of the tank system, as stated in the engineer's assessment, whichever is less. This assessment applies to onground or aboveground tank systems containing only non-RCRA hazardous wastes generated onsite, or for a small quantity generator onground or aboveground tank systems containing RCRA hazardous wastes generated onsite. |  |  | OBSERVATION: A hazardous waste tank reassessment has not been conducted for the [HAZARDOUS WASTE] tank system within 5 years of the previous tank system assessment or within the remaining service life of the tank system as stated in the engineer's report, whichever is less. CORRECTIVE ACTION: Obtain a written hazardous waste tank system reassessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192 and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130011 |  | 262.C | RCRA: Hazardous Waste Tank Standards | Failure to comply with general tank operating requirements: (a) Hazardous wastes or treatment reagents shall not be placed in a tank system if they could cause the tank , its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail. (b) The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: (1) spill prevention controls (e.g., check valves, dry discount couplings); (2) overfill prevention controls (e.g., level sensing devises, high level alarms, automatic feed cutoff, or bypass to a standby tank); and (3) maintenance of sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.194 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 42 | Hazardous Waste Management | Tank Management | Tanks are compatible with hazardous waste and have spill/overflow prevention provided | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to comply with general tank operating requirements: (a) Hazardous wastes or treatment reagents shall not be placed in a tank system if they could cause the tank , its ancillary equipment, or the secondary containment system to rupture, leak, corrode, or otherwise fail. (b) The owner or operator shall use appropriate controls and practices to prevent spills and overflows from tank or secondary containment systems. These include at a minimum: (1) spill prevention controls (e.g., check valves, dry discount couplings); (2) overfill prevention controls (e.g., level sensing devises, high level alarms, automatic feed cutoff, or bypass to a standby tank); and (3) maintenance of sufficient freeboard in uncovered tanks to prevent overtopping by wave or wind action or by precipitation. Uncovered tanks shall be operated to ensure at least 60 centimeters (2 feet) of freeboard, unless the tank is equipped with a containment structure (e.g., dike or trench), a drainage control system or a diversion structure (e.g., standby tank) with a capacity that equals or exceeds the volume of the top 60 centimeters (2 feet) of the tank. |  |  | OBSERVATION: Appropriate controls and practices are not in place to prevent spills and overflows from the [HAZARDOUS WASTE] tank or secondary containment system. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank or secondary containment system meets all requirements identified above. | OBSERVATION: The [HAZARDOUS WASTE] tank system is not compatible with [HAZARDOUS WASTE] observed accumulating in the tank system. Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] has been removed from the tanks system and has been placed in compatible containers/tanks. | [5 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130019 |  | 262.C | RCRA: Secondary Containment | Failure to meet required secondary containment requirements for hazardous waste tank systems or components. | 22 CCR 15 66265.193 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 43 | Hazardous Waste Management | Tank Management | Secondary containment provided and meets requirements for all hazardous waste tank systems | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to meet required secondary containment requirements for hazardous waste tank systems or components. |  |  | OBSERVATION: Secondary containment is not provided for the [HAZARDOUS WASTE] tank system. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating that secondary containment has been provided for the [HAZARDOUS WASTE] tank system and is in accordance with the requirements of 22 CCR 15 66265.193. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130012 |  | 262.C | RCRA: Hazardous Waste Tank Inspections | Failure to conduct and document inspections of hazardous waste tank systems each operating day and retain records of those inspections at the facility. | 22 CCR 12 66262.34 (a)(1); 22 CCR 15 66265.195(a), 66265.195(c) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 44 | Hazardous Waste Management | Tank Management | Conducts/documents daily inspections of hazardous waste tank system | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to conduct and document inspections of hazardous waste tank systems each operating day and retain records of those inspections at the facility. |  |  | OBSERVATION: Daily inspections of the [HAZARDOUS WASTE] tank system have not been conducted and documented. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank system is being properly inspected and documented. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130020 |  | 262.C | RCRA: Hazardous Waste Tank Cathodic Inspection | Failure of the owner or operator to inspect and document the cathodic protection systems to ensure the proper operation within six months after initial installation, and annually thereafter; and all sources of impressed current at least bimonthly (i.e., every other month). | 22 CCR 12 66262.34(a); 22 CCR 15 66265.195(b), 66265.195(c) | 2022-07-01 | 2099-12-31 | 2022-07-01 | Revised | 45 | Hazardous Waste Management | Tank Management | Inspect/document the HW tank system cathodic protection system annually/impressed current bimonthly | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of the owner or operator to inspect and document the cathodic protection systems to ensure the proper operation within six months after initial installation, and annually thereafter; and all sources of impressed current at least bimonthly (i.e., every other month). |  |  | OBSERVATION: Annual cathodic protection and bimonthly impressed current inspections of the [HAZARDOUS WASTE] tank system have not been conducted and documented. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the [HAZARDOUS WASTE] tank system has been inspected for cathodic protection and all sources of impressed current. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110015 |  | 262.C | RCRA: Hazardous Waste Tank Equipment Replacement | Failure to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). The notification to the CUPA of replacement shall include the following: (1) Name, address, and EPA identification number of the facility; (2) Date of planned replacement; (3) Description part or component to be replaced; (4) Description of the tank system and type of waste(s) handled; (5) Description of how the part or component is identical or functionally equivalent to the part or component to be replaced. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.192(m) | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 46 | Hazardous Waste Management | Tank Management | Obtained approval before replacement of identical/equivalent tank system parts not in 66265.192(l) | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain CUPA approval prior to the replacement of identical or functionally equivalent tank system parts or components not listed in CCR 66265.192(l). The notification to the CUPA of replacement shall include the following: (1) Name, address, and EPA identification number of the facility; (2) Date of planned replacement; (3) Description part or component to be replaced; (4) Description of the tank system and type of waste(s) handled; (5) Description of how the part or component is identical or functionally equivalent to the part or component to be replaced. |  |  | OBSERVATION: Replacement of [TANK SYSTEM PARTS] for the [HAZARDOUS WASTE] tank system were made on [DATE]. The written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system has not been updated and the generator did not contact the CUPA to determine if the tank system parts/components were identical or functionally equivalent. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating the [TANK SYSTEM PARTS] are identical or functionally equivalent or revise the written hazardous waste tank system assessment for the [HAZARDOUS WASTE] tank system in accordance with 22 CCR 15 66265.192(k) and submit a copy to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Release/Leaks/Spills | 3140001 |  | 262.C | RCRA: Hazardous Waste Tank Release | Failure to immediately remove from service a tank system or secondary containment system from which there has been a leak, spill, is unfit for use and comply with applicable requirements. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.196 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 47 | Hazardous Waste Management | Tank Management | Leaking/unfit HW tank or secondary containment removed from service | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to immediately remove from service a tank system or secondary containment system from which there has been a leak, spill, is unfit for use and comply with applicable requirements. |  |  | OBSERVATION: The [HAZARDOUS WASTE] tank system was observed leaking to [LOCATION] and is unfit for use. CORRECTIVE ACTION: Immediately remove the [HAZARDOUS WASTE] tanks system from service. Submit documentation to the CUPA demonstrating that all requirements in 22 CCR 15 66265.196 have been met. | [6 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150002 |  | 262.A | RCRA: Tank Closure Requirements and Documentation | Failure of owner or operator to properly close a hazardous waste tank system ensuring the minimization of further maintenance and that the required requirements have been met. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.111, 66265.114, 66265.197 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 48 | Hazardous Waste Management | Tank Management | Met all hazardous waste tank system closure requirements | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of owner or operator to properly close a hazardous waste tank system ensuring the minimization of further maintenance and that the required requirements have been met. |  |  | OBSERVATION: The [HAZARDOUS WASTE] tank system has not been properly closed. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the [HAZARDOUS WASTE] tank system has been closed in accordance with the requirements of 22 CCR 15 66265.197. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130026 |  | 262.C | RCRA: Air Emissions for wastes in Tanks | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. | 22 CCR 12 66262.34(a)(1); 22 CCR 15 66265.202 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Existing | 49 | Hazardous Waste Management | Tank Management | Complied with air emissions requirements for HW in tanks | 56 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with air emission requirements as specified in articles 27, 28, and 28.5 of chapter 15. |  |  | OBSERVATION: The facility Owner/Operator failed to meet the air emission requirements for hazardous waste tanks as observed by [ENTER SPECIFIC OBSERVATIONS]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the air emission requirements specified in articles 27, 28, and 28.5 of chapter 15 have been met. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130027 |  | 262.C | RCRA: Drip Pad requirements | Failure to comply with Drip Pad requirements, including but not limited to design and operating requirements, annual assessment, contingency plan, inspections, and closure requirements. | 22 CCR 12 66262.34 (a)(1)(B); 22 CCR 15 66265.440 - 66265.445 | 2017-11-01 | 2099-12-31 | 2017-11-01 | Existing | 50 | Hazardous Waste Management | Drip Pad | In compliance with drip pad requirements | 41 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to comply with Drip Pad requirements, including but not limited to design and operating requirements, annual assessment, contingency plan, inspections, and closure requirements. |  |  | OBSERVATION: Owner/Operator failed to comply with drip pad requirements including but not limited to design and operating requirements, annual assessment, contingency plan, inspections and closure requirements (Article 17.5 of Chapter 15). CORRECTIVE ACTION: Ensure compliance with all drip pad requirements including, but not limited to, design and operating requirements, annual assessment, contingency plan, inspections and closure requirements (Article 17.5 of Chapter 15) . | [6 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150004 |  |  | Recyclable Materials | Failure to properly manage a recyclable material. | HSC 6.5 25143.2, 25143.9 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 51 | Hazardous Waste Management | Recyclable Materials | Recyclable material is managed properly | 39 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to properly manage a recyclable material. |  |  | OBSERVATION: Owner/Operator failed to properly manage a recyclable material {Describe observed issues}. CORRECTIVE ACTION: Submit documentation demonstrating compliance with the requirements of HSC 6.5 25143.2 for any material you claim qualifies as an excluded recyclable material, or indicate that this material is to be managed as a hazardous waste. | [6 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150005 |  |  | Contamination of Used Oil | Failure to prevent intentional contamination of used oil with other hazardous waste other than minimal amounts of vehicle fuel. | HSC 6.5 25250.7(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 52 | Hazardous Waste Management | Used Oil | Generator does not intentionally contaminate used oil with other hazardous wastes | 81 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to prevent intentional contamination of used oil with other hazardous waste other than minimal amounts of vehicle fuel. |  |  | OBSERVATION: Generator failed to prevent intentional contamination of used oil with other hazardous waste other than minimal amounts of vehicle fuel. CORRECTIVE ACTION: Submit a statement to the CUPA demonstrating how you will prevent contamination of used oil with other hazardous wastes. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130029 |  |  | Used Oil Filter and Fuel Filter Handling Requirements | Failure to properly manage used oil filters and/or fuel filters in accordance with the requirements. | 22 CCR 16 66266.130; HSC 6.5 25250.22 | 2020-10-01 | 2099-12-31 | 2020-10-01 | Existing | 53 | Hazardous Waste Management | Used Oil and Fuel Filters | Properly manages used oil filters and fuel filters | 50 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly manage used oil filters and/or fuel filters in accordance with the requirements. |  |  | OBSERVATION: Used oil and/or fuel filters were observed [DESCRIBE: WITHOUT LIDS, WITHOUT A LABEL, WITHOUT AN ACCUMULATION START DATE / WITH AN ACCUMULATED START DATE OF (DATE)]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the used oil and/or fuel filters are being properly managed or submit a bill of lading to this department demonstrating proper disposal. | OBSERVATION: Bills of lading for used oil and fuel filters were not available at the time of inspection. CORRECTIVE ACTION: Obtain copies of all bills of lading for used oil and fuel filters for the past three years and submit copies to the CUPA. | [5 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130030 |  |  | Management of Spent Vehicle Lead-Acid Batteries | Failure to meet the spent lead acid battery management requirements, when handling, storing, or transporting more than 10 lead acid batteries at any one time. | 22 CCR 16 66266.81(a)(1) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 54 | Hazardous Waste Management | Lead Acid Batteries | Meets requirements for handling/storing/transporting lead acid batteries | 72 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet the spent lead acid battery management requirements, when handling, storing, or transporting more than 10 lead acid batteries at any one time. |  |  | OBSERVATION: Generator failed to meet the spent lead acid battery management requirements, when handling, storing, or transporting more than 10 lead acid batteries at any one time. CORRECTIVE ACTION: Owner/Operator shall immediately begin to handle, store, and/or transport lead acid batteries in accordance with Title 22 regulations. | OBSERVATION: Bills of lading for spent lead acid batteries recording the shipments off site were not retained at the facility for the past three years. CORRECTIVE ACTION: Obtain copies of all bills of lading for lead-acid batteries over the past three years and submit copies to the CUPA. | [5 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130031 |  |  | Management of 11 or More Spent Vehicle Lead-Acid Batteries | Failure of facilities that accept spent lead acid batteries in exchange or partial exchange for operable lead-acid storage batteries to comply with storage requirements by violating one of the following: 1) Storing more than one ton of spent batteries at any one location for more than 180 days. 2) Storing one ton or less of spent batteries at any one location for more than one year, or 3) Removing the electrolyte. | 22 CCR 16 66266.81(a)(3) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 55 | Hazardous Waste Management | Lead Acid Batteries | Meets all requirements when accepting spent lead-acid batteries | 63 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of facilities that accept spent lead acid batteries in exchange or partial exchange for operable lead-acid storage batteries to comply with storage requirements by violating one of the following: 1) Storing more than one ton of spent batteries at any one location for more than 180 days. 2) Storing one ton or less of spent batteries at any one location for more than one year, or 3) Removing the electrolyte. |  |  | OBSERVATION: The generator accepts lead acid batteries and was observed storing [MORE THAN ONE TON/LESS THAN ONE TON] of spent lead acid batteries for greater than [180 DAYS/1 YEAR], and/or removing electrolyte. CORRECTIVE ACTION: Submit a bill of lading or manifest to the CUPA demonstrating that the spent lead acid batteries have been properly managed or disposed of. Discontinue practice of removing electrolyte if applicable. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130032 |  |  | Damaged Lead Battery Handling | Failure to properly manage, store, and label a damaged lead acid battery in a nonreactive, structurally secure, closed container, and/or failure to label damaged lead acid battery with the date that the first battery in the container was placed there with ink, paint or other weather-resistant material so as to minimize the release of acid and lead and to protect the environment. | 22 CCR 16 66266.81(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 56 | Hazardous Waste Management | Lead Acid Batteries | Properly manages, stores and labels all damaged lead-acid batteries | 67 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to properly manage, store, and label a damaged lead acid battery in a nonreactive, structurally secure, closed container, and/or failure to label damaged lead acid battery with the date that the first battery in the container was placed there with ink, paint or other weather-resistant material so as to minimize the release of acid and lead and to protect the environment. |  |  | OBSERVATION: Damage lead acid batteries were observed in the [LOCATION] and were not [LABELED WITH AN ACCUMULATION START DATE, IN A CLOSED, COMPATIBLE CONTAINER] CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the damaged battery has been properly managed. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110024 |  |  | Certified Appliance Recyclers: Certification | Failure to obtain Certified Appliance Recycler certification (CAR) from DTSC. | HSC 6.5 25211.4 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 57 | Hazardous Waste Management | Certified Appliance Recyclers | Obtained Certified Appliance Recycler certification (CAR) from the DTSC | 71 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to obtain Certified Appliance Recycler certification (CAR) from DTSC. |  |  | OBSERVATION: Owner/Operator is removing materials that require special handling from appliances and does not have a Certified Appliance Recycler Certification from the DTSC. CORRECTIVE ACTION: Discontinue removing materials requiring special handling from appliances until you have obtained a Certified Appliance Recycler certification from DTSC. Provide copy of Certification when received from DTSC. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130033 |  |  | Certified Appliance Recyclers: MRSH properly managed | Failure of certified appliance recycler (CAR) to properly remove and dispose of all materials that require special handling (MRSH). | HSC 6.5 25212 | 2021-08-02 | 2099-12-31 | 2021-08-02 | Existing | 58 | Hazardous Waste Management | Certified Appliance Recyclers | CAR properly managed all MSRH as hazardous waste | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of certified appliance recycler (CAR) to properly remove and dispose of all materials that require special handling (MRSH). |  |  | OBSERVATION: The CAR has failed to properly remove and dispose of materials requiring special handling (MRSH) removed from appliances. CORRECTIVE ACTION: Immediately begin proper removal and disposal of all MRSH as hazardous waste. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110025 |  |  | Certified Appliance Recyclers: Documentation | Failure of certified appliance recycler (CAR) to provide documentation that all materials that require special handling (MRSH) have been properly removed and managed. | HSC 6.5 25211.2, 25211.3 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 59 | Hazardous Waste Management | Certified Appliance Recyclers | CAR maintains documentation regarding removal and management of MRSH from appliances | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of certified appliance recycler (CAR) to provide documentation that all materials that require special handling (MRSH) have been properly removed and managed. |  |  | OBSERVATION: Certified Appliance Recycler (CAR) failed to maintain required documentation demonstrating that all materials requiring special handling (MRSH) have been removed from appliances and properly managed. CORRECTIVE ACTION: Facility must comply with all requirements of sections 25211-25212 of the California Health & Safety Code, including, but not limited to, maintaining copies of all documentation required related to the removal and management of MRSH from appliances processed by the CAR. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130034 |  |  | Reusable soiled textile materials | Failure to properly manage reusable soiled textile materials prior to being sent for laundering. | HSC 6.5 25144.6 (b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 60 | Hazardous Waste Management | Reusable Soiled Textiles | Properly managed reusable soiled textile materials prior to being sent for laundering | 85 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to meet all of the following requirements for reusable soiled textile materials: (1) The materials or the management of the materials are not otherwise regulated by the Environmental Protection Agency pursuant to the federal act. (2) The materials are not used to clean up or control a spill or release that is required to be reported to any state or federal agency. (3) No hazardous waste has been added after the materials’ original use. (4) No free liquids, as defined by Section 22-66260.10 of Title 26 of the California Code of Regulations, are released during transportation or storage of the materials. (5) The facility laundering or cleaning the materials maintains records of the date, type, and quantities by piecework or weight of the materials collected and laundered. (6) The facility laundering or cleaning the materials prepares a contingency plan which specifies procedures for handling both onsite and offsite emergencies involving the materials, and employees are trained in the execution of the plan. |  |  | OBSERVATION: Reusable soiled textiles being managed on site were observed [ENTER APPLICABLE REGULATORY REQUIREMENTS IN 25144.6(b)]. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you are properly managing reusable soiled textiles in accordance with HSC 25144.6(b). | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130035 |  |  | Laboratory Accumulation Area | Failure of the owner or operator managing laboratory hazardous waste in a laboratory accumulation area to comply with the quantity limitations, management, training, or documentation requirements. | HSC 6.5 25200.3.1(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 61 | Hazardous Waste Management | Laboratory Waste | Laboratory waste managed in accordance with HSC 25200.3.1(b) | 60 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the owner or operator managing laboratory hazardous waste in a laboratory accumulation area to comply with the quantity limitations, management, training, or documentation requirements, in accordance with the HSC 25200.3.1(b). |  |  | OBSERVATION: Laboratory hazardous waste was observed being accumulated not in accordance with requirements 25200.3.1(b). CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the laboratory waste is being managed in accordance with HSC 25200.3.1(b). | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130036 |  |  | Laboratory Waste Treatment | Failure to treat laboratory hazardous waste according to all of the following requirements: 1) treated in containers and follow published procedures, 2) at a location as close as practical, and within 10 days, 3) single batch quantity limit to be 5 gallons or 18 kilograms, whichever is greater, 4) waste from a single procedure or from the same laboratory process, 5) performed by trained personnel, 6) training records are maintained for 3 years, 7) waste and residuals are managed according to applicable requirements, and 8) records are made available for inspection. | HSC 6.5 25200.3.1 (c) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Existing | 62 | Hazardous Waste Management | Laboratory Waste | Laboratory waste treated in accordance with HSC 25200.3.1(c) | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to treat laboratory hazardous waste according to all of the following requirements: 1) treated in containers and follow published procedures, 2) at a location as close as practical, and within 10 days, 3) single batch quantity limit to be 5 gallons or 18 kilograms, whichever is greater, 4) waste from a single procedure or from the same laboratory process, 5) performed by trained personnel, 6) training records are maintained for 3 years, 7) waste and residuals are managed according to applicable requirements, and 8) records are made available for inspection. |  |  | OBSERVATION: Laboratory hazardous waste was observed being treated not in accordance with the requirements of 25200.3.1(c). CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that the laboratory waste is being treated in accordance with HSC 25200.3.1(c). | [6 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150007 |  |  | RCRA: Unauthorized Treatment | Failure to obtain a hazardous waste facilities permit, or other grant authorization, prior to accepting, treating, storing, or disposing of a hazardous waste at the facility, area, or site. | HSC 6.5 25201(a) | 2023-07-01 | 2099-12-31 | 2023-07-01 | New | 63 | Hazardous Waste Management | Unauthorized Treatment | Obtained a HW facilities permit or grant of authorization prior to treating hazardous waste | 91 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to obtain a hazardous waste facilities permit, or other grant authorization, prior to accepting, treating, storing, or disposing of a hazardous waste at the facility, area, or site. |  |  | OBSERVATION: Owner/Operator failed to obtain a hazardous waste facilities permit or other grant authorization prior to accepting, treating, storing, or disposing of a hazardous waste at the facility, area, or site. CORRECTIVE ACTION: Complete required reporting needed to obtain a hazardous waste facilities permit or other grant of authorization to treat hazardous waste. Discontinue treating hazardous waste until permit or grant of authorization is approved. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130037 |  | 262.C | Emergency Coordinator | Failure to have at least one employee either on the facility premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.55 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 63 64 | General Facility Operations | Site Safety | Emergency coordinator on the premises or on call | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to have at least one employee either on the facility premises or on call (i.e., available to respond to an emergency by reaching the facility within a short period of time) with the responsibility for coordinating all emergency response measures. |  |  | OBSERVATION: An emergency coordinator was not on the premises or available on call. CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that at least one employee is either on the premises or on call with the responsibility for coordinating all emergency response measures. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130014 |  | 262.C | RCRA: Facility Emergency Equipment | Failure to equip the facility with required emergency equipment, unless none of the hazards posed by waste handled at the facility could require the particular kind of required equipment. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.32 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 64 65 | General Facility Operations | Site Safety | Facility equipped with all required emergency equipment | 55 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to equip the facility with required emergency equipment, unless none of the hazards posed by waste handled at the facility could require the particular kind of required equipment. |  |  | OBSERVATION: The facility has not been equip with [LIST EQUIPMENT]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the facility has been equip with [LIST EQUIPMENT]. to the CUPA within [# days]. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130015 |  | 262.C | RCRA: Emergency Equipment Maintenance | Failure of the facility to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.33 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 65 66 | General Facility Operations | Site Safety | Tests and maintains all required safety equipment at the facility | 66 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of the facility to test and maintain as necessary all facility communications or alarm systems, fire protection equipment, spill control equipment, and decontamination equipment to assure its proper operation in time of emergency. |  |  | OBSERVATION: [LIST EQUIPMENT] has not been tested and maintained to assure its proper operation in time of emergency. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating [LIST EQUIPMENT] has been properly tested or maintained. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130016 |  | 262.C | RCRA: Aisle Space | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless aisle space is not needed for any of these purposes. | 22 CCR 15 66265.35 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 66 67 | General Facility Operations | Site Safety | Maintains adequate aisle space | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to maintain aisle space to allow the unobstructed movement of personnel, fire protection equipment, spill control equipment, and decontamination equipment to any area of facility operation in an emergency, unless aisle space is not needed for any of these purposes. |  |  | OBSERVATION: The hazardous waste storage area located in the [LOCATION] did not have adequate aisle space allowing for unobstructed movement. CORRECTIVE ACTION: Submit photos to the CUPA demonstrating that adequate aisle space has been provided. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130013 |  | 262.C | RCRA: Facility Maintained to Prevent Fire/Explosion/Release | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. | 22 CCR 12 66262.34(a)(4); 22 CCR 15 66265.31 | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 67 68 | General Facility Operations | Site Safety | Maintains and operates the facility to minimize the possibility of fire/explosion/release | 89 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to maintain and operate the facility to minimize the possibility of a fire, explosion, or any unplanned sudden or non-sudden release of hazardous waste or hazardous waste constituents to air, soil, or surface water which could threaten human health or the environment. |  |  | OBSERVATION: [HAZARDOUS WASTE] was observed [DESCRIBE SPILL] in the [LOCATION]. CORRECTIVE ACTION: Submit photos/documentation to the CUPA demonstrating the spill has been properly removed and managed. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110026 |  |  | Universal Waste Handler: USEPA Notification | Failure of a universal waste handler to send written notification of universal waste management to the USEPA Regional Administrator and obtain a federal ID Number prior to accumulating 5,000 kilograms or more of RCRA universal waste. | 22 CCR 23 66273.32(a) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 68 69 | Universal Waste | >5000 Kg | UWH notified the EPA and obtained a federal ID number prior to storing 5,000 kg or more of RCRA UW | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of a universal waste handler to send written notification of universal waste management to the USEPA Regional Administrator and obtain a federal ID Number prior to accumulating 5,000 kilograms or more of RCRA universal waste. |  |  | OBSERVATION: The universal waste handler failed to notify the USEPA and/or obtain a federal ID number prior to storing 5,000 kg or more of RCRA universal waste. [enter specific observations] CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that you have notified the federal USEPA and obtained a federal EPA ID number. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110027 |  |  | Universal Waste Handler: Department Notification | Failure of a universal waste handler of PV modules, electronic devices, CRTs, and/or CRT glass who might accept and accumulate, but not treat, any PV module, electronic device, CRT, and/or CRT glass from an offsite source to submit notification with all required information to DTSC no later than 30 calendar days prior to accepting any above noted waste. | 22 CCR 23 66273.32(c), (e) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 69 70 | Universal Waste | Electronic Devices/CRT/PV Modules | UWH of PV modules/e-devices/CRTs/CRT glass that doesn't treat waste submitted required info to DTSC | 99 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a universal waste handler of PV modules, electronic devices, CRTs, and/or CRT glass who might accept and accumulate, but not treat, any PV module, electronic device, CRT, and/or CRT glass from an offsite source to submit notification with all required information to DTSC no later than 30 calendar days prior to accepting any above noted waste. |  |  | OBSERVATION: Failure of the universal waste handler who accepts and accumulates, but does not treat, any PV modules, electronic device, CRT, and/or CRT glass from an offsite source, to submit notification with all required information to DTSC no later than 30 calendar days prior to accepting any above noted waste. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that notification with all required information has been submitted to the DTSC prior to accepting any wastes noted above. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110028 |  |  | Universal Waste Handler: Annual Report | Failure of a universal waste handler who either: 1) accepts more than 100 kilograms (or 220 pounds) of PV modules or electronic devices, CRTs, and CRT glass calculated collectively, from any offsite sources in a calendar year, or 2) generates 5,000 kilograms (or 11,000 pounds; e.g., about 200 CRTs) or more of PV modules or electronic devices, CRTs, and CRT glass calculated collectively, in a calendar year, to submit to DTSC by February 1 of every year a an annual report that includes all required information. | 22 CCR 23 66273.32(d)(1), (2), (f)(1), (2) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 70 71 | Universal Waste | Electronic Devices/CRT/PV Modules | Accepts 100 kg or generates 5000 kg/yr of E-waste/CRTs/PV modules & reports to DTSC Feb 1 annually | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of a universal waste handler who either: 1) accepts more than 100 kilograms (or 220 pounds) of PV modules or electronic devices, CRTs, and CRT glass calculated collectively, from any offsite sources in a calendar year, or 2) generates 5,000 kilograms (or 11,000 pounds; e.g., about 200 CRTs) or more of PV modules or electronic devices, CRTs, and CRT glass calculated collectively, in a calendar year, to submit to DTSC by February 1 of every year a an annual report that includes all required information. |  |  | OBSERVATION: The UWH accepts 100 kg of PV modules, electronic devices, CRTs, and CRT glass per year from offsite sources, or generates 5,000 kg or more, and has not submitted the required information to the DTSC by February 1st. CORRECTIVE ACTION: Submit the required information listed above to the DTSC and submit a copy to the UPA. | OBSERVATION: The UWH generates greater that 5,000 Kg of electronic devices, CRTs, and CRT glass per year and has not submitted the required information to the DTSC by February 1st. CORRECTIVE ACTION: Submit the required information listed above to the DTSC and submit a copy to the CUPA. | [5 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110029 |  |  | Universal Waste: Exporting Notification | Failure of the universal waste handler who sends electronic devices, CRTs, and/or CRT glass to any foreign destination to comply with the following: (1) Notify the Department 60 days prior to the intended export before any electronic devices, CRTs, and/or CRT glass are scheduled to leave the United States and cover all export activities extending over the next twelve (12) month or lesser period; (2) Concurrently send a copy of the notification required pursuant to subsection 66273.40(a)(2)(B) of 22 CCR to the CUPA having jurisdiction over the universal waste handler’s facility; (3) sign the export notification; and (4) include all required information in the export notification. | 22 CCR 23 66273.40(a)(2), (3) and (4) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 71 72 | Universal Waste | Exporting Notification | UWH sending devices/CRTs/CRT glass to any foreign destination completed and submitted notification | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the universal waste handler who sends electronic devices, CRTs, and/or CRT glass to any foreign destination to comply with the following: (1) Notify the Department 60 days prior to the intended export before any electronic devices, CRTs, and/or CRT glass are scheduled to leave the United States and cover all export activities extending over the next twelve (12) month or lesser period; (2) Concurrently send a copy of the notification required pursuant to subsection 66273.40(a)(2)(B) of 22 CCR to the CUPA having jurisdiction over the universal waste handler’s facility; (3) sign the export notification; and (4) include all required information in the export notification. |  |  | OBSERVATION: The universal waste handler failed to comply with one or more of the following: (1) Notify the DTSC 60 days prior to the intended export before any electronic devices, CRTs, and/or CRT glass are scheduled to leave the United States and cover all export activities extending over the next twelve (12) month or lesser period; (2) Concurrently send a copy of the notification required pursuant to subsection 66273.40(a)(2)(B) of 22 CCR, to the CUPA having jurisdiction over the universal waste handler’s facility; (3) sign the export notification; and (4) include all required information in the export notification. [enter specific observations] CORRECTIVE ACTION: Complete and submit the required notification information listed above to DTSC and to the UPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130038 |  |  | Universal Waste Handler: Labeling Requirements | Failure to label or mark each individual or container or the designated area of universal waste with the following: 1. Waste batteries shall be marked with "Universal Waste-Battery(ies)” 2. Mercury containing equipment shall be marked with "Universal Waste -Mercury-Containing Equipment” 3. Lamps shall be marked with “Universal Waste-Lamp(s)” 4. Electronic devices or the container or pallet where the devices are stored shall be marked with “Universal Waste-Electronic Device(s)” 5. CRTs or the container or pallet where CRTs are stored shall be marked with "Universal Waste-CRT(s)” 6. Container for CRT glass shall be marked with “Universal Waste-CRT glass” 7. PV modules shall be marked with "Universal Waste-PV Module(s)" | 22 CCR 23 66273.34 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 72 73 | Universal Waste | UW Management | UWH labeled all universal waste | 31 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to label or mark each individual or container or the designated area of universal waste with the following: 1. Waste batteries shall be marked with "Universal Waste-Battery(ies)” 2. Mercury containing equipment shall be marked with "Universal Waste -Mercury-Containing Equipment” 3. Lamps shall be marked with “Universal Waste-Lamp(s)” 4. Electronic devices or the container or pallet where the devices are stored shall be marked with “Universal Waste-Electronic Device(s)” 5. CRTs or the container or pallet where CRTs are stored shall be marked with "Universal Waste-CRT(s)” 6. Container for CRT glass shall be marked with “Universal Waste-CRT glass” 7. PV modules shall be marked with "Universal Waste-PV Module(s)" |  |  | OBSERVATION: Owner/Operator failed to properly label universal waste. CORRECTIVE ACTION: Properly label universal waste [Identify] and submit statement of compliance and/or a photo of the waste labeled properly. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130039 |  |  | Universal Waste Handler: Accumulation Time | Failure to accumulate universal waste for one year or less and to demonstrate the length of time that the universal waste has been accumulated from the date it became a waste or was received. | 22 CCR 23 66273.35 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 73 74 | Universal Waste | UW Management | UWH accumulated universal waste for no longer than 1 year | 57 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure to accumulate universal waste for one year or less and to demonstrate the length of time that the universal waste has been accumulated from the date it became a waste or was received. |  |  | OBSERVATION: [UNIVERSAL WASTE] located in the [LOCATION] was observed with an accumulation start date of [DATE]. CORRECTIVE ACTION: Dispose of [UNIVERSAL WASTE] and submit a copy of the manifest/receipt to the CUPA. | OBSERVATION: [UNIVERSAL WASTE] located in the [LOCATION] was observed without an accumulation start date and the UWH was unable to demonstrate that the universal waste has been accumulating less than one year. CORRECTIVE ACTION: Dispose of [UNIVERSAL WASTE] and submit a copy of the manifest/receipt to the CUPA. | [5 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130040 |  |  | Universal Waste: Accumulation of Aerosol Cans | Failure to comply with the applicable requirements related to accumulation and containment standards for universal waste aerosol cans. | HSC 6.5 25201.16(f) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 74 75 | Universal Waste | UW Management | UWH meets all accumulation standards for universal waste aerosol cans | 69 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure to comply with the applicable requirements related to accumulation and containment standards for universal waste aerosol cans. |  |  | OBSERVATION: [Describe container - not closed, leaking, incompatible with contents, etc.]. [Aerosol cans, or contents removed from aerosol cans etc.] shall be accumulated in a container that is closed, structurally sound and compatible with the contents of the universal waste aerosol can and show no leakage, spillage, or damage that could cause leakage. CORRECTIVE ACTION: Immediately [close container, transfer to compatible container, etc.]. Submit documentation to the CUPA demonstrating what corrective actions were taken. | OBSERVATION: [Describe container, location, and condition of floor]. Containers holding aerosol cans or contents removed from aerosol cans shall be placed on or above a floor that is free of cracks or gaps and is sufficiently impervious and bermed to contain leaks and spills. CORRECTIVE ACTION: Immediately relocate this container to a proper location. Submit documentation to the CUPA demonstrating what corrective actions were taken. | OBSERVATION: [Describe aerosol cans found and note incompatibilities] were found stored in the same container. Incompatible materials shall be kept segregated and managed appropriately in separate containers. CORRECTIVE ACTION: Immediately separate the incompatible aerosol cans and store them in separate containers. Ensure that all aerosol cans are checked for compatibility prior to storage. Submit documentation to the CUPA demonstrating what corrective actions were taken. | OBSERVATION: [Describe container, location, and proximity to heat source]. A container holding flammable wastes shall be kept at a safe distance from heat and open flames. CORRECTIVE ACTION: Immediately relocate this container to a safe distance from [whatever the heat source is]. Submit documentation to the CUPA demonstrating what corrective actions were taken. | OBSERVATION: [Describe container and location] were found not labeled with the type of waste stored. Containers used to store aerosol cans shall be labeled or marked with one of the following phrases: “Universal Waste – Aerosol Cans”, “Waste Aerosol Cans”, or “Used Aerosol Cans”. CORRECTIVE ACTION: Immediately mark these containers and ensure that all containers of aerosol cans are marked in this manner. Submit documentation to the CUPA demonstrating what corrective actions were taken. |  |  | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130041 |  |  | Universal Waste: Handling of Aerosol Cans | Failure of the universal waste handler to manage universal waste aerosol cans in a manner that prevents fire, explosion, and the unauthorized release of any universal waste or component of a universal waste to the environment. | HSC 6.5 25201.16(e) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 75 76 | Universal Waste | UW Management | Universal waste aerosol cans managed to prevent fire, explosion and unauthorized release | 88 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the universal waste handler to manage universal waste aerosol cans in a manner that prevents fire, explosion, and the unauthorized release of any universal waste or component of a universal waste to the environment. |  |  | OBSERVATION: Owner/Operator failed to manage universal waste aerosol cans in a manner that prevents fire, explosion, and the unauthorized release of any universal waste or component of a universal waste to the environment. CORRECTIVE ACTION: Properly manage universal waste aerosol cans in a manner that prevents fire, explosion, and the unauthorized release of any universal waste or component of a universal waste to the environment. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110030 |  |  | Universal Waste Aerosol Can Processing | Failure to notify the CUPA of aerosol can processing procedures prior to commencement of operations | HSC 25201.16(j) | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 76 77 | Universal Waste | UW Management | Notified UPA of aerosol can processing procedures prior to starting this process | 80 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure to notify the CUPA of aerosol can processing procedures prior to commencement of operations |  |  | OBSERVATION: Owner/Operator failed to notify UPA of aerosol can processing procedures prior to starting this process. CORRECTIVE ACTION: Submit required notification to UPA of aerosol can processing procedures. Discontinue processing aerosol cans until this notification is submitted to UPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130042 |  |  | Universal Waste Handler: Offsite Shipments | Failure of the universal waste handler to transfer universal waste to another universal waste handler, or appropriate destination facility. Failure to package, label, mark and placard shipments and prepare shipping papers for any universal waste that meets the hazardous materials definition in accordance with DOT 49 CFR parts 171-180. | 22 CCR 23 66273.38; 49 CFR 1 172 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 77 78 | Universal Waste | UW Management | UWH properly prepares, handles and retains shipping papers for all universal waste shipped | 90 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of the universal waste handler to transfer universal waste to another universal waste handler, or appropriate destination facility. Failure to package, label, mark and placard shipments and prepare shipping papers for any universal waste that meets the hazardous materials definition in accordance with DOT 49 CFR parts 171-180. |  |  | OBSERVATION: Universal Waste Handler (UWH) failed to properly package, label, mark, placard, or prepare and retain shipping papers for all universal waste being shipped to another universal waste handler, destination facility, or foreign facility. [ENTER SPECIFIC OBSERVATION] CORRECTIVE ACTION: Submit documentation to the CUPA demonstrating that all universal waste noted above have been properly packaged, labeled, marked, placarded, or prepared and retain shipping papers. | OBSERVATION: Universal Waste Handler failed to send UW to another Universal Waste Handler or a permitted destination facility as observed by [ENTER OBSERVED SHIPPING/DISPOSAL VIOLATION]. CORRECTIVE ACTION: The UWH shall immediately submit a written statement to the CUPA documenting how the facility will properly manage and recycle all UW generated on site. | [5 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150006 |  |  | Universal Waste Handler: Illegal Disposal | Failure of the universal waste handler to prevent improper disposal of universal waste, or to transfer universal waste to the appropriate destination facility. | 22 CCR 23 66273.31(a), 66273.8(b) | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 78 79 | Universal Waste | UW Management | UWH transfers or disposes all universal waste to an appropriate destination facility | 84 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 30 | Failure of the universal waste handler to transfer universal waste to the appropriate destination facility. |  |  | OBSERVATION: The Universal Waste Handler improperly disposed of, or failed to transfer universal waste to an appropriate destination facility. CORRECTIVE ACTION: Ensure that all universal wastes are transferred to an appropriate destination facility and properly disposed. Submit documentation to the CUPA indicating that all universal waste has been transferred to an appropriate destination facility. | [6 empty] | Yes
RCRA Large Quantity Generator | Release/Leaks/Spills | 3140003 |  |  | Universal Waste Handler: Release | Failure of the universal waste handler of PV modules, electronic devices, CRTs, and CRT glass to prevent the release of the universal waste to the environment under reasonable conditions by the following methods: 1) Immediately clean spills and leaks of universal wastes; and 2) Place all universal waste spills and leaks in containers that are structurally sound and compatible with the universal waste. | 22 CCR 23 66273.33.5, 66273.33.6 | 2021-08-02 | 2099-12-31 | 2021-08-02 | Revised | 79 80 | Universal Waste | UW Management | UWH properly cleaned up and contained spills of PV modules, electronic devices, CRTs and CRT glass | 98 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Class 2 | Yes |  | 14 30 | Failure of the universal waste handler of PV modules, electronic devices, CRTs, and CRT glass to prevent the release of the universal waste to the environment under reasonable conditions by the following methods: 1) Immediately clean spills and leaks of universal wastes; and 2) Place all universal waste spills and leaks in containers that are structurally sound and compatible with the universal waste. |  |  | OBSERVATION: Failure of Universal Waste Handler of PV modules, electronic devices, CRTs and/or CRT glass to prevent the release of universal waste to the environment by failing to immediately clean spills and leaks of universal wastes and/or by placing spilled/leaked waste in containers that are not structurally sound and compatible with the waste. CORRECTIVE ACTION: Submit documentation to the UPA demonstrating that the spilled PV modules, electronic devices, CRTs and/or CRT glass have been properly removed/cleaned up and managed. | [6 empty] | Yes
RCRA Large Quantity Generator | Training | 3120002 |  |  | Universal Waste Handler: Employee Training | Failure of universal waste handler to provide initial and/or annual refresher training for employees who manage or handle universal waste and to maintain a written record for three years of personnel who took the initial or annual training. | 22 CCR 23 66273.36 | 2018-10-01 | 2099-12-31 | 2018-10-01 | Revised | 80 81 | Universal Waste | Training | UWH complied with all universal waste training requirements | 59 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Failure of universal waste handler to provide initial and/or annual refresher training for employees who manage or handle universal waste and to maintain a written record for three years of personnel who took the initial or annual training. |  |  | OBSERVATION: Owner/Operator failed to provide initial and/or annual refresher training for employees who manage or handle universal waste and to maintain a written record for three years of personnel who took the initial or annual training. CORRECTIVE ACTION: Provide employees with initial or refresher UW training. Submit a evidence of training to the CUPA. | [6 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3110 |  | 262.A | RCRA-Administration/Documentation - General | Administration/Documentation - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 81 82 | General Facility Requirements |  | Administration/Documentation - General | 38 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General | [9 empty] | Yes
RCRA Large Quantity Generator | Administration/Documentation | 3115 |  |  | RCRA-Administration/Documentation - General Local Ordinance | Administration/Documentation - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 82 83 | General Facility Requirements |  | Administration/Documentation - General Local Ordinance | 54 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Administration/Documentation - General Local Ordinance | [9 empty] | Yes
RCRA Large Quantity Generator | Training | 3120 |  | 262.A | RCRA-Training - General | Training - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 83 84 | General Facility Requirements |  | Training - General | 18 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General | [9 empty] | Yes
RCRA Large Quantity Generator | Training | 3125 |  |  | RCRA-Training - General Local Ordinance | Training - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 84 85 | General Facility Requirements |  | Training - General Local Ordinance | 34 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Training - General Local Ordinance | [9 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3130 |  | 262.A | RCRA-Operations/Maintenance - General | Operations/Maintenance - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 85 86 | General Facility Requirements |  | Operations/Maintenance - General | 32 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General | [9 empty] | Yes
RCRA Large Quantity Generator | Operations/Maintenance | 3135 |  |  | RCRA-Operations/Maintenance - General Local Ordinance | Operations/Maintenance - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 86 87 | General Facility Requirements |  | Operations/Maintenance - General Local Ordinance | 48 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Operations/Maintenance - General Local Ordinance | [9 empty] | Yes
RCRA Large Quantity Generator | Release/Leaks/Spills | 3140 |  | 262.A | RCRA-Release/Leaks/Spills - General | Release/Leaks/Spills - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 87 88 | General Facility Requirements |  | Release/Leaks/Spills - General | 30 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General | [9 empty] | Yes
RCRA Large Quantity Generator | Release/Leaks/Spills | 3145 |  |  | RCRA-Release/Leaks/Spills - General Local Ordinance | Release/Leaks/Spills - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 88 89 | General Facility Requirements |  | Release/Leaks/Spills - General Local Ordinance | 46 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Release/Leaks/Spills - General Local Ordinance | [9 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3150 |  | 262.A | RCRA-Abandonment/Illegal Disposal/Unauthorized Treatment - General | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 22 CCR Multiple Chapters, Multiple Sections; 40 CFR 1 265; HSC 6.5 Multiple Sections | 2017-11-01 | 2099-12-31 | 2017-11-01 | Revised | 89 90 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General | 61 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General | [9 empty] | Yes
RCRA Large Quantity Generator | Abandonment/Illegal Disposal/Unauthorized Treatment | 3155 |  |  | RCRA-Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance |  | 2016-06-01 | 2099-12-31 | 2016-06-01 | Revised | 90 91 | General Facility Requirements |  | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | 77 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minor | Yes |  | 30 | Abandonment/Illegal Disposal/Unauthorized Treatment - General Local Ordinance | [9 empty] | Yes

## Spreadsheet Notes
Please note the following regarding these spreadsheets:
These spreadsheets may be used by UPAs/PAs to create/update electronic inspection checklists for all Unified Programs.
These spreadsheets are updated each year after the CERS Violation Library has been updated.
The revised versions of these spreadsheets are made available generally 2-3 months before the CERS Violation Library changes go live in CERS.
The version of these spreadsheets that shows edits displays added text as underlined and deleted text with strikethrough, both of which are in red. Minor spelling corrections or formatting changes may not be displayed, but if any changes did occur the Violation Type Number cell and the cells that were updated are highlighted yellow and the Comment column says Revised. This is true even if the only thing that changed was the Checklist Item Order value. The same is true for the Clean version of the spreadsheets but only the final version of text is shown. Actual revisions are not detailed on the Clean version, so there is no underlined text or strikethrough and all text is black, but revised cells are highlighted in yellow. Note that the Comments column cells are not highlighted. New violations in the Edited version show the text in all cells in red and underlined. New violations in the Clean version also show all text in red, but not underlined. All cells of New violations in the Edited and Clean versions are not highlighted in yellow.
The column titled Comments says Existing for any violation that was not revised during this update period, Revised for any violation that had any cell updated, and New for new violations. Note that a violation is identified as Revised if any revision is made. However, a new Begin Date is only assigned if changes occurred to the CERS info (see below) and the change was deemed to be significant by CalEPA. When there are Revised violations that have a new Begin Date assigned, in CERS they assign a new End Date to the previous (expiring) version of the violation, which is one day before the Begin Date of the Revised versions. To maintain the previous versions of revised violations in your system, so they will continue to be displayed on reports as they should for the date they were cited, you will likely need to assign an End Date of 6/30/2023 to the previous versions of Revised violations since the new Begin Date of the Revised version of that violation will be 7/1/2023. The expiring versions of violations are not displayed in these spreadsheets. A separate spreadsheet is available showing all expiring versions of violations.
The word Deleted is entered in the Comments column for deleted violations, for which there is no revised version, and the Checklist Item Order value is blank, and as a result, deleted violations, if any, show up at the end of the lists. There are no Deleted violations in the 2023 update.
The Begin Dates will match the Begin Dates in CERS. If a violation only had CUPA column info updated this does not result in a new Begin Date. Only CERS info changes deemed significant result in a new Begin Date.
CERS Info refers the information provided in columns A-K. This information matches violation information in CERS.
CUPA Info refers to the information provided in all columns to the right of column K. This information is not in CERS.
Each row is a separate violation and the spreadsheets are sorted by Checklist Item Order, which represents the intended order on the checklists that the violations will be displayed.
Inspection Checklist Item Text is the text that will show on the inspection checklist for that violation. This field was originally set up to only allow for 100 characters, which is the reason for abbreviations and limited detail at times.
The character limit in CERS for violation comments is 1000 characters. There are some prewritten Inspector Comments (Observation and Corrective Action) that are over 1000 characters. Depending on your system this may result in only the first 1000 characters being transferred to CERS or it may result in a failure to transfer any of the information, if an inspector utilizes a default inspection comment that is >1000 characters.
When the spreadsheets were first developed the Default Degree of Violation (Class) was set for all violations. You may want to make this field blank in your inspection system so inspectors must set the class versus relying on a default class which may not always be correct given the specific circumstances.
The far right columns of each spreadsheet will have one or more columns for the type(s) of facilities for that program. i.e. HMBP will only have one, but UST will have three (DW, SW, Full). Violations will be set as Yes in these columns if they apply to that facility type and No if not. So those violations with a Yes in the UST DW column will show up on an inspection checklist for DW UST sites, and those with a No will not. Those with a Yes in the SW column will show on a checklist for SW sites. There is a Yes for every violation in the Full column so all violations will show on a checklist for Full, which, for UST, would be for a facility that includes both SW and DW components. This same method is used on all program sheets with multiple facility types. All programs except HMBP and RCRA LQG have multiple facility types. There is only a Full column for UST and TP spreadsheets.